## Year to Date
38 DN |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 41814442.7681 | 46089296.626 | -4274853.8579 | -9.275% | 44342735.405 | -2528292.6369 | -5.702%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
6th St. | CA | 1885221.5 | 1886461.055 | -1239.555 | -0.06571% | 2141831.572 | -256610.072 | -11.98%
Barton Acres | MA | 1478829 | 1708308.61 | -229479.61 | -13.43% | 1507988.996 | -29159.996 | -1.934%
Bowden | MA | 2999821 | 3193950.51 | -194129.51 | -6.078% | 3181466.244 | -181645.244 | -5.709%
Blair Wire Village | MA | 1462141 | 1773221.229 | -311080.229 | -17.54% | 1595433.394 | -133292.394 | -8.355%
Boutilier | MA | 4076666 | 4296245.815 | -219579.815 | -5.111% | 4139610.97 | -62944.97 | -1.521%
Cherry Valley | MA | 1383813 | 1710399.276 | -326586.276 | -19.09% | 1516724.335 | -132911.335 | -8.763%
Cohasse | MA | 1333902 | 1573391.676 | -239489.676 | -15.22% | 1670337.106 | -336435.106 | -20.14%
ISM Dighton Solar 2 | MA | 3212877 | 3160820.185 | 52056.815 | 1.647% | 3259371.07 | -46494.07 | -1.426%
Dudley River 1 | MA | 1469091 | 1633112.223 | -164021.223 | -10.04% | 1610020.268 | -140929.268 | -8.753%
Dudley River 2 | MA | 1440006 | 1583854.476 | -143848.476 | -9.082% | 1538754.023 | -98748.023 | -6.417%
Dudley River 3 | MA | 1501449 | 1586642.979 | -85193.979 | -5.369% | 1560509.053 | -59060.053 | -3.785%
Flint Pond | MA | 701851 | 707050.53 | -5199.53 | -0.7354% | 713662.36 | -11811.36 | -1.655%
Incom | MA | 3064242.7715 | 3583771.814 | -519529.0425 | -14.5% | 3378391.62 | -314148.8485 | -9.299%
JH | MA | 1372981 | 1620063.188 | -247082.188 | -15.25% | 1626854.68 | -253873.68 | -15.61%
Ledeaux | MA | 1250378 | 1447279.139 | -196901.139 | -13.6% | 1577021.166 | -326643.166 | -20.71%
Palombo A | MA | 3045223.9967 | 3405111.038 | -359887.0413 | -10.57% | 3471823.62 | -426599.6233 | -12.29%
Palombo B | MA | 1502064 | 1500886.957 | 1177.043 | 0.07842% | 1562699.46 | -60635.46 | -3.88%
St Josephs Church | MA | 1438263 | 1753824.928 | -315561.928 | -17.99% | 1562069.238 | -123806.238 | -7.926%
Sunset A | MA | 697350.5 | 855285.989 | -157935.489 | -18.47% | 709952.798 | -12602.298 | -1.775%
Sunset B | MA | 655921 | 756352.298 | -100431.298 | -13.28% | 699149.938 | -43228.938 | -6.183%
Woodchuck | MA | 1420252 | 1618715.391 | -198463.391 | -12.26% | 1650066.774 | -229814.774 | -13.93%
NY: Skaneateles - Spafford 1 - (PW) | NY | 3081687 | 3502802.381 | -421115.381 | -12.02% | 2583239.9 | 498447.1 | 19.3%
NY: Skaneateles - Spafford 2 - (PW) | NY | 1340412 | 1231744.939 | 108667.061 | 8.822% | 1085756.82 | 254655.18 | 23.45%

## 1st Qtr
38 DN |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 7176121.9967 | 10259800.8 | -3083678.8033 | -30.06% | 9158239.8 | -1982117.8033 | -21.64%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
6th St. | CA | 444186 | 287164.39 | 157021.61 | 54.68% | 482812.5 | -38626.5 | -8%
Barton Acres | MA | 230538 | 438008.7 | -207470.7 | -47.37% | 308750.26 | -78212.26 | -25.33%
Bowden | MA | 530464 | 727999 | -197535 | -27.13% | 680814.9 | -150350.9 | -22.08%
Blair Wire Village | MA | 258498 | 467163 | -208665 | -44.67% | 339598.43 | -81100.43 | -23.88%
Boutilier | MA | 725439 | 1083258.7 | -357819.7 | -33.03% | 847559.7 | -122120.7 | -14.41%
Cherry Valley | MA | 247783 | 453570.3 | -205787.3 | -45.37% | 328696 | -80913 | -24.62%
Cohasse | MA | 256962 | 429905.6 | -172943.6 | -40.23% | 419649.4 | -162687.4 | -38.77%
ISM Dighton Solar 2 | MA | 773019 | 846304.4 | -73285.4 | -8.659% | 723680 | 49339 | 6.818%
Dudley River 1 | MA | 278440 | 380481 | -102041 | -26.82% | 348226.75 | -69786.75 | -20.04%
Dudley River 2 | MA | 290147 | 386502.2 | -96355.2 | -24.93% | 333877.69 | -43730.69 | -13.1%
Dudley River 3 | MA | 313438 | 389853.3 | -76415.3 | -19.6% | 339181.09 | -25743.09 | -7.59%
Flint Pond | MA | 132190 | 200200.69 | -68010.69 | -33.97% | 148836.42 | -16646.42 | -11.18%
Incom | MA | 580235 | 859821.3 | -279586.3 | -32.52% | 822911.8 | -242676.8 | -29.49%
JH | MA | 240983 | 419234.4 | -178251.4 | -42.52% | 399271.1 | -158288.1 | -39.64%
Ledeaux | MA | 208236 | 318933.48 | -110697.48 | -34.71% | 378806.93 | -170570.93 | -45.03%
Palombo A | MA | 642572.9967 | 908872.2 | -266299.2033 | -29.3% | 905621 | -263048.0033 | -29.05%
Palombo B | MA | 297674 | 430698.1 | -133024.1 | -30.89% | 320372.22 | -22698.22 | -7.085%
St Josephs Church | MA | 259768 | 454634.7 | -194866.7 | -42.86% | 360543.32 | -100775.32 | -27.95%
Sunset A | MA | 112615 | 221638.56 | -109023.56 | -49.19% | 145359.43 | -32744.43 | -22.53%
Sunset B | MA | 109183 | 174489.28 | -65306.28 | -37.43% | 143619.53 | -34436.53 | -23.98%
Woodchuck | MA | 243751 | 381067.5 | -137316.5 | -36.03% | 380051.33 | -136300.33 | -35.86%
NY: Skaneateles - Spafford 1 - (PW) | NY
NY: Skaneateles - Spafford 2 - (PW) | NY
1338628

## 2nd Qtr
38 DN |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 12658175.5 | 12795229.66 | -137054.16 | -1.071% | 14212579.53 | -1554404.03 | -10.94%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
6th St. | CA | 670808 | 713840.6 | -43032.6 | -6.028% | 723242.4 | -52434.4 | -7.25%
Barton Acres | MA | 511911 | 500054.3 | 11856.7 | 2.371% | 557925 | -46014 | -8.247%
Bowden | MA | 1011126 | 1002705.3 | 8420.7 | 0.8398% | 1109859.1 | -98733.1 | -8.896%
Blair Wire Village | MA | 499832 | 519963.4 | -20131.4 | -3.872% | 556262.9 | -56430.9 | -10.14%
Boutilier | MA | 1423134 | 1368539.6 | 54594.4 | 3.989% | 1531557.4 | -108423.4 | -7.079%
Cherry Valley | MA | 472773 | 493158.6 | -20385.6 | -4.134% | 553860 | -81087 | -14.64%
Cohasse | MA | 447461 | 454376.9 | -6915.9 | -1.522% | 553831.5 | -106370.5 | -19.21%
ISM Dighton Solar 2 | MA | 1031647 | 1022394 | 9253 | 0.905% | 1135551 | -103904 | -9.15%
Dudley River 1 | MA | 498146 | 507837.1 | -9691.1 | -1.908% | 559136.1 | -60990.1 | -10.91%
Dudley River 2 | MA | 479554 | 492777.4 | -13223.4 | -2.683% | 534652.1 | -55098.1 | -10.31%
Dudley River 3 | MA | 490287 | 490712.8 | -425.8 | -0.08677% | 541681.8 | -51394.8 | -9.488%
Flint Pond | MA | 242532 | 201456.35 | 41075.65 | 20.39% | 263547.02 | -21015.02 | -7.974%
Incom | MA | 1001038 | 1125427.5 | -124389.5 | -11.05% | 1133235.6 | -132197.6 | -11.67%
JH | MA | 475459 | 481539.9 | -6080.9 | -1.263% | 549012.3 | -73553.3 | -13.4%
Ledeaux | MA | 443140 | 464368.8 | -21228.8 | -4.572% | 539570.2 | -96430.2 | -17.87%
Palombo A | MA | 1002886 | 1009720.8 | -6834.8 | -0.6769% | 1145758 | -142872 | -12.47%
Palombo B | MA | 504390 | 428528.7 | 75861.3 | 17.7% | 580575.9 | -76185.9 | -13.12%
St Josephs Church | MA | 488455 | 519324.2 | -30869.2 | -5.944% | 544012 | -55557 | -10.21%
Sunset A | MA | 242029 | 250906.76 | -8877.76 | -3.538% | 262678.88 | -20649.88 | -7.861%
Sunset B | MA | 230349.5 | 242262.65 | -11913.15 | -4.917% | 259523.83 | -29174.33 | -11.24%
Woodchuck | MA | 491218 | 505334 | -14116 | -2.793% | 577106.5 | -85888.5 | -14.88%
NY: Skaneateles - Spafford 1 - (PW) | NY
NY: Skaneateles - Spafford 2 - (PW) | NY

## 3rd Qtr
38 DN |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 17562481.2715 | 18236619.066 | -674137.7945 | -3.697% | 16876439.265 | 686042.0065 | 4.065%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
6th St. | CA | 598625 | 743772.265 | -145147.265 | -19.52% | 743190.572 | -144565.572 | -19.45%
Barton Acres | MA | 596179 | 605364.01 | -9185.01 | -1.517% | 533358.736 | 62820.264 | 11.78%
Bowden | MA | 1173440 | 1172912.51 | 527.49 | 0.04497% | 1112167.444 | 61272.556 | 5.509%
Blair Wire Village | MA | 567235 | 618195.729 | -50960.729 | -8.243% | 557949.064 | 9285.936 | 1.664%
Boutilier | MA | 1563343 | 1480347.215 | 82995.785 | 5.607% | 1464145.87 | 99197.13 | 6.775%
Cherry Valley | MA | 536983 | 600273.876 | -63290.876 | -10.54% | 521877.335 | 15105.665 | 2.894%
Cohasse | MA | 506157 | 536734.976 | -30577.976 | -5.697% | 550233.506 | -44076.506 | -8.011%
ISM Dighton Solar 2 | MA | 1173946 | 1119670.585 | 54275.415 | 4.847% | 1106156.27 | 67789.73 | 6.128%
Dudley River 1 | MA | 554583 | 598126.923 | -43543.923 | -7.28% | 560902.118 | -6319.118 | -1.127%
Dudley River 2 | MA | 533692 | 563357.276 | -29665.276 | -5.266% | 534339.333 | -647.333 | -0.1211%
Dudley River 3 | MA | 555172 | 563617.479 | -8445.479 | -1.498% | 541743.163 | 13428.837 | 2.479%
Flint Pond | MA | 270342 | 234356.69 | 35985.31 | 15.35% | 249951.97 | 20390.03 | 8.158%
Incom | MA | 1187950.7715 | 1282443.714 | -94492.9425 | -7.368% | 1131982.12 | 55968.6515 | 4.944%
JH | MA | 536582 | 561501.288 | -24919.288 | -4.438% | 540273.88 | -3691.88 | -0.6833%
Ledeaux | MA | 489843 | 536992.659 | -47149.659 | -8.78% | 526740.036 | -36897.036 | -7.005%
Palombo A | MA | 1129565 | 1171110.838 | -41545.838 | -3.548% | 1116392.42 | 13172.58 | 1.18%
Palombo B | MA | 569054 | 494527.757 | 74526.243 | 15.07% | 549745.64 | 19308.36 | 3.512%
St Josephs Church | MA | 554911 | 612588.608 | -57677.608 | -9.415% | 533345.668 | 21565.332 | 4.043%
Sunset A | MA | 278507.5 | 302100.439 | -23592.939 | -7.81% | 251089.438 | 27418.062 | 10.92%
Sunset B | MA | 258640 | 275190.918 | -16550.918 | -6.014% | 245790.418 | 12849.582 | 5.228%
Woodchuck | MA | 556946 | 588360.191 | -31414.191 | -5.339% | 560190.744 | -3244.744 | -0.5792%
NY: Skaneateles - Spafford 1 - (PW) | NY | 2354870 | 2642874.581 | -288004.581 | -10.9% | 2070559.9 | 284310.1 | 13.73%
NY: Skaneateles - Spafford 2 - (PW) | NY | 1015915 | 932198.539 | 83716.461 | 8.981% | 874313.62 | 141601.38 | 16.2%

## 4th Qtr
38 DN |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 4417664 | 4797647.1 | -379983.1 | -7.92% | 4095476.81 | 322187.19 | 7.867%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
6th St. | CA | 171602.5 | 141683.8 | 29918.7 | 21.12% | 192586.1 | -20983.6 | -10.9%
Barton Acres | MA | 140201 | 164881.6 | -24680.6 | -14.97% | 107955 | 32246 | 29.87%
Bowden | MA | 284791 | 290333.7 | -5542.7 | -1.909% | 278624.8 | 6166.2 | 2.213%
Blair Wire Village | MA | 136576 | 167899.1 | -31323.1 | -18.66% | 141623 | -5047 | -3.564%
Boutilier | MA | 364750 | 364100.3 | 649.7 | 0.1784% | 296348 | 68402 | 23.08%
Cherry Valley | MA | 126274 | 163396.5 | -37122.5 | -22.72% | 112291 | 13983 | 12.45%
Cohasse | MA | 123322 | 152374.2 | -29052.2 | -19.07% | 146622.7 | -23300.7 | -15.89%
ISM Dighton Solar 2 | MA | 234265 | 172451.2 | 61813.8 | 35.84% | 293983.8 | -59718.8 | -20.31%
Dudley River 1 | MA | 137922 | 146667.2 | -8745.2 | -5.963% | 141755.3 | -3833.3 | -2.704%
Dudley River 2 | MA | 136613 | 141217.6 | -4604.6 | -3.261% | 135884.9 | 728.1 | 0.5358%
Dudley River 3 | MA | 142552 | 142459.4 | 92.6 | 0.065% | 137903 | 4649 | 3.371%
Flint Pond | MA | 56787 | 71036.8 | -14249.8 | -20.06% | 51326.95 | 5460.05 | 10.64%
Incom | MA | 295019 | 316079.3 | -21060.3 | -6.663% | 290262.1 | 4756.9 | 1.639%
JH | MA | 119957 | 157787.6 | -37830.6 | -23.98% | 138297.4 | -18340.4 | -13.26%
Ledeaux | MA | 109159 | 126984.2 | -17825.2 | -14.04% | 131904 | -22745 | -17.24%
Palombo A | MA | 270200 | 315407.2 | -45207.2 | -14.33% | 304052.2 | -33852.2 | -11.13%
Palombo B | MA | 130946 | 147132.4 | -16186.4 | -11% | 112005.7 | 18940.3 | 16.91%
St Josephs Church | MA | 135129 | 167277.42 | -32148.42 | -19.22% | 124168.25 | 10960.75 | 8.827%
Sunset A | MA | 64199 | 80640.23 | -16441.23 | -20.39% | 50825.05 | 13373.95 | 26.31%
Sunset B | MA | 57748.5 | 64409.45 | -6660.95 | -10.34% | 50216.16 | 7532.34 | 15%
Woodchuck | MA | 128337 | 143953.7 | -15616.7 | -10.85% | 132718.2 | -4381.2 | -3.301%
NY: Skaneateles - Spafford 1 - (PW) | NY | 726817 | 859927.8 | -133110.8 | -15.48% | 512680 | 214137 | 41.77%
NY: Skaneateles - Spafford 2 - (PW) | NY | 324497 | 299546.4 | 24950.6 | 8.329% | 211443.2 | 113053.8 | 53.47%

## Jan
38 DN |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 1879993.2467 | 3100330.85 | -1220337.6033 | -39.36% | 2316666.03 | -436672.7833 | -18.85% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA | 129016 | 74840.77 | 54175.23 | 72.39% | 144521 | -15505 | -10.73% | 1. PAD 2 inverters and Meter 2 tripped offline at 13:10 on 01/07 due to missing Phase A voltage. The technician found the main breaker open and closed it, restoring PAD 2 inverters at 09:00 on 01/08. Additionally, Inverter 19 lost communication at 13:00 on 01/07 due to a thermal event in the power head control board. It was sent for RMA. A spare inverter was installed from storage, bringing the system back online at 13:15 on 01/08. | 1.SR095378
Barton Acres | MA | 56999 | 142857.9 | -85858.9 | -60.1% | 69105.15 | -12106.15 | -17.52% | 1.Site was taken offline from 9:00AM to 9:45AM on 01/27 as technician was onsite to collect DGA samples. | 1.SR095405
Bowden | MA | 138818 | 194548.5 | -55730.5 | -28.65% | 166837.3 | -28019.3 | -16.79% | 1. Inverter 4 tripped offline at 07:45 AM on 01/06. The technician power cycled it, restoring operation at 13:00. 2. The site tripped offline at 22:00 on 01/29 and was restored at 07:00 on 01/30 after remotely closing the recloser. | 1.SR095329 2.SR096129 | SR096129
Blair Wire Village | MA | 67575 | 148603.1 | -81028.1 | -54.53% | 82695.73 | -15120.73 | -18.28% | 1.Low generation due to weather/snow.
Boutilier | MA | 197770 | 316212.5 | -118442.5 | -37.46% | 189703.5 | 8066.5 | 4.252%
Cherry Valley | MA | 62784 | 141889.9 | -79105.9 | -55.75% | 77483 | -14699 | -18.97% | 1. The site tripped offline at 14:00 on 01/24 due to a utility outage. After power was restored, the technician re-energized the site, bringing it back online at 08:45 on 01/25. | 1.SR095966
Cohasse | MA | 68246 | 140408.6 | -72162.6 | -51.39% | 113608.5 | -45362.5 | -39.93% | 1.Low generation due to weather/snow.
ISM Dighton Solar 2 | MA | 216783 | 272074.2 | -55291.2 | -20.32% | 194872.6 | 21910.4 | 11.24% | 1. The site tripped offline at 06:45 AM and was restored at 08:30 AM on 01/04 after a remote recloser operation. 2. Inverter 2, Module 4 tripped offline at 10:15 on 01/26. PE replaced the fuse and re-energized the inverter. It was back online at 11:00 on 01/27. | 1.SR095306 2.SR095988 | SR095988
Dudley River 1 | MA | 81072 | 112668.6 | -31596.6 | -28.04% | 83342.55 | -2270.55 | -2.724% | 1. The site was taken offline from 11:00 AM to 12:00 PM on 01/09 due to technicians was onsite to collect a DGA sample. | 1.SR095426
Dudley River 2 | MA | 77646 | 116307.2 | -38661.2 | -33.24% | 81508.99 | -3862.99 | -4.739% | 1.Inverters tripped offline at 8:45AM on 01/08 due to Y3 bushing on the transformer has a leak and B phase BON fuse was blown and back online at 10:30AM on 01/09 after INCOM has been replaced the Bayonet Fuse and re-energized. 2. Inverter 2 did not start production on 01/26 due to a soft shutdown fault. The technician found the keypad bulging due to water and ice intrusion. It was replaced, and the inverter was re-energized and back online at 12:15 PM on the same day. | 1.SR095387 2.SR095983 | SR095983
Dudley River 3 | MA | 94540 | 117412.4 | -22872.4 | -19.48% | 83727.59 | 10812.41 | 12.91% | 1. The site was taken offline from 10:45 AM to 12:00 PM on 01/09 as a technician was onsite to collect DGA samples | 1. SR095427
Flint Pond | MA | 30334 | 62237.73 | -31903.73 | -51.26% | 33375.62 | -3041.62 | -9.113% | 1.Site was taken offline from 8:10 AM to 9:10 AM on 01/15 due to a technician checking in to replace the capacitors and SRV board in Inverter A. | 1.SR092409
Incom | MA | 130021 | 227416.1 | -97395.1 | -42.83% | 219053.9 | -89032.9 | -40.64% | 1.Site was tripped offline due to SEL relay open at 02:45 AM on 01/02. The technician stated that a utility pole was leaning on a tree. After being re-energized, the site was back online at 10:15 AM on 01/08. | 1.SR095216
JH | MA | 61371 | 130704.5 | -69333.5 | -53.05% | 105686.5 | -44315.5 | -41.93% | 1.Low generation due to weather/snow.
Ledeaux | MA | 55084 | 97988.62 | -42904.62 | -43.79% | 98275.13 | -43191.13 | -43.95% | 1.Low generation due to weather/snow.
Palombo A | MA | 160890.9967 | 285170.7 | -124279.7033 | -43.58% | 250093 | -89202.0033 | -35.67% | 1.Low generation due to weather/snow.
Palombo B | MA | 65753 | 144714.1 | -78961.1 | -54.56% | 71408.82 | -5655.82 | -7.92% | 1.Low generation due to weather/snow.
St Josephs Church | MA | 69927 | 146021.7 | -76094.7 | -52.11% | 91072.42 | -21145.42 | -23.22% | 1.Low generation due to weather/snow.
Sunset A | MA | 27107 | 67386.6 | -40279.6 | -59.77% | 32533.05 | -5426.05 | -16.68% | 1.Low generation due to weather/snow.
Sunset B | MA | 26946.25 | 49373.03 | -22426.78 | -45.42% | 32145.45 | -5199.2 | -16.17% | 1.Low generation due to weather/snow.
Woodchuck | MA | 61310 | 111494.1 | -50184.1 | -45.01% | 95616.23 | -34306.23 | -35.88% | 1.Low generation due to weather/snow.
NY: Skaneateles - Spafford 1 - (PW) | NY
NY: Skaneateles - Spafford 2 - (PW) | NY

## Feb
38 DN |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 1480981.75 | 3093806.68 | -1612824.93 | -52.13% | 2901680.55 | -1420698.8 | -48.96% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA | 140097 | 83888.82 | 56208.18 | 67% | 146883.4 | -6786.4 | -4.62% | 1. Inverter 6 has been offline since 02/14/25 due to night mode. On 02/17, the technician performed necessary tests, but it worked for about 5 minutes before returning to night mode. After contacting SE for assistance, it was concluded that the DC main board had an issue. The technician RMA'd Inverter 6, replaced it with a spare, and brought it back online at 09:45 AM the same day. 2. Site was taken offline from 04:00AM to 10:00AM on 02/19/25 to work on quarterly generator load testing. | 1. SR097092 2. SR097707 | SR097707
Barton Acres | MA | 24856 | 131629.6 | -106773.6 | -81.12% | 97688.41 | -72832.41 | -74.56% | 1. Due to rain on 2/6 and heavy snow from 02/9 to 02/13, followed by snow shed until 02/23, there was low generation due to the weather."
Bowden | MA | 98772 | 222831.5 | -124059.5 | -55.67% | 215787.2 | -117015.2 | -54.23% | 1. Inverter 3 was offline on 02/14/25 due to Phase C voltage dropping to zero at 01:00 AM. The technician found no AC voltage and discovered the main AC breaker was tripped. After resetting the breaker, the inverter was brought back online at 08:00 AM the same day. | 1. SR097002
Blair Wire Village | MA | 38463 | 142760 | -104297 | -73.06% | 107644.1 | -69181.1 | -64.27% | 1. Site tripped offline at 22:56 on 02/16/25 and back online at 02:45 on 02/17/25 after a brife utility outage. | 1. SR097177
Boutilier | MA | 99725 | 329455.9 | -229730.9 | -69.73% | 268167.8 | -168442.8 | -62.81% | 1. Due to rain on 02/6 and heavy snow from 02/9 to 02/13, followed by snow shed until 02/23, there was low generation due to the weather."
Cherry Valley | MA | 39146 | 139696.5 | -100550.5 | -71.98% | 104227 | -65081 | -62.44% | 1. Site was taken offline from 08:15 AM to 10:00 AM on 02/11/25. A technician was on-site to collect transformer DGA samples | 1. SR095399
Cohasse | MA | 45443 | 128875.9 | -83432.9 | -64.74% | 135078.3 | -89635.3 | -66.36% | 1. Site was taken offline from 12:00 to 13:30 on 02/11/25. A technician was on-site to collect transformer DGA samples | 1. SR095398
ISM Dighton Solar 2 | MA | 233433 | 259693.3 | -26260.3 | -10.11% | 225679.4 | 7753.6 | 3.436% | 1. Site tripped offline at 08:15AM on 02/17/25 due to a breaker trip and was brought back online at 11:15 AM after a remote reset on the same day. | 1. SR097186
Dudley River 1 | MA | 61369 | 112575.9 | -51206.9 | -45.49% | 109352.8 | -47983.8 | -43.88% | 1. Due to rain on 02/6 and heavy snow from 02/9 to 02/13, followed by snow shed until 2/23, there was low generation due to the weather."
Dudley River 2 | MA | 62968 | 114772 | -51804 | -45.14% | 104036.4 | -41068.4 | -39.48% | 1. Due to rain on 02/6 and heavy snow from 02/9 to 02/13, followed by snow shed until 02/23, there was low generation due to the weather."
Dudley River 3 | MA | 64188 | 116653.8 | -52465.8 | -44.98% | 105482.7 | -41294.7 | -39.15% | 1.Due to rain on 02/6 and heavy snow from 02/9 to 02/13, followed by snow shed until 02/23, there was low generation due to the weather.
Flint Pond | MA | 29507.5 | 62544.76 | -33037.26 | -52.82% | 47235.91 | -17728.41 | -37.53% | 1. Site tripped offline at 09:00 on 02/26/25 and brought back online at 09:25AM after utility replaced blown fuse. | 1. SR097782
Incom | MA | 131063 | 271075.6 | -140012.6 | -51.65% | 262450.7 | -131387.7 | -50.06% | 1. Due to rain on 2/6 and heavy snow from 2/9 to 2/13, followed by snow shed until 2/23, there was low generation due to the weather.
JH | MA | 36137 | 123566.6 | -87429.6 | -70.76% | 128903.6 | -92766.6 | -71.97% | 1. Site tripped offline at 12:15 on 02/02/25 and was brought back online at 3:00 PM after the technician restored AC power by closing the SEL recloser on the same day. 2. Site tripped offline at 14:15 on 02/21/25, and the technician brought it back online at 13:00 on 02/22/25 after clearing the carcass from the B-phase connections. National Grid was contacted to reset their recloser, and the SEL recloser was closed. | 1. SR096228 2. SR097629 | SR097629
Ledeaux | MA | 21586 | 77598.96 | -56012.96 | -72.18% | 121085.5 | -99499.5 | -82.17% | 1. Site tripped offline at 12:15 PM on 02/02 due to a relay open. On 02/03, upon the technician's arrival, it was found that a blown fuse in the B-phase cutout and failed conductors . The site was brought back online at 12:15 PM on 02/12. 2. Site tripped offline at 02:15 PM on 02/21/25, and the technician brought it back online at 12:30PM on 02/22/25 after clearing the carcass from the B-phase connections. National Grid was contacted to reset their recloser, and the SEL recloser was closed. | 1.SR096225 2.SR097630 | SR097630
Palombo A | MA | 170055 | 276728 | -106673 | -38.55% | 292221 | -122166 | -41.81% | 1.Due to rain on 2/6 and heavy snow from 2/9 to 2/13, followed by snow shed until 2/23, there was low generation due to the weather.
Palombo B | MA | 76780 | 129139.3 | -52359.3 | -40.54% | 101396.5 | -24616.5 | -24.28% | 1.Due to rain on 02/6 and heavy snow from 02/9 to 02/13, followed by snow shed until 02/23, there was low generation due to the weather.
St Josephs Church | MA | 41512 | 137398.2 | -95886.2 | -69.79% | 115376.7 | -73864.7 | -64.02% | 1.Due to rain on 02/6 and heavy snow from 02/9 to 02/13, followed by snow shed until 02/23, there was low generation due to the weather.
Sunset A | MA | 15903.5 | 68409.08 | -52505.58 | -76.75% | 45991.62 | -30088.12 | -65.42% | 1.Due to rain on 02/6 and heavy snow from 02/9 to 02/13, followed by snow shed until 02/23, there was low generation due to the weather.
Sunset B | MA | 15154.75 | 51245.76 | -36091.01 | -70.43% | 45441.21 | -30286.46 | -66.65% | 1.Due to rain on 02/6 and heavy snow from 2/9 to 02/13, followed by snow shed until 02/23, there was low generation due to the weather.
Woodchuck | MA | 34823 | 113267.2 | -78444.2 | -69.26% | 121550.3 | -86727.3 | -71.35% | 1. Inverter 1, Combiner Box 4, tripped offline at 11:30 AM on 02/25. Upon the technician's arrival, it was found that ARC Card 2 had tripped, most likely due to melting snow. The strings on Cards 1 and 2 were swapped, and brought back online at 10:00 AM on 02/26. 2.Site tripped offline at 22:56 on 02/16/25 and back online at 02:45 on 02/17/25 after a brife utility outage. | 1.SR097765 2.SR097177 | SR097177
NY: Skaneateles - Spafford 1 - (PW) | NY
NY: Skaneateles - Spafford 2 - (PW) | NY

## Mar
38 DN |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 3815147 | 4065663.27 | -250516.27 | -6.162% | 3939893.22 | -124746.22 | -3.166% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA | 175073 | 128434.8 | 46638.2 | 36.31% | 191408.1 | -16335.1 | -8.534%
Barton Acres | MA | 148683 | 163521.2 | -14838.2 | -9.074% | 141956.7 | 6726.3 | 4.738%
Bowden | MA | 292874 | 310619 | -17745 | -5.713% | 298190.4 | -5316.4 | -1.783% | 1.Site tripped offline at 18:05 on 03/17,and later the site was remotely reclosed at 07:00 AM on 03/18 2.Inverter D (4) did not start after site recloser closed in after a relay trip on 03/18. Technician dispatched to site and found the inverter was in sleep mode caused by the outage, after troubleshooting he reset the inverter, and it was back online at 11:45 on 03/18 3.Inverters 1 & 2 tripped at 9:35am on 03/20 and were back online at 12:35 on 03/21 after technician replaced the back panel boards | 1.SR098683 2.SR098696 3.SR098774 | SR098696 | SR098774
Blair Wire Village | MA | 152460 | 175799.9 | -23339.9 | -13.28% | 149258.6 | 3201.4 | 2.145% | 1. The site was offline from 10:42AM to 11:53AM on 03/20 due to technician was onsite to collect DGA samples. | 1. SR098794
Boutilier | MA | 427944 | 437590.3 | -9646.3 | -2.204% | 389688.4 | 38255.6 | 9.817% | 1 .Inverter 4 tripped offline at 12:45 on 03/28. The technician found that the inverter's keypad was not working, so he replaced it and restarted the inverter. The inverter came back online at 15:15 on 03/28. | 1. SR099104
Cherry Valley | MA | 145853 | 171983.9 | -26130.9 | -15.19% | 146986 | -1133 | -0.7708% | 1. Inverter A was taken offline from 08:30am to 11:00am on 03/03 by technician to complete preventive maintenance. | 1. PM6833, SR098027
Cohasse | MA | 143273 | 160621.1 | -17348.1 | -10.8% | 170962.6 | -27689.6 | -16.2% | 1. Inverters 1 and 2 was offline from 10:45AM to 11:25AM due to technician was onsite for preventive maintenance. | 1. PM6834
ISM Dighton Solar 2 | MA | 322803 | 314536.9 | 8266.1 | 2.628% | 303128 | 19675 | 6.491% | 1. Inverters 1.1 to 1.5 were taken offline by technician during PM Event on 03/25 from 11:00am to 02:30pm. | 1. PM6837
Dudley River 1 | MA | 135999 | 155236.5 | -19237.5 | -12.39% | 155531.4 | -19532.4 | -12.56% | 1. Inverter 2 tripped offline at 10:00 AM on 03/12. The technician later troubleshot the inverter, and the bottom DMGI was RMA'd. After the replacement of the bottom DMGI, the inverter came back online at 10:45 AM on 03/19. 2. The site was taken offline from 09:15 AM to 10:30 AM on 03/19/25. Due to technician was on site for a PM event. | 1. SR098450 2. SR098450,PM6867 | SR098450
Dudley River 2 | MA | 149533 | 155423 | -5890 | -3.79% | 148332.3 | 1200.7 | 0.8095% | 1. During PM inspection on 03/14, technician observed that a fallen tree caused minor damage to 4 modules on the array and technician replaced 4 modules on 03/24. | 1. PM6957, SR098592
Dudley River 3 | MA | 154710 | 155787.1 | -1077.1 | -0.6914% | 149970.8 | 4739.2 | 3.16% | 1. Inverter 1 Combiner box 1 was offline from 11:45am to 02:00pm on 03/20 during the PM Inspection. | 1. PM7499
Flint Pond | MA | 72348.5 | 75418.2 | -3069.7 | -4.07% | 68224.89 | 4123.61 | 6.044% | 1. The site was taken offline from 08:35 AM to 09:30 AM on 03/20/25. Due to technician was on site to take DGA samples. | 1. SR098793
Incom | MA | 319151 | 361329.6 | -42178.6 | -11.67% | 341407.2 | -22256.2 | -6.519% | 1. Meter experienced intermittent communication issue from 03/15 to 03/18, 03/23 and 03/24. But all the time the energy has been backfilled. | 1. SR098928, SR098611 | SR098611
JH | MA | 143475 | 164963.3 | -21488.3 | -13.03% | 164681 | -21206 | -12.88% | 1.The site was taken offline from 07:30 AM to 08:15 AM on 03/21 by technicians to collect transformer DGA samples. 2. Inverter 1 was offline from 13:45 to 14:15 on 03/20 due to technician was onsite for preventive maintenance. | 1.SR098815 2. PM6868
Ledeaux | MA | 131566 | 143345.9 | -11779.9 | -8.218% | 159446.3 | -27880.3 | -17.49% | 1.The site was taken offline from 08:30 AM to 09:45 AM on 03/21 by technicians to collect transformer DGA samples. 2.The inverters are offline from 10:00AM to 10:45AM on 03/27 for preventive maintenance work. | 1.SR098816 2.PM6838
Palombo A | MA | 311627 | 346973.5 | -35346.5 | -10.19% | 363307 | -51680 | -14.22% | 1.Inverter A was offline from 09:20 AM to 10:15 AM on 03/03 due to technicians onsite to replace the keypad on Inverter A. | 1.SR091674
Palombo B | MA | 155141 | 156844.7 | -1703.7 | -1.086% | 147566.9 | 7574.1 | 5.133% | 1. As a part of preventive maintenenace inverter 2 combiner box 5 was offline from 10:45AM to 11:30AM. | 1. PM6958
St Josephs Church | MA | 148329 | 171214.8 | -22885.8 | -13.37% | 154094.2 | -5765.2 | -3.741% | 1.The site lost communication at 2:30PM on restored at 3:30PM on 03/13.
Sunset A | MA | 69604.5 | 85842.88 | -16238.38 | -18.92% | 66834.76 | 2769.74 | 4.144% | 1.During PM inspection site was taken offline by technician from 12:29 PM to 02:15 PM on 03/20 and on 03/18 durig PM event CBs were experienced tripping on and offline. | 1.PM6839
Sunset B | MA | 67082 | 73870.49 | -6788.49 | -9.19% | 66032.87 | 1049.13 | 1.589% | 1.During PM inspection site was taken offline by technician from 02:10 PM to 03:10 PM on 03/21. | 1.PM6886
Woodchuck | MA | 147618 | 156306.2 | -8688.2 | -5.558% | 162884.8 | -15266.8 | -9.373% | 1.The site was taken offline by technician from 10:45 to 12:15 on 03/20 to collect transformer DGA samples. 2. Inverters tripped offline from 12:45 to 13:00 on 03/10 for preventive maintenance work. | 1.SR098795 2.PM6970
NY: Skaneateles - Spafford 1 - (PW) | NY
NY: Skaneateles - Spafford 2 - (PW) | NY

## Apr
38 DN |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 4138952 | 4263880.91 | -124928.91 | -2.93% | 4272144.53 | -133192.53 | -3.118% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA | 199467.5 | 180569.8 | 18897.7 | 10.47% | 219710.8 | -20243.3 | -9.214% | 1.Inverter 25 stopped communicating at 10:00 AM PDT on 04/07. On 04/08, a technician replaced the DC board fan, which had been causing the inverter to overheat and trip offline. The inverter has been operating normally since the repair 2.Inverter 25 stopped communicating at 11:15 PDT AM on 04/12, and production couldn’t be verified. On 04/15, a technician reset the breaker, restoring production, and noted overheating due to warm weather, requiring breaker replacement. On 04/23, Inverter 25 and its breaker were replaced; PAD 2 was offline from 14:01 to 15:12 during the work. Inverter 25 is producing normally from 15:00 PDT on 04/23. | 1.SR099489 2.SR099734 | SR099734
Barton Acres | MA | 161773 | 171040.2 | -9267.2 | -5.418% | 162787.2 | -1014.2 | -0.623% | 1. Site tripped offline from 20:05 to 21:00 on 04/29 due to utility outage. 2.Inverter 2 tripped offline at 09:45AM on 04/30 and back online at 13:30 on the same day after technician re-energizing the inverter | 1.SR100677 2.SR100708 | SR100708
Bowden | MA | 331971 | 328461.6 | 3509.4 | 1.068% | 330949.5 | 1021.5 | 0.3087%
Blair Wire Village | MA | 163662 | 177911.3 | -14249.3 | -8.009% | 166260 | -2598 | -1.563%
Boutilier | MA | 463631 | 465714.9 | -2083.9 | -0.4475% | 446865.5 | 16765.5 | 3.752% | 1.Inverter 4 DC string 4 has tripped offline at 16:30 on 04/08. On 04/09, technician has reset the combiner box and it has resumed operation at 12:50PM. 2.Inverter 6 did not start due to a ground fault on 04/27. A technician reset the Ground Fault Breaker, and Inverter 6 was back online at 12:30PM on the same day. | 1.SR099544 2.SR100456 | SR100456
Cherry Valley | MA | 157223 | 172407.5 | -15184.5 | -8.807% | 163486 | -6263 | -3.831% | 1.Weather station stopped communicating at 22:45 on 04/04 and it regained communication at 06:30AM on 04/05 issue got self resolved | 1.SR099440
Cohasse | MA | 151432 | 158349.1 | -6917.1 | -4.368% | 172569 | -21137 | -12.25% | 1.Site was offline from 04:15AM to 7:45AM on 04/20 due to utility outage. | 1.SR100031
ISM Dighton Solar 2 | MA | 336156 | 327997.9 | 8158.1 | 2.487% | 337271.4 | -1115.4 | -0.3307% | 1. SEL Relay 1 and the production meter stopped communicating at 12:30PM on 04/16, although SEL Relay 2 voltages remained available. Technicians visited the site and restored communication by resetting the DAS equipment. However, they found that Inverter 2 had not started production on 04/16. Power Electronics remotely diagnosed the issue and re-energized the inverter. Inverter 2 was back online at 17:20 EST the same day. | 1.SR099860, SR099891 | SR099891
Dudley River 1 | MA | 163432 | 165933.1 | -2501.1 | -1.507% | 166674.3 | -3242.3 | -1.945% | 1.The site tripped offline at 1:00AM on 04/11 due to four utility poles being knocked down in an accident at the intersection of Chestnut and East Main Street. Power was restored and the site came back online at 2:30AM the same day. | 1.SR099671
Dudley River 2 | MA | 157704 | 164615.3 | -6911.3 | -4.198% | 160600.9 | -2896.9 | -1.804% | 1.The site tripped offline at 1:00AM on 04/11 due to four utility poles being knocked down in an accident at the intersection of Chestnut and East Main Street. Power was restored and the site came back online at 2:30AM the same day. | 1.SR099669
Dudley River 3 | MA | 162557 | 164852.1 | -2295.1 | -1.392% | 162431.4 | 125.6 | 0.07732% | 1.The site tripped offline at 1:00 AM on 04/11 due to four utility poles being knocked down in an accident at the intersection of Chestnut and East Main Street. Power was restored and the site came back online at 14:30 AM the same day. | 1.SR099670
Flint Pond | MA | 79734 | 73305.09 | 6428.91 | 8.77% | 77715.95 | 2018.05 | 2.597%
Incom | MA | 337911 | 382456.3 | -44545.3 | -11.65% | 346956.7 | -9045.7 | -2.607% | 1. Site was taken offline from 07:15AM to 09:00AM on 04/04 due to technician checked in to collect DGA samples. | 1.SR099381
JH | MA | 156348 | 166290.3 |  | 0% | 170416.9 | -14068.9 | -8.256%
Ledeaux | MA | 147299 | 154599.8 | -7300.8 | -4.722% | 165182.4 | -17883.4 | -10.83% | 1.Inverters and relay lost communication in both PowerTrack and Locus at 13:30 on 04/11. Later, AlsoEnergy remotely pushed data via the Aquisuite, updated the firmware, and successfully backfilled the missing data. | 1.SR099675
Palombo A | MA | 331617 | 350277 | -18660 | -5.327% | 361541 | -29924 | -8.277% | 1.Inverter D derated by approximately 220KW compared to its peers on 04/10. On 04/11 technician checked in and RMA'D DMGI of inverter D. | 1.SR099667
Palombo B | MA | 164726 | 150219.5 | 14506.5 | 9.657% | 169314.7 | -4588.7 | -2.71% | 1.The site tripped offline at 12:30PM on 04/10 and was restored at 17:00 on the same day after a technician reset the SEL relay. | 1.SR099654
St Josephs Church | MA | 157361 | 173444 | -16083 | -9.273% | 164666.3 | -7305.3 | -4.436% | 1.Site was taken offline from 9:30AM to 10:30AMon 04/04 due to technician checked in to collect DGA samples. | 1.SR099382
Sunset A | MA | 79692.5 | 87744.1 | -8051.6 | -9.176% | 76642.34 | 3050.16 | 3.98%
Sunset B | MA | 75645 | 80108.52 | -4463.52 | -5.572% | 75721.84 | -76.84 | -0.1015%
Woodchuck | MA | 159610 | 167583.5 | -7973.5 | -4.758% | 174380.4 | -14770.4 | -8.47%
NY: Skaneateles - Spafford 1 - (PW) | NY
NY: Skaneateles - Spafford 2 - (PW) | NY

## May
38 DN |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 3947879.25 | 3982334.16 | -34454.91 | -0.8652% | 4962356.52 | -1014477.27 | -20.44% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA | 225966 | 243463.2 | -17497.2 | -7.187% | 259128.8 | -33162.8 | -12.8% | 1. Inverter 19 was offline from 11:30 on 05/21. The technician later power cycled the inverter, and it came back online at 11:00 on 05/28. 2. The site tripped offline at 01:00 on 05/01, and meter voltages dropped to 0. The site came back online at 06:00 on 05/01 after IEUA reset the breaker. | 1.SR101805 2.SR100801 | SR100801
Barton Acres | MA | 159221 | 152419.1 | 6801.9 | 4.463% | 196293.4 | -37072.4 | -18.89% | 1. Inverter 1 CB1 tripped offline at 12:37 on 05/07. The technician later power-cycled CB1, and it came back online at 15:45 on 05/07. | 1. SR101118
Bowden | MA | 318831 | 316793.3 | 2037.7 | 0.6432% | 383114.2 | -64283.2 | -16.78% | 1. Site production was low on 05/05, 05/06, 05/09, 05/15, 05/21, 05/22, 05/25, 05/29 and 05/31.
Blair Wire Village | MA | 148953 | 158461.1 | -9508.1 | -6% | 192216.8 | -43263.8 | -22.51% | 1.The meter has not been capturing full inverter production since 10:30 on 05/11 due to a drop in Phase C voltage. Later, the technician found that Line C to ground was reading 100V, compared to Lines A and B at 120V. However, the issue was not present while the technician was on-site. The meter started capturing full production again from 14:00 on 05/12. | 1. SR101288
Boutilier | MA | 431151 | 419276.1 | 11874.9 | 2.832% | 538844.9 | -107693.9 | -19.99% | 1. Site production was low on 05/05, 05/06, 05/09, 05/15, 05/21, 05/22, 05/25, 05/29 and 05/31.
Cherry Valley | MA | 141723 | 152648 | -10925 | -7.157% | 194395 | -52672 | -27.1% | 1. Site production was low on 05/05, 05/06, 05/09, 05/15, 05/21, 05/22, 05/25, 05/29 and 05/31.
Cohasse | MA | 141805 | 139695.5 | 2109.5 | 1.51% | 192755.8 | -50950.8 | -26.43% | 1. Site production was low on 05/05, 05/06, 05/09, 05/15, 05/21, 05/22, 05/25, 05/29 and 05/31.
ISM Dighton Solar 2 | MA | 343730 | 336698.1 | 7031.9 | 2.088% | 394456.8 | -50726.8 | -12.86% | 1. The planned site outage has started at 09:00 on 05/08. The technician was able to close the recloser, and the site came back online at 09:15 on 05/09. 2. The site tripped offline at 17:50 on 05/31 and later came back online via remote reset at 18:35 on the same day. | 1. SR100570 2. SR102227 | SR102227
Dudley River 1 | MA | 153538 | 156975.9 | -3437.9 | -2.19% | 193593.9 | -40055.9 | -20.69% | 1. Site production was low on 05/05, 05/06, 05/09, 05/15, 05/21, 05/22, 05/25, 05/29 and 05/31.
Dudley River 2 | MA | 148601 | 152438.5 | -3837.5 | -2.517% | 184610.2 | -36009.2 | -19.51% | 1. Site production was low on 05/05, 05/06, 05/09, 05/15, 05/21, 05/22, 05/25, 05/29 and 05/31.
Dudley River 3 | MA | 152932 | 152896 | 36 | 0.02355% | 187114.1 | -34182.1 | -18.27% | 1. Site production was low on 05/05, 05/06, 05/09, 05/15, 05/21, 05/22, 05/25, 05/29 and 05/31.
Flint Pond | MA | 74546.5 | 61311.65 | 13234.85 | 21.59% | 92665.36 | -18118.86 | -19.55% | 1. Site production was low on 05/05, 05/06, 05/09, 05/21, 05/22, 05/23, and 05/31 due to rain.
Incom | MA | 328694 | 338334.8 | -9640.8 | -2.849% | 394560.1 | -65866.1 | -16.69% | 1. Site production was low on 05/05, 05/06, 05/09, 05/22, 05/29, and 05/31 due to rain.
JH | MA | 143890 | 147015.5 | -3125.5 | -2.126% | 191735.3 | -47845.3 | -24.95% | 1. Site production was low on 05/04, 05/05, 05/06, 05/09, 05/10, 05/15, 05/21, 05/22, 05/25 and 05/31 due to rain.
Ledeaux | MA | 133678 | 142273.1 | -8595.1 | -6.041% | 188253.6 | -54575.6 | -28.99% | 1. Inverter 1 CB3 tripped offline at 12:15 on 05/02. Later, the technician found an arc fault on Inverter 1 CB3, cleared the fault, and re-energized CB3. It came back online at 17:00 on 05/02. | 1. SR100927
Palombo A | MA | 307732 | 313557.9 | -5825.9 | -1.858% | 398271 | -90539 | -22.73% | 1. Technician performed an overall inspection on the inverter D and concluded the replacement of DGMI’s is not necessary on 05/21.While on site technician has taken inverter C was offline from 09:15 to 13:45 and inverter D was offline from 09:15 to 13:30. | 1. SR099667
Palombo B | MA | 156009 | 132398.3 | 23610.7 | 17.83% | 204302.2 | -48293.2 | -23.64% | 1. Site production was low on 05/05, 05/06, 05/09, 05/15, 05/21, 05/22, 05/29, and 05/31 due to rain.
St Josephs Church | MA | 149532 | 161092.5 | -11560.5 | -7.176% | 190363.2 | -40831.2 | -21.45% | 1. Site production was low on 05/05, 05/06, 05/09, 05/15, 05/21, 05/22, 05/29, and 05/31 due to rain.
Sunset A | MA | 70981 | 74200.91 | -3219.91 | -4.339% | 92417.78 | -21436.78 | -23.2% | 1. The planned site outage has started at 05:00 on 05/28, and the site auto-reclosed at 20:45 on the same day. | 1. SR101411
Sunset B | MA | 67294.75 | 74837.5 | -7542.75 | -10.08% | 91307.58 | -24012.83 | -26.3% | 1. The planned site outage commenced at 05:00 on 05/28, and the site auto-reclosed at 20:45 on the same day. 2. Combiner Box 5 tripped offline at 09:30 on 05/19. Later, the technician found that the arc card had faulted and power-cycled the combiner box. It came back online at 16:45 on 05/19. | 1. SR101412 2. SR101678 | SR101678
Woodchuck | MA | 149071 | 155547.2 | -6476.2 | -4.163% | 201956.5 | -52885.5 | -26.19% | 1. Site production was low on 05/05, 05/06, 05/09, 05/15, 05/21, 05/22, 05/29, and 05/31 due to rain.
NY: Skaneateles - Spafford 1 - (PW) | NY
NY: Skaneateles - Spafford 2 - (PW) | NY

## Jun
38 DN |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 4571344.25 | 4549014.59 | 22329.66 | 0.4909% | 4978078.48 | -406734.23 | -8.171% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA | 245374.5 | 289807.6 | -44433.1 | -15.33% | 244402.8 | 971.7 | 0.3976% | 1. Inverter 7 is offline at 10:15 on 06/15 and back online at 10:15 on 06/16 2.Pyranometer may have an issue. It is reporting lower irradiance than previous years (635 vs 815 W/m^2 in 2024), and there appears to be shading on the pyranometer in the late afternoon, which was not present last year. See 3/19 - 3/21 in 2025. | 1. SR103000 2.SR101179 | SR101179
Barton Acres | MA | 190917 | 176595 | 14322 | 8.11% | 198844.4 | -7927.4 | -3.987%
Bowden | MA | 360324 | 357450.4 | 2873.6 | 0.8039% | 395795.4 | -35471.4 | -8.962% | 1. Site was offline at 7:30 on 06/15 and later came back online at 15:30 on 06/15 2. Site has tripped offline at 01:15am on 06/27 and came back online at 9:00am on 06/28 | 1. SR102992 2. SR103675 | SR103675
Blair Wire Village | MA | 187217 | 183591 | 3626 | 1.975% | 197786.1 | -10569.1 | -5.344%
Boutilier | MA | 528352 | 483548.6 | 44803.4 | 9.266% | 545847 | -17495 | -3.205%
Cherry Valley | MA | 173827 | 168103.1 | 5723.9 | 3.405% | 195979 | -22152 | -11.3% | 1.Site production was low due to low irradiance on 06/14 ,06/26 ,06/28
Cohasse | MA | 154224 | 156332.3 | -2108.3 | -1.349% | 188506.7 | -34282.7 | -18.19% | 1. Site was offline from 10:00 on 06/11 to 12:00 on 06/12. 2. The site was offline from 17:00 to 20:00 on 06/18, and again from 11:00 on 06/19 to 08:00 on 06/20. | 1. SR102823 2. SR103158 | SR103158
ISM Dighton Solar 2 | MA | 351761 | 357698 | -5937 | -1.66% | 403822.8 | -52061.8 | -12.89% | 1. Site was offline from 08:00 to 15:15 on 06/02. 2. Site was offline from 08:15 to 09:30 on 06/20. 3. The site was offline from 07:15 on 06/21 to 11:15 on 06/22, and again from 17:45 on 06/23 to 16:45 on 06/24. | 1. SR102227 2. SR103204 3. SR103261 | SR103204 | SR103261
Dudley River 1 | MA | 181176 | 184928.1 | -3752.1 | -2.029% | 198867.9 | -17691.9 | -8.896% | 1. Site was offline from 07:00 to 07:30 on 06/21. 2. Site was offline from 12:00 to 14:45 on 06/24 due to utility outage 3. On 06/03 string BCB 2-12 AND 2-17 were identified as offline while inspecting through Aerial Thermal Flight and on 06/12 technician replaced the fuse. | 1. SR103251 2. SR103392 3. SR102789 | SR103392 | SR102789
Dudley River 2 | MA | 173249 | 175723.6 | -2474.6 | -1.408% | 189441 | -16192 | -8.547% | 1. Site was offline from 07:00 to 07:30 on 06/21. 2. Site was offline from 12:00 to 14:45 on 06/24 due to utility outage 3. On 06/03 string A3-3 was identified as offline while inspecting through Aerial Thermal Flight and on 06/12 technician replaced the fuse. | 1. SR103252 2. SR103393 3. SR102790 | SR103393 | SR102790
Dudley River 3 | MA | 174798 | 172964.7 | 1833.3 | 1.06% | 192136.3 | -17338.3 | -9.024% | 1. Site was offline from 07:00 to 13:00 on 06/21. 2. Site was offline from 12:00 to 14:45 on 06/24 due to utility outage. | 1. SR103253 2. SR103394 | SR103394
Flint Pond | MA | 88251.5 | 66839.61 | 21411.89 | 32.03% | 93165.71 | -4914.21 | -5.275% | 1. Site was taken offline by technician from 08:30 to 09:00 on 06/10 to take measurements for the new transformer | 1. SR101999
Incom | MA | 334433 | 404636.4 | -70203.4 | -17.35% | 391718.8 | -57285.8 | -14.62% | 1. Site was offline from 11:00 on 06/05 to 18:00 on 06/06 and was offline again from 13:00 on 06/06 to 09:00 on 06/07. 2. The site was offline from 09:00 to 12:00 on 06/12. It was offline again from 12:15 on 06/12 to 14:00 on 06/13, and once more from 15:00 on 06/13 to 10:30 on 06/14. Additionally, S3 took the site offline from 07:00 to 12:00 on 06/16 to replace the recloser. | 1. SR102523 2. SR102822 | SR102822
JH | MA | 175221 | 168234.1 |  | 0% | 186860.1 | -11639.1 | -6.229%
Ledeaux | MA | 162163 | 167495.9 | -5332.9 | -3.184% | 186134.2 | -23971.2 | -12.88% | 1.Site production was low due to low on 06/14 ,06/26 ,06/28 due to rain and cloudy weather
Palombo A | MA | 363537 | 345885.9 | 17651.1 | 5.103% | 385946 | -22409 | -5.806%
Palombo B | MA | 183655 | 145910.9 | 37744.1 | 25.87% | 206959 | -23304 | -11.26% | 1.Site production was low due to low irradiance on 06/14 ,06/26 ,06/28 due to rain cloudy weather
St Josephs Church | MA | 181562 | 184787.7 | -3225.7 | -1.746% | 188982.5 | -7420.5 | -3.927%
Sunset A | MA | 91355.5 | 88961.75 | 2393.75 | 2.691% | 93618.76 | -2263.26 | -2.418% | 1. Site was offline from 13:00 on 06/26 to 08:15 on 06/27 due to utility outage. | 1. SR103612
Sunset B | MA | 87409.75 | 87316.63 | 93.12 | 0.1066% | 92494.41 | -5084.66 | -5.497% | 1. Site was offline from 13:00 on 06/26 to 08:15 on 06/27 due to utility outage. | 1. SR103613
Woodchuck | MA | 182537 | 182203.3 | 333.7 | 0.1831% | 200769.6 | -18232.6 | -9.081%
NY: Skaneateles - Spafford 1 - (PW) | NY
NY: Skaneateles - Spafford 2 - (PW) | NY

## Jul
` |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 4912958.3655 | 5024810.28 | -111851.9145 | -2.226% | 5182490.44 | -269532.0745 | -5.201% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA | 234169.5 | 312097.4 | -77927.9 | -24.97% | 257170.4 | -23000.9 | -8.944% | 1.Inverter 20 started late for production at 14:00 on 07/21. On 07/22 inverter didn't started and after troubleshooting inverter was RMA'd. It will remain offline until new inverter is installed. 2. The Weather station issue resolved from 07/07. 3. Site tripped offline at 22:30 on 07/09 and back online on 07/10. 4. Site was offline from 09:00 to 10:00 on 07/02 | 1.SR104709 ,SR104853 2.SR101179 3. SR104233 4. PM9812 | SR104853 | SR101179 | SR104233
Barton Acres | MA | 209385 | 204943 | 4442 | 2.167% | 208831.7 | 553.3 | 0.265%
Bowden | MA | 408592 | 408907 | -315 | -0.07703% | 401558.8 | 7033.2 | 1.751%
Blair Wire Village | MA | 198811 | 204815 | -6004 | -2.931% | 200918.6 | -2107.6 | -1.049%
Boutilier | MA | 512437 | 481743.3 | 30693.7 | 6.371% | 573267.5 | -60830.5 | -10.61% | 1. Site tripped offline at 15:45 on 07/06 due to thermal event in transformer. On 07/10 site came back online at 14:15 | 1.SR104057
Cherry Valley | MA | 186515 | 200754.6 | -14239.6 | -7.093% | 206366 | -19851 | -9.619%
Cohasse | MA | 167868 | 175389.2 | -7521.2 | -4.288% | 201682.1 | -33814.1 | -16.77% | 1. Site tripped offline at 13:45 on 07/06 and came back online at 07:45 on 07/07 2. Site tripped offline at 12:45 on 07/10 and came back online at 07:00 on 07/12 and again offline from 10:00 to 13:00 on the same day. 3. Site relay voltages dropped to zero at 23:00 on 07/31 and remains offline. | 1. SR104052 2.SR104273 3. SR105462 | SR104273 | SR105462
ISM Dighton Solar 2 | MA | 409896 | 384861 | 25035 | 6.505% | 392181.9 | 17714.1 | 4.517%
Dudley River 1 | MA | 187132 | 202130.7 | -14998.7 | -7.42% | 202485.3 | -15353.3 | -7.582%
Dudley River 2 | MA | 178623 | 189672.6 | -11049.6 | -5.826% | 191961 | -13338 | -6.948%
Dudley River 3 | MA | 185910 | 192454.4 | -6544.4 | -3.4% | 194847.6 | -8937.6 | -4.587%
Flint Pond | MA | 94335.5 | 74175.81 | 20159.69 | 27.18% | 97673.53 | -3338.03 | -3.418% | 1. Actual vs expected delta is showing 27% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years).
Incom | MA | 403132.3655 | 445338.3 | -42205.9345 | -9.477% | 414404.6 | -11272.2345 | -2.72%
JH | MA | 188280 | 187932.8 | 347.2 | 0.1847% | 200943.9 | -12663.9 | -6.302%
Ledeaux | MA | 172741 | 188240.8 | -15499.8 | -8.234% | 197102.8 | -24361.8 | -12.36% | 1Inverter A started late for production at 08:45 on 07/02 and again at 08:00 on 07/06 due to a soft shutdown alert. On 07/07, a technician replaced the LCD board for Inverter A. 2.Inverter A tripped offline at 17:15 and reporting Soft Shutdown and it came back online at 09:45 on 07/15. | 1. SR103873 2.SR104423 | SR104423
Palombo A | MA | 397496 | 395713 | 1783 | 0.4506% | 414569 | -17073 | -4.118%
Palombo B | MA | 200219 | 167285.3 | 32933.7 | 19.69% | 217414.8 | -17195.8 | -7.909% | 1. Actual vs expected delta is showing 20% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years).
St Josephs Church | MA | 192599 | 206949.6 | -14350.6 | -6.934% | 200648 | -8049 | -4.012%
Sunset A | MA | 97775 | 101365.5 | -3590.5 | -3.542% | 98321.17 | -546.17 | -0.5555%
Sunset B | MA | 92987 | 97092.97 | -4105.97 | -4.229% | 97139.84 | -4152.84 | -4.275%
Woodchuck | MA | 194055 | 202948 | -8893 | -4.382% | 213001.9 | -18946.9 | -8.895%
NY: Skaneateles - Spafford 1 - (PW) | NY
NY: Skaneateles - Spafford 2 - (PW) | NY

## Aug
38 DN |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 6933643.9059 | 7154439.45 | -220795.5441 | -3.086% | 6449563.64 | 484080.2659 | 7.506%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA | 193219 | 252341.3 | -59122.3 | -23.43% | 263153.9 | -69934.9 | -26.58% | 1. Site was offline from 04:00 on 08/20 to 08:30 on 08/20. 2. Meter 2 reported 0 production from 12:00 on 08/12 to 09:00 on 08/14. 3. Inverter 20 was offline from 14:00 on 07/21 to 13:00 on 08/08. | 1. SR106576 2. SR106228 3. SR104853 | SR106228 | SR104853
Barton Acres | MA | 210415 | 211632.1 | -1217.1 | -0.5751% | 185479 | 24936 | 13.44%
Bowden | MA | 418110 | 414692.5 | 3417.5 | 0.8241% | 390151.3 | 27958.7 | 7.166%
Blair Wire Village | MA | 204637 | 218762.5 | -14125.5 | -6.457% | 196160.3 | 8476.7 | 4.321% | 1. Site was offline from 12:00 to 15:00 on 08/16. | 1. SR106381
Boutilier | MA | 581210 | 555218.6 | 25991.4 | 4.681% | 509160 | 72050 | 14.15%
Cherry Valley | MA | 192315 | 212173.5 | -19858.5 | -9.36% | 176281.9 | 16033.1 | 9.095%
Cohasse | MA | 185210 | 190609.2 | -5399.2 | -2.833% | 186586 | -1376 | -0.7375% | 1. Site was taken offline by technician for relay replacement on 08/14 from 07:00 to 09:00. and again was taken offline from 05:00 to 09:00 on 08/16. 2. Site was offline from 22:00 on 07/31 to 09:00 on 08/01. | 1. SR106309 2. SR105462 | SR105462
ISM Dighton Solar 2 | MA | 437547 | 418995.7 | 18551.3 | 4.428% | 385800 | 51747 | 13.41%
Dudley River 1 | MA | 201912 | 216798.5 | -14886.5 | -6.867% | 197241.9 | 4670.1 | 2.368% | 1. Site was offline from 08:00 to 13:45 on 08/29 2. Inverter 1 combiner box 5 was offline from 12:30 on 08/26 to 06:45 on 08/27 | 1. SR107176 2. SR106969 | SR106969
Dudley River 2 | MA | 194598 | 203452 | -8854 | -4.352% | 188128.3 | 6469.7 | 3.439% | 1. Site was offline from 08:00 to 14:00 on 08/29 | 1. SR107177
Dudley River 3 | MA | 202054 | 201967.2 | 86.8 | 0.04298% | 190532.8 | 11521.2 | 6.047% | 1. Site was offline from 08:00 to 13:45 on 08/29 | 1. SR107178
Flint Pond | MA | 98249.5 | 84236.23 | 14013.27 | 16.64% | 86843 | 11406.5 | 13.13% | 1. Actual vs expected delta is showing 17% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years).
Incom | MA | 428711.4059 | 465042.8 | -36331.3941 | -7.812% | 392355 | 36356.4059 | 9.266%
JH | MA | 191399 | 199109.4 |  | 0% | 182844.8 | 8554.2 | 4.678%
Ledeaux | MA | 175701 | 190747 | -15046 | -7.888% | 179142.6 | -3441.6 | -1.921%
Palombo A | MA | 405362 | 416657.6 | -11295.6 | -2.711% | 372566.8 | 32795.2 | 8.803%
Palombo B | MA | 205084 | 169768.9 | 35315.1 | 20.8% | 187850.3 | 17233.7 | 9.174% | 1. Actual vs expected delta is showing 21% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years).
St Josephs Church | MA | 200171 | 218554.5 | -18383.5 | -8.411% | 184626 | 15545 | 8.42%
Sunset A | MA | 99406.5 | 106835.9 | -7429.4 | -6.954% | 87326 | 12080.5 | 13.83%
Sunset B | MA | 91922.5 | 97218.01 | -5295.51 | -5.447% | 83989.54 | 7932.96 | 9.445% | 1. inverter power limited to 200kw on 8/24 and resolved at 06:00 on 08/25. | 1. SR106816
Woodchuck | MA | 201062 | 209795.5 | -8733.5 | -4.163% | 190594.2 | 10467.8 | 5.492%
NY: Skaneateles - Spafford 1 - (PW) | NY | 1277259 | 1420077.971 | -142818.971 | -10.06% | 1147250 | 130009 | 11.33% | 1. Trackers 1, 4, 117, 129, & 132 were stuck for whole month. | 1. SR104836
NY: Skaneateles - Spafford 2 - (PW) | NY | 538089 | 479752.539 | 58336.461 | 12.16% | 485500 | 52589 | 10.83% | 1. Site was offline from 09:15 on 08/13 to 10:15 on 08/14 2. Weather station(POA) has been reporting continuous fluctuations around midday, indicating inconsistent readings. | 1. SR106230 2.SR107733 | SR107733

## Sep
38 DN |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 5715879 | 6057369.336 | -341490.336 | -5.638% | 5244385.185 | 471493.815 | 8.99%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA | 171236.5 | 179333.565 | -8097.065 | -4.515% | 222866.272 | -51629.772 | -23.17% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance
Barton Acres | MA | 176379 | 188788.91 | -12409.91 | -6.573% | 139048.036 | 37330.964 | 26.85% | 1. 1. The plant is performing as expected. The forecasted (theoretical) values may appear lower and they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance.
Bowden | MA | 346738 | 349313.01 | -2575.01 | -0.7372% | 320457.344 | 26280.656 | 8.201%
Blair Wire Village | MA | 163787 | 194618.229 | -30831.229 | -15.84% | 160870.164 | 2916.836 | 1.813% | 1. Site was offline from 08:00 on 09/17 to 10:00 on 09/18. 2. Inverter A was derated to 230 kW from 09:30 to 16:00 on 09/10 | 1. SR108112 2. SR107776 | SR107776
Boutilier | MA | 469696 | 443385.315 | 26310.685 | 5.934% | 381718.37 | 87977.63 | 23.05% | 1. The plant is performing as expected. The forecasted (theoretical) values may appear lower and they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance.
Cherry Valley | MA | 158153 | 187345.776 | -29192.776 | -15.58% | 139229.435 | 18923.565 | 13.59% | 1. Site production was low on 09/07, 09/24 and 09/25 due to rain.
Cohasse | MA | 153079 | 170736.576 | -17657.576 | -10.34% | 161965.406 | -8886.406 | -5.487% | 1. Site production was low on 09/07, 09/24 and 09/25 due to rain.
ISM Dighton Solar 2 | MA | 326503 | 315813.885 | 10689.115 | 3.385% | 328174.37 | -1671.37 | -0.5093% | 1. Inverter 1 was offline from 07:15 to 17:15 on 09/12. | 1. SR107896
Dudley River 1 | MA | 165539 | 179197.723 | -13658.723 | -7.622% | 161174.918 | 4364.082 | 2.708% | 1. Site was offline from 16:00 on 09/07 to 12:00 on 09/08. | 1. SR107582
Dudley River 2 | MA | 160471 | 170232.676 | -9761.676 | -5.734% | 154250.033 | 6220.967 | 4.033% | 1. Site was offline from 16:00 on 09/07 to 12:00 on 09/08. | 1. SR107583
Dudley River 3 | MA | 167208 | 169195.879 | -1987.879 | -1.175% | 156362.763 | 10845.237 | 6.936% | 1. Site was offline from 16:00 on 09/07 to 12:00 on 09/08. | 1. SR107584
Flint Pond | MA | 77757 | 75944.65 | 1812.35 | 2.386% | 65435.44 | 12321.56 | 18.83% | 1. The plant is performing as expected. The forecasted (theoretical) values may appear lower and they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance.
Incom | MA | 356107 | 372062.614 | -15955.614 | -4.288% | 325222.52 | 30884.48 | 9.496%
JH | MA | 156903 | 174459.088 | -17556.088 | -10.06% | 156485.18 | 417.82 | 0.267% | 1. Inverter 1 has morning shading, and Inverter 2 has evening shading. | 1. SR109126
Ledeaux | MA | 141401 | 158004.859 | -16603.859 | -10.51% | 150494.636 | -9093.636 | -6.042% | 1. Inverters experiecing intermittent communication issue throughout the month, production can be verified at meter level. 2. Site production was low on 09/07, 09/24 and 09/25 due to rain. | 1. SR107564
Palombo A | MA | 326707 | 358740.238 | -32033.238 | -8.929% | 329256.62 | -2549.62 | -0.7744%
Palombo B | MA | 163751 | 157473.557 | 6277.443 | 3.986% | 144480.54 | 19270.46 | 13.34% | 1. The plant is performing as expected. The forecasted (theoretical) values may appear lower and they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance.
St Josephs Church | MA | 162141 | 187084.508 | -24943.508 | -13.33% | 148071.668 | 14069.332 | 9.502% | 1. Meter loosing communications intermittently, production can be verified at inverter level. 2. Site production was low on 09/07, 09/24 and 09/25 due to rain. | 1. SR107537
Sunset A | MA | 81326 | 93899.039 | -12573.039 | -13.39% | 65442.268 | 15883.732 | 24.27% | Site production was low on 09/07, 09/24 and 09/25 due to rain.
Sunset B | MA | 73730.5 | 80879.938 | -7149.438 | -8.84% | 64661.038 | 9069.462 | 14.03% | 1. Inverter was derated to 215kW from 09:45 to 15:00 on 09/27. | 1. SR108677
Woodchuck | MA | 161829 | 175616.691 | -13787.691 | -7.851% | 156594.644 | 5234.356 | 3.343% | 1. Site was offline from 08:00 to 15:00 on 09/17. | 1. SR108114
NY: Skaneateles - Spafford 1 - (PW) | NY | 1077611 | 1222796.61 | -145185.61 | -11.87% | 923309.9 | 154301.1 | 16.71% | 1. Trackers 1, 4, 117, 129, & 132 were stuck from 09/01 to 09/12. | 1. SR104836
NY: Skaneateles - Spafford 2 - (PW) | NY | 477826 | 452446 | 25380 | 5.61% | 388813.62 | 89012.38 | 22.89% | 1. 4 trackers were stuck: #9, 12, 42, & 52 for whole month. 2. Inverter 1 was offline from 12:37 to 13:47 on 09/26. | 1. SR108532 2. SR108617 | SR108617

## Oct
38 DN |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 4417664 | 4797647.1 | -379983.1 | -7.92% | 4095476.81 | 322187.19 | 7.867%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
6th St. | CA | 171602.5 | 141683.8 | 29918.7 | 21.12% | 192586.1 | -20983.6 | -10.9% | 1.The following optimizers are not communicating and appear to be causing inverter underperformance: Inv 04 - 4.0.1320, 4.0.1445 Inv 05 - 5.0.1328, 5.0.1346 Inv 14 - 14.0.1670 Inv 18 - 18.0.1521 Inv 28 - 28.0.480 Inv 29 - 29.0.143 Inv 32 - 32.0.887 Inv 33 - 33.0.654, 33.0.658, 33.0.682, 33.0.683 Inv 35 - 35.0.12, 35.0.31 | 1. SR104098 | 1.Workin progress
Barton Acres | MA | 140201 | 164881.6 | -24680.6 | -14.97% | 107955 | 32246 | 29.87% | 1. Inverter 2 is derating at ~220kW from 08:45 on 10/04 and module temperature 1 has increased. | 1. SR109022 | 1.Closed
Bowden | MA | 284791 | 290333.7 | -5542.7 | -1.909% | 278624.8 | 6166.2 | 2.213%
Blair Wire Village | MA | 136576 | 167899.1 | -31323.1 | -18.66% | 141623 | -5047 | -3.564% | 1. Inverter 2 has afternoon to evening shading.
Boutilier | MA | 364750 | 364100.3 | 649.7 | 0.1784% | 296348 | 68402 | 23.08% | 1.Site was offline from 10:15 to 13:30 on 10/09 and again site was offline from 13:30 to 14:30 on 10/10 | 1. SR108726 | 1.Closed
Cherry Valley | MA | 126274 | 163396.5 | -37122.5 | -22.72% | 112291 | 13983 | 12.45% | 1. On 10/27, the technician was on site performing a PM inspection. During the inspection, Inverter A CB 1 was taken offline from 12:00 to 16:00, and String 20 was offline from 10/25 to 10/27. 2. Inverter b has afternoon to evening shading. | 1. PM9962, | 1. work in progress
Cohasse | MA | 123322 | 152374.2 | -29052.2 | -19.07% | 146622.7 | -23300.7 | -15.89% | 1. Inverter 1 CB 5 and inverter 2 CB 5 had afternoon shading
ISM Dighton Solar 2 | MA | 234265 | 172451.2 | 61813.8 | 35.84% | 293983.8 | -59718.8 | -20.31% | 1.Site was offline at 09:00 on 10/06 and it came back online at 13:15 on 10/11 2.- Weather Station stopped communicating on 10/18 at 11:21. It came back online at 13:00 on 10/21 | 1. SR108614 2. SR109670 | 1.Closed 2.Pending | SR109670
Dudley River 1 | MA | 137922 | 146667.2 | -8745.2 | -5.963% | 141755.3 | -3833.3 | -2.704%
Dudley River 2 | MA | 136613 | 141217.6 | -4604.6 | -3.261% | 135884.9 | 728.1 | 0.5358%
Dudley River 3 | MA | 142552 | 142459.4 | 92.6 | 0.065% | 137903 | 4649 | 3.371%
Flint Pond | MA | 56787 | 71036.8 | -14249.8 | -20.06% | 51326.95 | 5460.05 | 10.64% | 1.Site tripped offline from 09:15 to 13:15 on 10/17 2.Inverter tripped offline from 13:00 to 13:00 on 10/22 due to technician was on site | 1.SR109627 2.SR109642 | 1.Closed 2.Closed | SR109642
Incom | MA | 295019 | 316079.3 | -21060.3 | -6.663% | 290262.1 | 4756.9 | 1.639%
JH | MA | 119957 | 157787.6 |  | 0% | 138297.4 | -18340.4 | -13.26% | 1.Site tripped offline at 15:00 on 10/01 and it came back online at 11:00 on 10/02 2. Inverter 1 has morning shading, and Inverter 2 has evening shading. 3.Site offline from 07:30 to 09:30 on 10/08 | 1.SR108848 2.SR109126 3.SR109174 | 1.Closed 2.Closed 3.Closed | SR109126 | SR109174
Ledeaux | MA | 109159 | 126984.2 | -17825.2 | -14.04% | 131904 | -22745 | -17.24% | 1.Site offline 07:30 to 09:30 on 10/08 | 1.SR109175 | 1.Closed
Palombo A | MA | 270200 | 315407.2 | -45207.2 | -14.33% | 304052.2 | -33852.2 | -11.13% | 1. Inverter D has evening shading and inverter B has morning shading.
Palombo B | MA | 130946 | 147132.4 | -16186.4 | -11% | 112005.7 | 18940.3 | 16.91% | 1. Inverter A has eveing shading.
St Josephs Church | MA | 135129 | 167277.42 | -32148.42 | -19.22% | 124168.25 | 10960.75 | 8.827% | 1. Inverter 1 was taken offline from 10:30 to 11:45 and inverter 2 was taken offline from 08:00 to 10:45 on 10/22 during PM. | 1. PM9703 | 1. Completed
Sunset A | MA | 64199 | 80640.23 | -16441.23 | -20.39% | 50825.05 | 13373.95 | 26.31% | 1. Inverter 1 CB 4 has afternoon to evening shading.
Sunset B | MA | 57748.5 | 64409.45 | -6660.95 | -10.34% | 50216.16 | 7532.34 | 15% | 1. Inverter 1 CB 3 has heavy afternoon to evening shading
Woodchuck | MA | 128337 | 143953.7 | -15616.7 | -10.85% | 132718.2 | -4381.2 | -3.301% | 1. Inverter 2 CB 5 has heavy shading troughot the day.
NY: Skaneateles - Spafford 1 - (PW) | NY | 726817 | 859927.8 | -133110.8 | -15.48% | 512680 | 214137 | 41.77% | 1.Tracker 60 not operating: Terrasmart deploying resources on site, tentatively end of this week. 2. EV Solar checked in to test inverters , remotely turning them on and off on 10/03 3.Inverter 1 trippeed offline at 13:30 on 10/20 and it came back online at 08:45 on 10/22 4.Site tripped offline from 12:30 to 13:45 on 10/25 | 1. SR108528 2.SR108950 3.SR109750 4.SR109982 | 1.Pending 2.Closed 3.Closed | SR108950 | SR109750 | SR109982
NY: Skaneateles - Spafford 2 - (PW) | NY | 324497 | 299546.4 | 24950.6 | 8.329% | 211443.2 | 113053.8 | 53.47% | 1.Site tripped offline from 12:30 to 13:45 on 10/25 2. EV Solar checked in to test inverters , remotely turning them on and off on 10/03 | 1. SR109983 2.SR108950 | 1.Closed 2.Closed | SR108950

## Nov
38 DN |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA
Barton Acres | MA
Bowden | MA
Blair Wire Village | MA
Boutilier | MA
Cherry Valley | MA
Cohasse | MA
ISM Dighton Solar 2 | MA
Dudley River 1 | MA
Dudley River 2 | MA
Dudley River 3 | MA
Flint Pond | MA
Incom | MA
JH | MA
Ledeaux | MA
Palombo A | MA
Palombo B | MA
St Josephs Church | MA
Sunset A | MA
Sunset B | MA
Woodchuck | MA
NY: Skaneateles - Spafford 1 - (PW) | NY
NY: Skaneateles - Spafford 2 - (PW) | NY

## Dec
38 DN |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA
Barton Acres | MA
Bowden | MA
Blair Wire Village | MA
Boutilier | MA
Cherry Valley | MA
Cohasse | MA
ISM Dighton Solar 2 | MA
Dudley River 1 | MA
Dudley River 2 | MA
Dudley River 3 | MA
Flint Pond | MA
Incom | MA
JH | MA
Ledeaux | MA
Palombo A | MA
Palombo B | MA
St Josephs Church | MA
Sunset A | MA
Sunset B | MA
Woodchuck | MA
NY: Skaneateles - Spafford 1 - (PW) | NY
NY: Skaneateles - Spafford 2 - (PW) | NY

## Sites
Portfolio: | 38 DN
Site DAS Name | Site | State | Update | DAS
6th St. | 6th St. | CA | AEF | PowerTrack
Barton Acres | Barton Acres | MA | AEF | PowerTrack
Bowden | Bowden | MA | AEF | PowerTrack
Blair Wire Village | Blair Wire Village | MA | AEF | PowerTrack
Boutilier | Boutilier | MA | AEF | PowerTrack
Cherry Valley | Cherry Valley | MA | AEF | PowerTrack
Cohasse | Cohasse | MA | AEF | PowerTrack
ISM Dighton Solar 2 | ISM Dighton Solar 2 | MA | AEF | PowerTrack
Dudley River 1 | Dudley River 1 | MA | AEF | PowerTrack
Dudley River 2 | Dudley River 2 | MA | AEF | PowerTrack
Dudley River 3 | Dudley River 3 | MA | AEF | PowerTrack
Flint Pond | Flint Pond | MA | AEF | PowerTrack
Incom | Incom | MA | AEF | PowerTrack
JH | JH | MA | AEF | PowerTrack
Ledeaux | Ledeaux | MA | AEF | PowerTrack
Palombo A | Palombo A | MA | AEF | PowerTrack
Palombo B | Palombo B | MA | AEF | PowerTrack
St Josephs Church | St Josephs Church | MA |  | PowerTrack
Sunset A | Sunset A | MA | AEF | PowerTrack
Sunset B | Sunset B | MA | AEF | PowerTrack
Woodchuck | Woodchuck | MA | AEF | PowerTrack
Spafford 1 - Rose Hill Road Solar 1 LLC | NY: Skaneateles - Spafford 1 - (PW) | NY | AEF | PowerTrack
Spafford 2 - Rose Hill Road Solar 2 LLC | NY: Skaneateles - Spafford 2 - (PW) | NY | AEF | PowerTrack