## Year to Date
CITI |  |  | PPA Modeled Output | Production VS Acual | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 21102732.68 | 21577439.69 | 97.8% | 21357069.923 | -254337.243 | -1.191% | 24272019.215 | -3169286.535 | -13.06%
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | %
CA: Antioch Deer Valley - Citi | CA | 607047.75 | 595934.74 | 101.9% | 599937.293 | 7110.457 | 1.185% | 609568.532 | -2520.782 | -0.4135%
CA: Antioch MC CUP - Citi | CA | 2031041 | 2014158.18 | 100.8% | 2028906.725 | 2134.275 | 0.1052% | 2082625.994 | -51584.994 | -2.477%
CA: Clovis - Citi | CA | 842368.07 | 843752 | 99.84% | 529678.263 | 312689.807 | 59.03% | 645790.365 | 196577.705 | 30.44%
CA: Elk Grove MOB - Citi | CA | 1304493.5 | 1368843 | 95.3% | 1363712.875 | -59219.375 | -4.343% | 1402691.003 | -98197.503 | -7.001%
CA: Elk Grove Promenade - Citi | CA | 696714 | 730618.5 | 95.36% | 711615.171 | -14901.171 | -2.094% | 751600.739 | -54886.739 | -7.303%
CA: Fresno Sequioa - Citi | CA | 1361766.5 | 1428247.56 | 95.35% | 1420484.409 | -58717.909 | -4.134% | 1464816.109 | -103049.609 | -7.035%
CA: Fresno MOB - Citi | CA | 515830.63 | 576213.88 | 89.52% | 551530.867 | -35700.237 | -6.473% | 562657.724 | -46827.094 | -8.322%
CA: Modesto Bangs - Citi | CA | 330909.38 | 388853.72 | 85.1% | 257573.893 | 73335.487 | 28.47% | 303554.415 | 27354.965 | 9.012%
CA: Napa Data Center - Citi | CA | 353572.5 | 412452.29 | 85.72% | 459177.486 | -105604.986 | -23% | 410899.181 | -57326.681 | -13.95%
CA: Petaluma MOB - Citi | CA | 764448 | 955072.5 | 80.04% | 723168.762 | 41279.238 | 5.708% | 747982.416 | 16465.584 | 2.201%
CA: Pleasanton Tec Ctr - Citi | CA | 1149752 | 1331789.36 | 86.33% | 1276124.625 | -126372.625 | -9.903% | 1343245.484 | -193493.484 | -14.4%
CA: Rancho Cordova - Citi | CA | 1882427.36 | 1925493.78 | 97.76% | 1880389.867 | 2037.493 | 0.1084% | 2022188.169 | -139760.809 | -6.911%
CA: S Sacramento Wyndham - Citi | CA | 1034209.78 | 1183651.69 | 87.37% | 1100793.414 | -66583.634 | -6.049% | 1204181.951 | -169972.171 | -14.12%
CA: Sacramento Point West - Citi | CA | 2079806.98 | 2265283.9 | 91.81% | 2185642.034 | -105835.054 | -4.842% | 2375340.607 | -295533.627 | -12.44%
CA: San Jose FHC - Citi | CA | 398940.75 | 462636.35 | 86.23% | 452367.164 | -53426.414 | -11.81% | 472622.872 | -73682.122 | -15.59%
CA: San Jose MOB - Citi | CA | 676202.07 | 740235.84 | 91.35% | 699238.901 | -23036.831 | -3.295% | 752902.579 | -76700.509 | -10.19%
CA: Selma - Citi | CA | 372294.06 | 427972.96 | 86.99% | 420539.169 | -48245.109 | -11.47% | 451752.149 | -79458.089 | -17.59%
CA: Vacaville Hospital | CA | 2005139.67 | 2982440.44 | 67.23% | 3024242.161 | -1019102.491 | -33.7% | 3170921.897 | -1165782.227 | -36.76%
CA: Manteca - KP Manteca Hospital | CA | 782652.63 | 943789 | 82.93% | 817017.826 | -34365.196 | -4.206% | 927381.776 | -144729.146 | -15.61%
Sacramento - KP South Sacramento HSP | CA | 1913116.05 | 0 | #DIV/0! | 854929.018 | 1058187.032 | 123.8% | 2569295.253 | -656179.203 | -25.54%

## 1st Qtr
CITI |  |  | PPA Modeled Output | Production VS Acual | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 4011350.76 | 4010868.14 | 100% | 3987723.821 | 23626.939 | 0.5925% | 4290441.327 | -279090.567 | -6.505%
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | %
CA: Antioch Deer Valley - Citi | CA | 114367.75 | 115399.63 | 99.11% | 114257 | 110.75 | 0.09693% | 117533.717 | -3165.967 | -2.694%
CA: Antioch MC CUP - Citi | CA | 407599 | 382684.3 | 106.5% | 378862 | 28737 | 7.585% | 426400.31 | -18801.31 | -4.409%
CA: Clovis - Citi | CA | 169263.25 | 152182.5 | 111.2% | 146927 | 22336.25 | 15.2% | 131624.31 | 37638.94 | 28.6%
CA: Elk Grove MOB - Citi | CA | 253724 | 246151.5 | 103.1% | 243714 | 10010 | 4.107% | 270600.8 | -16876.8 | -6.237%
CA: Elk Grove Promenade - Citi | CA | 138337 | 134028.5 | 103.2% | 132731.356 | 5605.644 | 4.223% | 151578.198 | -13241.198 | -8.736%
CA: Fresno Sequioa - Citi | CA | 267893 | 267133.21 | 100.3% | 264542 | 3351 | 1.267% | 300633.3 | -32740.3 | -10.89%
CA: Fresno MOB - Citi | CA | 102206.13 | 107787.71 | 94.82% | 107041 | -4834.87 | -4.517% | 108339.676 | -6133.546 | -5.661%
CA: Modesto Bangs - Citi | CA | 68432.75 | 63424.51 | 107.9% | 63171 | 5261.75 | 8.329% | 70099.062 | -1666.312 | -2.377%
CA: Napa Data Center - Citi | CA | 69031.88 | 78540.47 | 87.89% | 75905 | -6873.12 | -9.055% | 82484.785 | -13452.905 | -16.31%
CA: Petaluma MOB - Citi | CA | 162762.5 | 180900.23 | 89.97% | 174082 | -11319.5 | -6.502% | 174722.89 | -11960.39 | -6.845%
CA: Pleasanton Tec Ctr - Citi | CA | 229990.5 | 252333.64 | 91.15% | 249546 | -19555.5 | -7.836% | 262865.856 | -32875.356 | -12.51%
CA: Rancho Cordova - Citi | CA | 427880 | 377789.61 | 113.3% | 373634 | 54246 | 14.52% | 445759.21 | -17879.21 | -4.011%
CA: S Sacramento Wyndham - Citi | CA | 212055 | 211985.13 | 100% | 209458 | 2597 | 1.24% | 213255.123 | -1200.123 | -0.5628%
CA: Sacramento Point West - Citi | CA | 405840 | 404736.4 | 100.3% | 402651 | 3189 | 0.792% | 453841.26 | -48001.26 | -10.58%
CA: San Jose FHC - Citi | CA | 78955.5 | 90592.39 | 87.15% | 92852 | -13896.5 | -14.97% | 92874.624 | -13919.124 | -14.99%
CA: San Jose MOB - Citi | CA | 115879.25 | 146703.06 | 78.99% | 147955 | -32075.75 | -21.68% | 149689.114 | -33809.864 | -22.59%
CA: Selma - Citi | CA | 82293.5 | 77199.57 | 106.6% | 76362 | 5931.5 | 7.768% | 93408.791 | -11115.291 | -11.9%
CA: Vacaville Hospital | CA | 519252.25 | 553199.78 | 93.86% | 551443 | -32190.75 | -5.838% | 552775.637 | -33523.387 | -6.065%
CA: Manteca - KP Manteca Hospital | CA | 185587.5 | 168096 | 110.4% | 182590.465 | 2997.035 |  | 191954.664 | -6367.164 | -3.317%
Sacramento - KP South Sacramento HSP | CA

## 2nd Qtr
CITI |  |  | PPA Modeled Output | Production VS Acual | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 8281607.71 | 7975892.55 | 103.8% | 7665622.548 | 615985.162 | 8.036% | 8826489.48 | -544881.77 | -6.173%
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | %
CA: Antioch Deer Valley - Citi | CA | 231100.75 | 216346.11 | 106.8% | 220131 | 10969.75 | 4.983% | 229737.815 | 1362.935 | 0.5933%
CA: Antioch MC CUP - Citi | CA | 759648 | 737990.88 | 102.9% | 753268 | 6380 | 0.847% | 771667.684 | -12019.684 | -1.558%
CA: Clovis - Citi | CA | 314798.25 | 319928.5 | 98.4% | 201995 | 112803.25 | 55.84% | 134885.361 | 179912.889 | 133.4%
CA: Elk Grove MOB - Citi | CA | 488764.5 | 508752.5 | 96.07% | 511707 | -22942.5 | -4.484% | 522169.203 | -33404.703 | -6.397%
CA: Elk Grove Promenade - Citi | CA | 264966 | 268413 | 98.72% | 267177.633 | -2211.633 | -0.8278% | 273996.955 | -9030.955 | -3.296%
CA: Fresno Sequioa - Citi | CA | 516338 | 530010.35 | 97.42% | 532329 | -15991 | -3.004% | 538945.809 | -22607.809 | -4.195%
CA: Fresno MOB - Citi | CA | 188291.37 | 214895.17 | 87.62% | 214658 | -26366.63 | -12.28% | 200642.048 | -12350.678 | -6.156%
CA: Modesto Bangs - Citi | CA | 131376.88 | 153672.21 | 85.49% | 98493 | 32883.88 | 33.39% | 62537.353 | 68839.527 | 110.1%
CA: Napa Data Center - Citi | CA | 135351.37 | 153580.82 | 88.13% | 151677 | -16325.63 | -10.76% | 154637.396 | -19286.026 | -12.47%
CA: Petaluma MOB - Citi | CA | 305358.5 | 353186.27 | 86.46% | 231715 | 73643.5 | 31.78% | 174401.526 | 130956.974 | 75.09%
CA: Pleasanton Tec Ctr - Citi | CA | 414645.5 | 489521.72 | 84.7% | 493407 | -78761.5 | -15.96% | 495720.628 | -81075.128 | -16.36%
CA: Rancho Cordova - Citi | CA | 693218 | 678501.17 | 102.2% | 691844 | 1374 | 0.1986% | 712662.477 | -19444.477 | -2.728%
CA: S Sacramento Wyndham - Citi | CA | 394459.5 | 441074.56 | 89.43% | 428966 | -34506.5 | -8.044% | 432826.634 | -38367.134 | -8.864%
CA: Sacramento Point West - Citi | CA | 802124 | 842401.5 | 95.22% | 844998 | -42874 | -5.074% | 868540.301 | -66416.301 | -7.647%
CA: San Jose FHC - Citi | CA | 151713.5 | 167415.96 | 90.62% | 169629 | -17915.5 | -10.56% | 170017.248 | -18303.748 | -10.77%
CA: San Jose MOB - Citi | CA | 234883 | 265727.78 | 88.39% | 271100 | -36217 | -13.36% | 275756.74 | -40873.74 | -14.82%
CA: Selma - Citi | CA | 148096.5 | 162742.39 | 91% | 163395 | -15298.5 | -9.363% | 164229.568 | -16133.068 | -9.823%
CA: Vacaville Hospital | CA | 926498.25 | 1109686.66 | 83.49% | 1153144 | -226645.75 | -19.65% | 1203220.881 | -276722.631 | -23%
CA: Manteca - KP Manteca Hospital | CA | 225844.25 | 362045 | 62.38% | 265988.915 | -40144.665 | -15.09% | 301048.853 | -75204.603 | -24.98%
Sacramento - KP South Sacramento HSP | CA | 954131.59 | 0 |  | 0 | 954131.59 |  | 1138845 | -184713.41 | -16.22%

## 3rd Qtr
CITI |  |  | PPA Modeled Output | Production VS Acual | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 7165779.26 | 7850811 | 91.27% | 7934631.57 | -768852.31 | -9.69% | 8905756.125 | -1739976.865 | -19.54%
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | %
CA: Antioch Deer Valley - Citi | CA | 213439.75 | 215398 | 99.09% | 215815.471 | -2375.721 | -1.101% | 213742 | -302.25 | -0.1414%
CA: Antioch MC CUP - Citi | CA | 704779 | 732026 | 96.28% | 734468.746 | -29689.746 | -4.042% | 724714 | -19935 | -2.751%
CA: Clovis - Citi | CA | 284783 | 303873 | 93.72% | 113620.539 | 171162.461 | 150.6% | 293381 | -8598 | -2.931%
CA: Elk Grove MOB - Citi | CA | 461498 | 506237 | 91.16% | 505327.22 | -43829.22 | -8.673% | 502741 | -41243 | -8.204%
CA: Elk Grove Promenade - Citi | CA | 238397.75 | 269083 | 88.6% | 254437.558 | -16039.808 | -6.304% | 267218.086 | -28820.336 | -10.79%
CA: Fresno Sequioa - Citi | CA | 467821.5 | 509820 | 91.76% | 509125.442 | -41303.942 | -8.113% | 504875 | -37053.5 | -7.339%
CA: Fresno MOB - Citi | CA | 183237.88 | 204972 | 89.4% | 185174.053 | -1936.173 | -1.046% | 205219 | -21981.12 | -10.71%
CA: Modesto Bangs - Citi | CA | 107974.25 | 140504 | 76.85% | 69396.679 | 38577.571 | 55.59% | 139818 | -31843.75 | -22.78%
CA: Napa Data Center - Citi | CA | 123767.75 | 147673 | 83.81% | 186048.542 | -62280.792 | -33.48% | 142169 | -18401.25 | -12.94%
CA: Petaluma MOB - Citi | CA | 253999 | 345890 | 73.43% | 257129.762 | -3130.762 | -1.218% | 332853 | -78854 | -23.69%
CA: Pleasanton Tec Ctr - Citi | CA | 407958.5 | 485068 | 84.1% | 431869.797 | -23911.297 | -5.537% | 480567 | -72608.5 | -15.11%
CA: Rancho Cordova - Citi | CA | 611986 | 697236 | 87.77% | 689583.264 | -77597.264 | -11.25% | 693063 | -81077 | -11.7%
CA: S Sacramento Wyndham - Citi | CA | 353104 | 438015 | 80.61% | 384673.093 | -31569.093 | -8.207% | 434991 | -81887 | -18.82%
CA: Sacramento Point West - Citi | CA | 693080 | 839782 | 82.53% | 789406.455 | -96326.455 | -12.2% | 832599 | -139519 | -16.76%
CA: San Jose FHC - Citi | CA | 137568.25 | 167296 | 82.23% | 154293.859 | -16725.609 | -10.84% | 171468 | -33899.75 | -19.77%
CA: San Jose MOB - Citi | CA | 215929.75 | 266797 | 80.93% | 242061.346 | -26131.596 | -10.8% | 269073 | -53143.25 | -19.75%
CA: Selma - Citi | CA | 127535.87 | 153772 | 82.94% | 152910.02 | -25374.15 | -16.59% | 152724 | -25188.13 | -16.49%
CA: Vacaville Hospital | CA | 518760.25 | 1082113 | 47.94% | 1093980.992 | -575220.742 | -52.58% | 1068170 | -549409.75 | -51.43%
CA: Manteca - KP Manteca Hospital | CA | 302855.5 | 345256 | 87.72% | 301886.336 | 969.164 | 0.321% | 338437.039 | -35581.539 | -10.51%
Sacramento - KP South Sacramento HSP | CA | 757303.26 | 0 |  | 663422.396 | 93880.864 | 14.15% | 1137934 | -380630.74 | -33.45%

## 4th Qtr
CITI |  |  | PPA Modeled Output | Production VS Acual | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 1643994.95 | 1739868 | 94.49% | 1739868 | -95873.05 | -5.51% | -125097.034 | 1769091.984 | -1414%
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | %
CA: Antioch Deer Valley - Citi | CA | 48139.5 | 48791 | 98.66% | 49733.822 | -1594.322 | -3.206% | 48555 | -415.5 | -0.8557%
CA: Antioch MC CUP - Citi | CA | 159015 | 161457 | 0.98488 | 162307.979 | -3292.979 | -2.029% | 159844 | -829 | -0.5186%
CA: Clovis - Citi | CA | 73523.57 | 67768 | 108.5% | 67135.724 | 6387.846 | 9.515% | 85899.694 | -12376.124 | -14.41%
CA: Elk Grove MOB - Citi | CA | 100507 | 107702 | 0.9332 | 102964.655 | -2457.655 | -2.387% | 107180 | -6673 | -6.226%
CA: Elk Grove Promenade - Citi | CA | 55013.25 | 59094 | 93.09% | 57268.624 | -2255.374 | -3.938% | 58807.5 | -3794.25 | -6.452%
CA: Fresno Sequioa - Citi | CA | 109714 | 121284 | 0.9046 | 114487.967 | -4773.967 | -4.17% | 120362 | -10648 | -8.847%
CA: Fresno MOB - Citi | CA | 42095.25 | 48559 | 86.69% | 44657.814 | -2562.564 | -5.738% | 48457 | -6361.75 | -13.13%
CA: Modesto Bangs - Citi | CA | 23125.5 | 31253 | 0.73994 | 26513.214 | -3387.714 | -12.78% | 31100 | -7974.5 | -25.64%
CA: Napa Data Center - Citi | CA | 25421.5 | 32658 | 77.84% | 45546.944 | -20125.444 | -44.19% | 31608 | -6186.5 | -19.57%
CA: Petaluma MOB - Citi | CA | 42328 | 75096 | 0.56365 | 60242 | -17914 | -29.74% | 66005 | -23677 | -35.87%
CA: Pleasanton Tec Ctr - Citi | CA | 97157.5 | 104866 | 92.65% | 101301.828 | -4144.328 | -4.091% | 104092 | -6934.5 | -6.662%
CA: Rancho Cordova - Citi | CA | 149343.36 | 171967 | 0.86844 | 125328.603 | 24014.757 | 19.16% | 170703.482 | -21360.122 | -12.51%
CA: S Sacramento Wyndham - Citi | CA | 74591.28 | 92577 | 80.57% | 77696.321 | -3105.041 | -3.996% | 123109.194 | -48517.914 | -39.41%
CA: Sacramento Point West - Citi | CA | 178762.98 | 178364 | 1.0022 | 148586.579 | 30176.401 | 20.31% | 220360.046 | -41597.066 | -18.88%
CA: San Jose FHC - Citi | CA | 30703.5 | 37332 | 82.24% | 35592.305 | -4888.805 | -13.74% | 38263 | -7559.5 | -19.76%
CA: San Jose MOB - Citi | CA | 109510.07 | 61008 | 1.795 | 38122.555 | 71387.515 | 187.3% | 58383.725 | 51126.345 | 87.57%
CA: Selma - Citi | CA | 14368.19 | 34259 | 41.94% | 27872.149 | -13503.959 | -48.45% | 41389.79 | -27021.6 | -65.29%
CA: Vacaville Hospital | CA | 40628.92 | 237441 | 0.17111 | 225674.169 | -185045.249 | -82% | 346755.379 | -306126.459 | -88.28%
CA: Manteca - KP Manteca Hospital | CA | 68365.38 | 68392 | 99.96% | 66552.11 | 1813.27 | 2.725% | 95941.22 | -27575.84 | -28.74%
Sacramento - KP South Sacramento HSP | CA | 201681.2 | 0 |  | 191506.622 | 10174.578 | 5.313% | 292516.253 | -90835.053 | -31.05%

## Jan
CITI |  |  | PPA Modeled Output | Production VS Acual | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 1141760.88 | 909254.01 | 125.6% | 911851.348 | 229909.532 | 25.21% | 1228093.936 | -86333.056 | -7.03% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA | 35199.75 | 26934.83 | 130.7% | 26668 | 8531.75 | 31.99% | 36723.827 | -1524.077 | -4.15%
CA: Antioch MC CUP - Citi | CA | 107451 | 88103.5 | 122% | 87223 | 20228 | 23.19% | 116934.996 | -9483.996 | -8.11%
CA: Clovis - Citi | CA | 47404.25 | 30338 | 156.3% | 29290 | 18114.25 | 61.84% | 48625.771 | -1221.521 | -2.512% | 1.Inverter 1 tripped offline at 19:45 on 01/27 due to an arc protection fault and remained offline for through out the month. | 1.SR096073
CA: Elk Grove MOB - Citi | CA | 70088 | 55258.5 | 126.8% | 54711 | 15377 | 28.11% | 76608 | -6520 | -8.511%
CA: Elk Grove Promenade - Citi | CA | 39878 | 30505 | 130.7% | 30232.711 | 9645.289 | 31.9% | 44081.56 | -4203.56 | -9.536%
CA: Fresno Sequioa - Citi | CA | 72064.5 | 54436.21 | 132.4% | 53908 | 18156.5 | 33.68% | 83519.138 | -11454.638 | -13.71% | 1.Inverter 2 tripped offline at 18:35 on 12/31/24 due to an arc protection fault. The technician cleared the fault and re-energized the inverter, bringing it back online at 12:10 on 01/03/25. Inverter 2 again tripped offline at 18:45 on 01/07/25 and was being RMA'D. | 1.SR095212,SR095408 | SR095408
CA: Fresno MOB - Citi | CA | 30119.5 | 21917.91 | 137.4% | 21759 | 8360.5 | 38.42% | 33751.72 | -3632.22 | -10.76% | 1.Inverter 5's arc board is being RMA'd to prevent recurring trips. On 01/22, the technician installed the arc board, and then Inverter 5 is producing usually. | 1.SR095363
CA: Modesto Bangs - Citi | CA | 18323.25 | 12108.41 | 151.3% | 12105 | 6218.25 | 51.37% | 18407 | -83.75 | -0.455%
CA: Napa Data Center - Citi | CA | 18167.75 | 18607.37 | 97.64% | 18005 | 162.75 | 0.9039% | 22393.513 | -4225.763 | -18.87% | 1.Inverters 1, 2, 3, 5 and 6 experienced multiple tripping events. On 01/29, the technician arrived and found all inverters producing. Six new strings were installed for inverters 2, 3, and 5 to prevent further insulation faults. | 1.SR093544,SR094968 | SR094968
CA: Petaluma MOB - Citi | CA | 42798.5 | 45402.4 | 94.26% | 43691 | -892.5 | -2.043% | 42214.46 | 584.04 | 1.384% | 1.When the technician was on site to troubleshot Inverter 2 for its previous trip event on 12/17/24, he identified that it was underperforming and initiated an RMA. Inverter 2 has been in RMA since 01/03/25. | 1.SR094669,SR095487 | SR095487
CA: Pleasanton Tec Ctr - Citi | CA | 60053.5 | 61177.84 | 98.16% | 60279 | -225.5 | -0.3741% | 72294.92 | -12241.42 | -16.93% | 1.Inverter 9 tripped offline at 10:10 AM on 01/16/25 and self-resolved, Invereter 9 was back online at 08:30 PM on the same day. | 1.SR095637
CA: Rancho Cordova - Citi | CA | 138722 | 89789.61 | 154.5% | 88802 | 49920 | 56.21% | 146135.825 | -7413.825 | -5.073%
CA: S Sacramento Wyndham - Citi | CA | 61514 | 47416.43 | 129.7% | 46851 | 14663 | 31.3% | 56726.753 | 4787.247 | 8.439%
CA: Sacramento Point West - Citi | CA | 116857 | 90698.8 | 128.8% | 90230 | 26627 | 29.51% | 132201.526 | -15344.526 | -11.61%
CA: San Jose FHC - Citi | CA | 20174.5 | 22811.79 | 88.44% | 23381 | -3206.5 | -13.71% | 25499.26 | -5324.76 | -20.88% | 1.Meter current phase B is 10 amps lower than A and C and further troubleshooting will be needed. | 1.SR092732 , SR094546 | SR094546
CA: San Jose MOB - Citi | CA | 30984.25 | 37719.66 | 82.14% | 38042 | -7057.75 | -18.55% | 41140.37 | -10156.12 | -24.69% | 1.Inverter 1 has a history of multiple tripings and technician set the inverter to isolation mode and reenergized it. Then inverter 1 started producing as expected from 01/02. | 1.SR093725
CA: Selma - Citi | CA | 22758.75 | 15404.17 | 147.7% | 15194 | 7564.75 | 49.79% | 26945.834 | -4187.084 | -15.54%
CA: Vacaville Hospital | CA | 158667 | 130650.58 | 121.4% | 130413 | 28254 | 21.67% | 151623.242 | 7043.758 | 4.646%
CA: Manteca - KP Manteca Hospital | CA | 50535.38 | 29973 | 168.6% | 41066.637 | 9468.743 | 23.06% | 52266.221 | -1730.841 | -3.312%
Sacramento - KP South Sacramento HSP | CA

## Feb
CITI |  |  | PPA Modeled Output | Production VS Acual | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 1161890.88 | 1192644.33 | 97.42% | 1191822.5 | -29931.62 | -2.511% | 1241928.529 | -80037.649 | -6.445% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA | 32720 | 33837.7 | 96.7% | 33503 | -783 | -2.337% | 33108.406 | -388.406 | -1.173% | 1.The site offline on 02/26 at 12:45. On 02/28, a technician checked in and reported a blown fuse and reenergized the site. | 1.SR097891
CA: Antioch MC CUP - Citi | CA | 117003 | 111655.8 | 104.8% | 110541 | 6462 | 5.846% | 121440.242 | -4437.242 | -3.654%
CA: Clovis - Citi | CA | 49039.75 | 46787.5 | 104.8% | 45172 | 3867.75 | 8.562% | 45847.381 | 3192.369 | 6.963% | 1. Inverter 1 tripped offline at 16:45 from 01/27 due to arc protection fault and back online at 09:30 on 02/05. | 1.SR096073
CA: Elk Grove MOB - Citi | CA | 73432 | 74269 | 98.87% | 73534 | -102 | -0.1387% | 77096.73 | -3664.73 | -4.753%
CA: Elk Grove Promenade - Citi | CA | 39950 | 40582 | 98.44% | 40180.25 | -230.25 | -0.573% | 43579.704 | -3629.704 | -8.329%
CA: Fresno Sequioa - Citi | CA | 78020.5 | 83831.7 | 93.07% | 83019 | -4998.5 | -6.021% | 87819.042 | -9798.542 | -11.16% | 1. Inverter 2 tripped offline at 18:45 on 01/07 due to an arc protection fault and was RMA'd on 02/17. | 1.SR095408
CA: Fresno MOB - Citi | CA | 29859.88 | 33738.1 | 88.5% | 33456 | -3596.12 | -10.75% | 29656.131 | 203.749 | 0.687% | 1. Inverter 7 tripped offline at 19:35 on 02/14 due to an isolation fault and is now under RMA'd. | 1. SR097152
CA: Modesto Bangs - Citi | CA | 19801.5 | 20447.6 | 96.84% | 20348 | -546.5 | -2.686% | 20554.278 | -752.778 | -3.662%
CA: Napa Data Center - Citi | CA | 20347.88 | 22694.3 | 89.66% | 21965 | -1617.12 | -7.362% | 23987.7 | -3639.82 | -15.17% | 1. Inverter 1 tripped offline at 07:00 AM on 02/01 and back online at 16:55 on 02/02. It tripped offline again at 07:00 AM on 02/13 and back online at 12:40 on 02/14 due to an isolation fault. 2. Inverter 5 tripped offline at 07:00AM on 02/25 and back online at 16:55 on 02/25. | 1. SR096910 2. SR097715 | SR097715
CA: Petaluma MOB - Citi | CA | 45669.5 | 52699.23 | 86.66% | 50713 | -5043.5 | -9.945% | 52104.259 | -6434.759 | -12.35% | 1. When the technician was on site to troubleshot Inverter 2 for its previous trip event on 12/17/24, he identified that it was underperforming and initiated an RMA. Inverter 2 has been in RMA since 01/03/25. Inverter produced normally on 2/26 technician swapped with new inverter. 2.Inverter 14 has experienced multiple tripping events since 02/09 and is reporting 'PV abnormal input.' On 02/19, the technician removed the jumper bus bar and switched the input mode to 'independent' as per Chint's request, and it resumed normal operation. 3.Inverter 13 has reoccurring late starts, reporting insulation resistance low. This inverter has a history. On 02/26 technician swapped with new inverter and produced normallly. | 1. SR094669,SR095487 2. SR096553 3. SR92736 , SR095488 | SR095487 | SR096553 | SR92736 | SR095488
CA: Pleasanton Tec Ctr - Citi | CA | 64678 | 71770 | 90.12% | 70963 | -6285 | -8.857% | 73511.443 | -8833.443 | -12.02%
CA: Rancho Cordova - Citi | CA | 123056 | 116944 | 105.2% | 115658 | 7398 | 6.396% | 126414.863 | -3358.863 | -2.657%
CA: S Sacramento Wyndham - Citi | CA | 62431 | 63883.2 | 97.73% | 63122 | -691 | -1.095% | 61291.02 | 1139.98 | 1.86%
CA: Sacramento Point West - Citi | CA | 117073 | 122199 | 95.81% | 121584 | -4511 | -3.71% | 131537.929 | -14464.929 | -11% | 1. Inverter 5.4 tripped offline at 10:30 AM on 02/22 due to ARC protection and water in the wire box, so a new wire box is needed for replacement to get back the inverter. | 1. SR097653
CA: San Jose FHC - Citi | CA | 21935.75 | 25812.8 | 84.98% | 26457 | -4521.25 | -17.09% | 26911.372 | -4975.622 | -18.49% | 1.Meter current phase B is 10 amps lower than A and C and further troubleshooting will be needed. 2. The site was offline from 12:05 to 13:35 on 02/28 due to the technician being on site to work on the solar system. | 1. SR092732 , SR094546 2. SR094546 | SR094546 | SR094546
CA: San Jose MOB - Citi | CA | 34046.5 | 41783.9 | 81.48% | 42140 | -8093.5 | -19.21% | 43555.535 | -9509.035 | -21.83% | 1. Inverter 10 has a multiple tripings from 02/27 and technician set the inverter to isolation mode and reenergized it. 2. Inverter 2 is derating by 6 kW, likely due to overheating, and is now under RMA'd. 3. Inverter 12 may have a string down (~3 kW), and inverter 8 may have several strings down (~13 kW). | 1. SR097893 2. SR097777 3. SR097778 | SR097777 | SR097778
CA: Selma - Citi | CA | 23596.12 | 23766.7 | 99.28% | 23523 | 73.12 | 0.3108% | 27065.457 | -3469.337 | -12.82%
CA: Vacaville Hospital | CA | 157387 | 157634.8 | 99.84% | 157886 | -499 | -0.3161% | 160526.898 | -3139.898 | -1.956%
CA: Manteca - KP Manteca Hospital | CA | 51843.5 | 48307 | 107.3% | 58058.25 | -6214.75 | -10.7% | 55920.139 | -4076.639 | -7.29%
Sacramento - KP South Sacramento HSP | CA

## Mar
CITI |  |  | PPA Modeled Output | Production VS Acual | Q1 Production Vs PPA | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 1707699 | 1908969.8 | 89.46% | 99.25% | 1884049.973 | -176350.973 | -9.36% | 1820418.862 | -112719.862 | -6.192% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual |  |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA | 46448 | 54627.1 | 85.03% | 99.11% | 54086 | -7638 | -14.12% | 47701.484 | -1253.484 | -2.628% | 1.Site was ofline from 03:45 pm on 02/26 to 11:50 am on 03/07. On 03/07 a technician has checked in site and they replaced the blown fuse and reenergized the site. | 1.SR097891
CA: Antioch MC CUP - Citi | CA | 183145 | 182925 | 100.1% | 106.5% | 181098 | 2047 | 1.13% | 188025.072 | -4880.072 | -2.595%
CA: Clovis - Citi | CA | 72819.25 | 75057 | 97.02% | 111.2% | 72465 | 354.25 | 0.4889% | 37151.158 | 35668.092 | 96.01% | 1.Inverter 1 is being RMA'D from 02/25 due to its communication and tripping issues.On 03/19,technician swapped the powerhead on inverter 1 .Inverter 1 is back online after technician troubleshoot the inverter. Additionally, technician completed Preventative Maintenance Inspection for the day (PM8554). 2. The weather station has been reporting erroneous values. Its graph shows continuous fluctuations throughout the day, indicating inconsistent readings. 3. The forecasted energy values are too low for the site. | 1.SR096008 2. SR099622 | SR099622
CA: Elk Grove MOB - Citi | CA | 110204 | 116624 | 94.5% | 103.1% | 115469 | -5265 | -4.56% | 116896.07 | -6692.07 | -5.725%
CA: Elk Grove Promenade - Citi | CA | 58509 | 62941.5 | 92.96% | 103.2% | 62318.395 | -3809.395 | -6.113% | 63916.934 | -5407.934 | -8.461% | 1. Inverter 1.4 is underperforming by 3 kW and is in independent mode | 1.SR099434
CA: Fresno Sequioa - Citi | CA | 117808 | 128865.3 | 91.42% | 100.3% | 127615 | -9807 | -7.685% | 129295.12 | -11487.12 | -8.884% | 1.Inverter 2 was being RMA'D from 02/17 due to repeated Arc Protection Faults causing it to drop offline.On 03/28, a technician has replaced Inverter 2 and it is online and producing from 01:00 pm on 03/28. | 1.SR095408
CA: Fresno MOB - Citi | CA | 42226.75 | 52131.7 | 81% | 94.82% | 51826 | -9599.25 | -18.52% | 44931.825 | -2705.075 | -6.02% | 1.Inverter 7 is being RMA'D from 02/17.On 03/25 technicians checked into the site and mentioned that Inverter 7 required further troubleshooting, as it was only producing about 3 kW. An technician later returned to replace Inverter 7, which is back online at 12:25pm on 03/25 and inverter 7 is underperforming by 30 kW from 03/25. | 1.SR097152, SR099432 | SR099432
CA: Modesto Bangs - Citi | CA | 30308 | 30868.5 | 98.18% | 107.9% | 30718 | -410 | -1.335% | 31137.784 | -829.784 | -2.665%
CA: Napa Data Center - Citi | CA | 30516.25 | 37238.8 | 81.95% | 87.89% | 35935 | -5418.75 | -15.08% | 36103.572 | -5587.322 | -15.48% | 1.Inverter 5 has experienced multiple tripping events throughout the month due to an insulation fault. 2. Inverters 1 and 2 tripped offline at 07:00 AM on 03/17 due to 'Insulation Resistance Low' and later self-resolved at 14:55 on 03/17. | 1. SR097715 2. SR098674 | SR098674
CA: Petaluma MOB - Citi | CA | 74294.5 | 82798.6 | 89.73% | 89.97% | 79678 | -5383.5 | -6.757% | 80404.171 | -6109.671 | -7.599% | 1. The phase B and C CTs of the meter have each been 40 amps lower than the phase A CT Since 03/21. There is a 5% variance between the meter and total inverter power. After the technician swapped the phase A and B CTs, it was confirmed to be a CT issue and need to be replace. Additionally, the meter has been reporting negative values since 03/27. | 1.SR098872, SR099542 | SR099542
CA: Pleasanton Tec Ctr - Citi | CA | 105259 | 119385.8 | 88.17% | 91.15% | 118304 | -13045 | -11.03% | 117059.493 | -11800.493 | -10.08% | 1. Inverter 3 tripped offline at 18:20 on 03/31 and reporting Insulation Resistance Low. | 1. SR099235
CA: Rancho Cordova - Citi | CA | 166102 | 171056 | 97.1% | 113.3% | 169174 | -3072 | -1.816% | 173208.522 | -7106.522 | -4.103% | 1. Inverter 5-3 was derated to a maximum of 13.8 kW on 03/17 and later self-resolved on 03/19. | 1. SR098684
CA: S Sacramento Wyndham - Citi | CA | 88110 | 100685.5 | 87.51% | 100% | 99485 | -11375 | -11.43% | 95237.35 | -7127.35 | -7.484%
CA: Sacramento Point West - Citi | CA | 171910 | 191838.6 | 89.61% | 100.3% | 190837 | -18927 | -9.918% | 190101.805 | -18191.805 | -9.57% | 1. Inverter 5.4 tripped offline at 10:30 AM on 02/22 due to ARC protection and water in the wire box, so a new wire box is needed for replacement to get back the inverter. 2. Inverter 1.3 is underperforming by about 10 kW compared to its peers due to a string being offline for an isolated module check. | 1. SR097653 2. SR098986 | SR098986
CA: San Jose FHC - Citi | CA | 36845.25 | 41967.8 | 87.79% | 87.15% | 43014 | -6168.75 | -14.34% | 40463.992 | -3618.742 | -8.943% | 1 The meter's phase B CT is 25 amps lower than the phase A and C CTs. There is a 3% variance between the meter and total inverter power. After the technician arrived, it was confirmed that the meter's CTs need to be replaced. | 1. SR098874, SR092732 | SR092732
CA: San Jose MOB - Citi | CA | 50848.5 | 67199.5 | 75.67% | 78.99% | 67773 | -16924.5 | -24.97% | 64993.209 | -14144.709 | -21.76% | 1. Inverter 10 experienced multiple trippings from 02/27. The technician set the inverter to isolation mode and re-energized it on 03/03. After the technician confirmed that the inverter settings were modified to temporarily improve conditions, it is now under RMA. 2. Inverter 2 is derating by 6 kW, likely due to overheating, and is now under RMA. Additionally, after the technician's arrival, the inverter has been offline at 12:25 PM on 03/18 and remains offline throughout the month. | 1. SR097893 2. SR097777, SR099041 | SR097777 | SR099041
CA: Selma - Citi | CA | 35938.63 | 38028.7 | 94.5% | 106.6% | 37645 | -1706.37 | -4.533% | 39397.5 | -3458.87 | -8.779%
CA: Vacaville Hospital | CA | 203198.25 | 264914.4 | 76.7% | 93.86% | 263144 | -59945.75 | -22.78% | 240625.497 | -37427.247 | -15.55% | 1. Inverters 2 to 4, 7, 8 , 10, 12, 13, 15, 20, 25 and 33 had shading issue during 7:00AM to 11:00AM. | 1. SR099626
CA: Manteca - KP Manteca Hospital | CA | 83208.62 | 89816 | 92.64% | 110.4% | 83465.578 | -256.958 | -0.3079% | 83768.304 | -559.684 | -0.6681%
Sacramento - KP South Sacramento HSP | CA

## Apr
CITI |  |  | PPA Modeled Output | Production VS Acual | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 2445429.72 | 2349739.64 | 104.1% | 2318877.102 | 126552.618 | 5.457% | 2530994.875 | -85565.155 | -3.381%
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA | 66912.5 | 65019.85 | 102.9% | 64376 | 2536.5 | 3.94% | 68707.091 | -1794.591 | -2.612%
CA: Antioch MC CUP - Citi | CA | 221831 | 220973.05 | 100.4% | 218766 | 3065 | 1.401% | 225921.981 | -4090.981 | -1.811%
CA: Clovis - Citi | CA | 89193.75 | 97022.5 | 91.93% | 93673 | -4479.25 | -4.782% | 16682.648 | 72511.102 | 434.6% | 1. Weather station showing erratic data with continuous fluctuations. On 04/29/25, tech checked DAS cabinet—24VDC present, connections good. Contacted AlsoEnergy; they confirmed data issues. Checked sensor terminal voltages and reported back. Sent emails with photos and readings. AlsoEnergy unable to ping sensors—recommended replacement. Tech contacting AlsoEnergy sales for irradiance and temp sensor quotes 2. Inverter 7 underperforming by ~4kW vs peers. On 04/29/25, tech found voltages and fuses OK. Called CPS—no site access. AlsoEnergy confirmed Inverter 7 producing ~2kW vs 8 & 9. Tech will follow up with CPS to check settings. 3. Forcasted values are too low compared to actual values it indicates there is an issue with forcasted values. | 1. SR099622, SR099968 2. SR100881, SR099968
CA: Elk Grove MOB - Citi | CA | 142227 | 144992 | 98.09% | 143557 | -1330 | -0.9265% | 151438.333 | -9211.333 | -6.083%
CA: Elk Grove Promenade - Citi | CA | 74427.75 | 77224 | 96.38% | 76459.5 | -2031.75 | -2.657% | 79947.745 | -5519.995 | -6.905% | 1. Inverter 1.4 is underperforming by 3 kW and is in independent mode, possibly relates to MPPTs being unbalanced. | 1. SR099434
CA: Fresno Sequioa - Citi | CA | 150829 | 162120.93 | 93.03% | 160548 | -9719 | -6.054% | 159435.694 | -8606.694 | -5.398%
CA: Fresno MOB - Citi | CA | 50968.75 | 66110.13 | 77.1% | 65850 | -14881.25 | -22.6% | 54041.677 | -3072.927 | -5.686% | 1.Inverter 7 is underperforming by 30 kW from 03/25. On 04/03/25, tech onsite to investigate canopy damage. One module visibly damaged; Inverter 7 underperforming by 30 kW but still online with no errors. Tech isolated string with bad module. Likely due to ongoing isolations—Ameresco to verify on return visit. | 1. SR099369, SR097152 & SR099432
CA: Modesto Bangs - Citi | CA | 37883.75 | 45977.64 | 82.4% | 45753 | -7869.25 | -17.2% | 7847.79 | 30035.96 | 382.7% | 1. Weather station has been reporting erroneous values since 04/07 at 13:45, with continuous fluctuations on the graph indicating inconsistent readings throughout the day. 2. Forcasted values are too low compared to actual values it indicates there is an issue with forcasted values. | 1. SR099861
CA: Napa Data Center - Citi | CA | 38486 | 45541.33 | 84.51% | 43705 | -5219 | -11.94% | 45408.781 | -6922.781 | -15.25% | 1.Inverter 4 was offline from 04/01 to 16:45 on 04/02 and started delayed for production at 15:15 on 04/27.This inverter has previously exhibited a pattern of delayed startups. | 1.SR098674,SR097715
CA: Petaluma MOB - Citi | CA | 93558.5 | 105601.15 | 88.6% | 101621 | -8062.5 | -7.934% | 42822.349 | 50736.151 | 118.5% | 1.Since 03/21, Phase B and C CTs have read 40A lower than Phase A, causing a 5% variance. The CT issue was confirmed after swapping, with replacement needed. The meter has reported negative values since 03/27. On 04/24, technicians found incorrect power factor values, affecting production readings. After swapping phases, the meter showed the correct value. 2.Inverters 5 and 14 are underperforming by 3 kW from 03/28 and are in independent mode 3.Weather station is currently reading inaccurately | 1.SR098872,SR099542 2.SR099433 3.SR100933
CA: Pleasanton Tec Ctr - Citi | CA | 114378 | 145619.1 | 78.55% | 144180 | -29802 | -20.67% | 141226.66 | -26848.66 | -19.01% | 1.Meter phase B CT is 170 amps lower than A and C phase CTs. There is a 7% variance, meter vs inv total power.Meter is being RMAD from 03/27 2.Inverters 1, 3, and 5 remained offline throughout the month. On 04/01, the technician indicated that further troubleshooting is required and the inverters will remain offline until necessary repairs are completed.Issue did not resolve | 1.SR098873 2.SR099231,SR099235,SR099339
CA: Rancho Cordova - Citi | CA | 206681 | 200365.35 | 103.2% | 199166 | 7515 | 3.773% | 215158.23 | -8477.23 | -3.94% | 1.Inverter 5-3 was derated to a maximum of 13.8 kW starting from 03/17. On 04/22, a technician inspected the site and found no abnormalities. The technician has contacted the inverter manufacturer for further assistance, as the issue persisted despite inverter troubleshooting. | 1.SR098684,SR100658
CA: S Sacramento Wyndham - Citi | CA | 113159 | 125048.54 | 90.49% | 121244 | -8085 | -6.668% | 122861.986 | -9702.986 | -7.897%
CA: Sacramento Point West - Citi | CA | 226270 | 239197.4 | 94.6% | 237736 | -11466 | -4.823% | 250953.627 | -24683.627 | -9.836% | 1.Inverter 5.4 remained offline throughout the month due to arc protection faults and water ingress in the wire box. A new wire box is needed, and further troubleshooting is required 2.. Inverter 1.3 is underperforming by about 10 kW compared to its peers due to a string being offline | 1.SR097653 2.SR098986
CA: San Jose FHC - Citi | CA | 43419.25 | 49237.46 | 88.18% | 50465 | -7045.75 | -13.96% | 47240.384 | -3821.134 | -8.089% | 1.The meter's phase B CT is 25 amps lower than the phase A and C CTs. There is a 3% variance between the meter and total inverter power. On 04/03, After the technician arrived, it was confirmed that the meter's CTs need to be replaced. | 1.SR098874
CA: San Jose MOB - Citi | CA | 60746.75 | 78443.78 | 77.44% | 79113 | -18366.25 | -23.22% | 77333.965 | -16587.215 | -21.45% | 1.Inverter 2 and under RMA for its derating issue caused by overheating and remains offline throughout the month. 2. Inverter 1 is underperforming by 3 kW and is independent mode from 03/07 | 1.SR099041 2.SR099435
CA: Selma - Citi | CA | 43135.12 | 49331.1 | 87.44% | 48801 | -5665.88 | -11.61% | 48076.644 | -4941.524 | -10.28% | 1. Inverters 3 and 4 are experiencing shading from morning to midday, while Inverter 1 is experiencing shading from midday to evening. | 1. SR101090
CA: Vacaville Hospital | CA | 275899.5 | 326133.33 | 84.6% | 322891 | -46991.5 | -14.55% | 354931.493 | -79031.993 | -22.27% | 1.Meter 2 phase A current is about 65 amps lower than phase B and C currents. 18 % variance in total inv power and meter power 2. Inverters 2 to 4, 7, 8 , 10, 12, 13, 15, 20, 25 and 33 had shading issue during 7:00AM to 11:00AM. 3.Multiple inverters are reporting lower-than-expected production, possibly due to incorrect system drawings or the need for a firmware update | 1.SR100428 2.SR099626 3.SR100428
CA: Manteca - KP Manteca Hospital | CA | 99787.38 | 105781 | 94.33% | 100972.602 | -1185.222 | -1.174% | 95175.797 | 4611.583 | 4.845% | 1. Weather station is heavily shaded until around 10:00 each morning.Dispatch is scheduled on 05/08. | 1.SR099704
Sacramento - KP South Sacramento HSP | CA | 295635.72 | 0 |  | 0 | 295635.72 |  | 325782 | -30146.28 | -9.254% | 1.Inverter 10.1 was offline from 04/01 ,technician Opened up inverter and found wire box to be water damaged and corroded, requires further trubleshooting.on 04/16,technician replacd the wirebox for inverter.Inverter 10.1 was back online on 04/16 but production cannot be seen through DAS. 2.Inverter 1.3 was offline from 04/01 .Technician Opened combiner box and noticed visual signs of corrosion, causing the inverter to run on standby mode.Inverter 1.3 was being RMAD from 01/02.Inverter 1.3 was back online at 19:05 on 04/17 3.Inverter 5.3 was reporting production data in Locus portal.As mentioned by the technician the comms card is not plugged in.On 04/14,technician troubleshoot the inverter 5.3 and bringed it back online onsite on same day.it requires additional troubleshooting.Production cannot be seen through DAS 4.Inverter 6.4 was intermittently derating. The issue was resolved on 04/17 after a technician conducted troubleshooting and indicated that the derating was likely caused by nearby trees 5. 11.1, 11.2, and 11.3 were offline throughout the month.Production cannot be seen through DAS | 1.SR095613 2.SR090290,SR095613,SR098811 3.SR095613,SR098811 4.SR099818,SR100096 5.SR099875,SR095613

## May
CITI |  |  | PPA Modeled Output | Production VS Acual | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 2973920.05 | 2778688.91 | 107% | 2742135.446 | 231784.604 | 8.453% | 3076294.605 | -102374.555 | -3.328%
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA | 81492.5 | 74449.26 | 109.5% | 73712 | 7780.5 | 10.56% | 84914.724 | -3422.224 | -4.03%
CA: Antioch MC CUP - Citi | CA | 269650 | 254348.83 | 106% | 251808 | 17842 | 7.086% | 285700.703 | -16050.703 | -5.618%
CA: Clovis - Citi | CA | 110990 | 108547 | 102.3% | 104799 | 6191 | 5.907% | 7792.713 | 103197.287 | 1324% | 1. The weather station has been reporting erroneous values, with its graph showing continuous fluctuations throughout the day,indicating inconsistent readings. We are contacting AlsoEnergy sales for a quote for a replacement irradiance sensor and temperature sensor for this site. | 1.SR099622
CA: Elk Grove MOB - Citi | CA | 174908.5 | 181338.5 | 96.45% | 179543 | -4634.5 | -2.581% | 190114.87 | -15206.37 | -7.999%
CA: Elk Grove Promenade - Citi | CA | 92961.75 | 95545 | 97.3% | 94599.133 | -1637.383 | -1.731% | 99352.21 | -6390.46 | -6.432%
CA: Fresno Sequioa - Citi | CA | 177350.5 | 179936.42 | 98.56% | 178191 | -840.5 | -0.4717% | 193380.115 | -16029.615 | -8.289%
CA: Fresno MOB - Citi | CA | 64388.87 | 72873.04 | 88.36% | 72791 | -8402.13 | -11.54% | 70583.371 | -6194.501 | -8.776% | 1.Inverter 7 is down 5 strings.On 05/19, technician closed in all fuses and restarted inverter.Issue was resolved since then. | 1.SR101507
CA: Modesto Bangs - Citi | CA | 47080.25 | 52921.57 | 88.96% | 52663 | -5582.75 | -10.6% | 183.563 | 46896.687 | 25548% | 1.The weather station has been reporting erroneous values since 04/07 at 13:45. The data graph shows continuous fluctuations throughout the day, indicating inconsistent readings. The issue is currently under investigation, and we are reaching out to AlsoEnergy for a quote on a replacement reference cell | 1.SR099861
CA: Napa Data Center - Citi | CA | 48683.25 | 53542.49 | 90.92% | 51546 | -2862.75 | -5.554% | 56772.615 | -8089.365 | -14.25% | 1.Inverter 4 has a history of multiple trip events. On 05/07, a technician visited the site, performed troubleshooting on Inverter 4, and initiated an RMA request for replacement. | 1.SR098674
CA: Petaluma MOB - Citi | CA | 105493.5 | 123235.12 | 85.6% | 118590 | -13096.5 | -11.04% | 11916.177 | 93577.323 | 785.3% | 1.Inverters 5 and 14 are underperforming by approximately 3 kW and are operating in independent mode. On 05/20, Chint support informed the technician that the 3 kW production loss was not significant enough to initiate the RMA process, as both inverters are online and producing. The matter is currently being followed up with CPS management for further review 2.weather station was reading inaccurately.on 05/20 ,technician checked into site site and confirmed that the weather station sensor was determined to be faulty and new one is needed.confirmed with ROC the need for replacement device | 1.SR099433 2.SR100933 | SR100933
CA: Pleasanton Tec Ctr - Citi | CA | 146888 | 167397.62 | 87.75% | 165841 | -18953 | -11.43% | 179634.968 | -32746.968 | -18.23% | 1. Meter phase B CT is 170 amps lower than A and C phase CTs. There is a 7% variance, meter vs inv total power.On 05/20,technician applied LOTO to the main disconnect, removed damaged CTs, and installed new ones.from then Phase B CT is functioning properly with no further issues. 2.Inverters 1, 3, and 5 remained offline throughout the month. On 04/09, the technician indicated that further troubleshooting is required and the inverters will remain offline until necessary repairs are done.Technicain metioned that about 65 modules will need to be removed for repairs. | 1.SR098873 2.SR099231,SR099339 | SR099231 | SR099339
CA: Rancho Cordova - Citi | CA | 248219 | 241187.82 | 102.9% | 239745 | 8474 | 3.535% | 261974.247 | -13755.247 | -5.251%
CA: S Sacramento Wyndham - Citi | CA | 138356.5 | 157421.02 | 87.89% | 156334 | -17977.5 | -11.5% | 152454.648 | -14098.148 | -9.247% | 1.Site has intermittent communication throughout the month
CA: Sacramento Point West - Citi | CA | 285798 | 300484.1 | 95.11% | 298182 | -12384 | -4.153% | 317297.674 | -31499.674 | -9.927%
CA: San Jose FHC - Citi | CA | 53378.5 | 57715.5 | 92.49% | 59155 | -5776.5 | -9.765% | 60806.864 | -7428.364 | -12.22% | 1.The meter's phase B CT is 25 amps lower than the phase A and C CTs. There is a 3% variance between the meter and total inverter power. On 04/03, After the technician arrived, it was confirmed that the meter's CTs need to be replaced. | 1.SR098874,SR101694 | SR101694
CA: San Jose MOB - Citi | CA | 81782.75 | 91386 | 89.49% | 92166 | -10383.25 | -11.27% | 101706.775 | -19924.025 | -19.59% | 1.Inverter 2 was being RMAD for its derating issue caused by overheating .Issue got resolved on 05/15 after technician swaped the inverter 2. Inverter 1 was underperforming by approximately 3 kW and operating in independent mode. The issue was resolved on 05/15 after technician has troubleshoot | 1.SR099041 2.SR099435 | SR099435
CA: Selma - Citi | CA | 49911.5 | 55270.29 | 90.3% | 54770 | -4858.5 | -8.871% | 58466.924 | -8555.424 | -14.63% | 1.Inverters 3 and 4 are experiencing shading from morning to midday, while Inverter 1 is experiencing shading from midday to evenin | 1.SR101090
CA: Vacaville Hospital | CA | 344789 | 384708.33 | 89.62% | 379954 | -35165 | -9.255% | 454280.388 | -109491.388 | -24.1% | 1.Inverters 2 to 4, 7, 8 , 10, 12, 13, 15, 20, 25 and 33 had shading issue during 7:00 to 11:00. 2.Meter 2 phase A current is about 65 amps lower than phase B and C currents. 18 % variance in total inv power and meter power.This requires additional troubleshooting. 3.Multiple inverters are reporting lower-than-expected production, possibly due to incorrect system drawings or the need for a firmware update.This requires additional troubleshooting. | 1.SR099626 2.SR100428 3.SR100428 | SR100428 | SR100428
CA: Manteca - KP Manteca Hospital | CA | 75256.25 | 126381 | 59.55% | 117746.313 | -42490.063 | -36.09% | 83101.056 | -7844.806 | -9.44% | 1. Weather station is heavily shaded until around 10am each morning.On 05/22 technician checked into site and mentioned it Requires further troubleshooting 2.Site was offline from 15:05 to 16:50 on 05/06.Issue self resolved 3.Site was offline from 10:15 on 05/09 to 10:35 on 05/12.Site was again offline from 15:40 on 05/19 to 15:50 on 05/22.site was back online after technician replaced blown fuse.Site remained offline offline from 13:45 on 05/26 for the rest of the month.Additional troubleshooting is required. | 1.SR099704 2.SR101255 3.SR101695 | SR101255 | SR101695
Sacramento - KP South Sacramento HSP | CA | 376541.43 | 0 |  | 0 | 376541.43 |  | 405860 | -29318.57 | -7.224% | 1. Inverter 6.4 is intermittently derating in the morning.Issue resolved on 05/08 after technician adjusted few parameters 2.Inverters 4.1,4.2,.4.3, 5.1,5.2, 8.3, 10.2, 10.3 tripped offline at 10:45 on 05/12 reporting Steady State GFCI faults.Issue got resolved on 05/29 3.Reference cell 4 stopped communicating on 5/27/25.Dispatch is scheduled in the month of june | 1.SR100096 2.SR101335 3.SR102064 | SR101335 | SR102064

## Jun
CITI |  |  | PPA Modeled Output | Production VS Acual | Q2 Production Vs PPA | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 2862257.94 | 2847464 | 100.5% | 91.34% | 2604610 | 257647.94 | 9.892% | 3219200 | -356942.06 | -11.09%
Site | State | Actual |  |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA | 82695.75 | 76877 | 107.6% | 106.8% | 82043 | 652.75 | 0.7956% | 76116 | 6579.75 | 8.644%
CA: Antioch MC CUP - Citi | CA | 268167 | 262669 | 102.1% | 102.9% | 282694 | -14527 | -5.139% | 260045 | 8122 | 3.123%
CA: Clovis - Citi | CA | 114614.5 | 114359 | 100.2% | 98.4% | 3523 | 111091.5 | 3153% | 110410 | 4204.5 | 3.808% | 1. The weather station has been reporting erroneous values, with its graph showing continuous fluctuations throughout the day,indicating inconsistent readings. We are contacting AlsoEnergy sales for a quote for a replacement irradiance sensor and temperature sensor for this site. | 1.SR099622
CA: Elk Grove MOB - Citi | CA | 171629 | 182422 | 94.08% | 96.07% | 188607 | -16978 | -9.002% | 180616 | -8987 | -4.976%
CA: Elk Grove Promenade - Citi | CA | 97576.5 | 95644 | 102% | 98.72% | 96119 | 1457.5 | 1.516% | 94697 | 2879.5 | 3.041% | 1. Inverter 1.4 is underperforming by 3 kW and is in independent mode, possibly relates to MPPTs being unbalanced. | 1.SR0099434
CA: Fresno Sequioa - Citi | CA | 188158.5 | 187953 | 100.1% | 97.42% | 193590 | -5431.5 | -2.806% | 186130 | 2028.5 | 1.09%
CA: Fresno MOB - Citi | CA | 72933.75 | 75912 | 96.08% | 87.62% | 76017 | -3083.25 | -4.056% | 76017 | -3083.25 | -4.056% | 1. Inverter 3 tripped offline at 21:05 on 06/30 and reporting an arc protection. | 1. SR103832
CA: Modesto Bangs - Citi | CA | 46412.88 | 54773 | 84.74% | 85.49% | 77 | 46335.88 | 60176% | 54506 | -8093.12 | -14.85% | 1.The weather station has been reporting erroneous values since 04/07 at 13:45. The data graph shows continuous fluctuations throughout the day, indicating inconsistent readings. The issue is currently under investigation, and we are reaching out to AlsoEnergy for a quote on a replacement reference cell and pending CT replacement. | 1. SR099861
CA: Napa Data Center - Citi | CA | 48182.12 | 54497 | 88.41% | 88.13% | 56426 | -8243.88 | -14.61% | 52456 | -4273.88 | -8.148% | 1.Inverter 4 has a history of multiple trip events. On 05/07, a technician visited the site, performed troubleshooting on Inverter 4, and initiated an RMA request for replacement. on 06/23, technician replaced the inverter 4 now it's producting as expected. | 1. SR098674
CA: Petaluma MOB - Citi | CA | 106306.5 | 124350 | 85.49% | 86.46% | 11504 | 94802.5 | 824.1% | 119663 | -13356.5 | -11.16% | 1.Inverters 5 and 14 are underperforming by approximately 3 kW and are operating in independent mode. On 05/20, Chint support informed the technician that the 3 kW production loss was not significant enough to initiate the RMA process, as both inverters are online and producing. The matter is currently being followed up with CPS management for Flex Gateway to install at the site is pending replacement. 2.weather station was reading inaccurately.On 05/20 ,technician checked into site site and confirmed that the weather station sensor was determined to be faulty and new one is needed.confirmed with ROC the need for replacement device like CT's. | 1. SR099433 2. SR100933 | SR100933
CA: Pleasanton Tec Ctr - Citi | CA | 153379.5 | 176505 | 86.9% | 84.7% | 183386 | -30006.5 | -16.36% | 174859 | -21479.5 | -12.28% | 1. Inverters 1, 3, and 5 remained offline throughout the month. On 04/09, the technician indicated that further troubleshooting is required and the inverters will remain offline until necessary repairs are done.Technicain metioned that about 65 modules will need to be removed for repairs. | 1. SR099231,SR099339 | SR099339
CA: Rancho Cordova - Citi | CA | 238318 | 236948 | 100.6% | 102.2% | 252933 | -14615 | -5.778% | 235530 | 2788 | 1.184% | 1. Inverter 1-1 tripped offline at 15:55 on 05/31 and reporting "Grid line voltage out of range" and back online at 16:25 on 06/03. 2. Inverter 3.4 tripped offline at 16:00 on 06/18 due to a 'Grid line voltage out of range' error. On 06/26, a technician inspected the system, reset the Inverter 3.4 breaker, and re-energized the inverter. It's back online at 12:50 on 06/26. | 1. SR102225 2. SR103154 | SR103154
CA: S Sacramento Wyndham - Citi | CA | 142944 | 158605 | 90.13% | 89.43% | 151388 | -8444 | -5.578% | 157510 | -14566 | -9.248% | 1.Site has intermittent communication throughout the month
CA: Sacramento Point West - Citi | CA | 290056 | 302720 | 95.82% | 95.22% | 309080 | -19024 | -6.155% | 300289 | -10233 | -3.408% | 1. Inverter 5.4 has been offline since 02/22, reporting an 'ARC Protection' fault. Replacement parts are pending. 2.Inverter 1.3 has been underperforming by approximately 10 kW compared to its peers since 03/25, possibly due to a string being offline because of an isolated module pending replacement. 3. Inverter 1.1 tripped offline at 17:15 on 06/28 and reporting "Inverter hardware over current". later, self resolved and back online at 17:45 on 06/28. | 1. SR097653 2. SR098986 3. SR103688 | SR098986 | SR103688
CA: San Jose FHC - Citi | CA | 54915.75 | 60463 | 90.83% | 90.62% | 60009 | -5093.25 | -8.487% | 61970 | -7054.25 | -11.38% | 1.The meter's phase B CT is 25 amps lower than the phase A and C CTs. There is a 3% variance between the meter and total inverter power. On 04/03, After the technician arrived, it was confirmed that the meter's CTs need to be replaced. Pending to replace the meter's CTs. | 1.SR098874,SR101694, SR101694 | SR101694 | SR101694
CA: San Jose MOB - Citi | CA | 92353.5 | 95898 | 96.3% | 88.39% | 99821 | -7467.5 | -7.481% | 96716 | -4362.5 | -4.511% | 1. Inverter 1 was underperforming by approximately 3 kW and operating in independent mode. and need to replace Flex gateway is pendiging to install. | 1. SR099435
CA: Selma - Citi | CA | 55049.88 | 58141 | 94.68% | 91% | 59824 | -4774.12 | -7.98% | 57686 | -2636.12 | -4.57%
CA: Vacaville Hospital | CA | 305809.75 | 398845 | 76.67% | 83.49% | 450299 | -144489.25 | -32.09% | 394009 | -88199.25 | -22.39% | 1.Meter 2 Phase A current is approximately 65 amps lower than the Phase B and C currents, resulting in an 18% variance between total inverter power and meter power. This issue requires further troubleshooting. Additionally, multiple inverters are reporting lower-than-expected production, possibly due to incorrect system drawings or the need for a firmware update. This also requires further investigation. | 1. SR100428
CA: Manteca - KP Manteca Hospital | CA | 50800.62 | 129883 | 39.11% | 62.38% | 47270 | 3530.62 | 7.469% | 122772 | -71971.38 | -58.62% | 1. The site tripped offline at 13:45 on 05/26. On 05/28, a technician visited the site and determined that the disconnect needed to be replaced. Later, on 06/18, after resetting the site, it was brought back online at 13:00 on 06/18. 2. Weather station is heavily shaded until around 10am each morning.On 05/22 technician checked into site and mentioned it Requires further troubleshooting. | 1. SR101695 2. SR099704 | SR099704
Sacramento - KP South Sacramento HSP | CA | 281954.44 | 0 |  |  | 0 | 281954.44 |  | 407203 | -125248.56 | -30.76% | 1. Reference Cell 4 stopped communicating on 05/27. On 05/29, a technician visited the site and found that Meter 1 had sustained thermal damage. The breaker and feeders connected to the meter were burnt and require replacement. Additional work is needed due to ongoing construction repairs on the cabinet and feeders. | 1. SR102064

## Jul
CITI |  |  | PPA Modeled Output | Production VS Acual | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 2742771.05 | 2915075 | 94.09% | 2682824 | 59947.05 | 2.234% | 3303304 | -560532.95 | -16.97%
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA | 82623 | 80328 | 102.9% | 80915 | 1708 | 2.111% | 79533 | 3090 | 3.885%
CA: Antioch MC CUP - Citi | CA | 264875 | 274546 | 96.48% | 276467 | -11592 | -4.193% | 271804 | -6929 | -2.549%
CA: Clovis - Citi | CA | 112136 | 112980 | 99.25% | 2035 | 110101 | 5410% | 109079 | 3057 | 2.803% | 1. The weather station has been reporting erroneous values. Its graph shows continuous fluctuations throughout the day, indicating inconsistent readings. Scheduled to be investigate on 08/20. | 1. SR099622
CA: Elk Grove MOB - Citi | CA | 167796 | 188726 | 88.91% | 195536 | -27740 | -14.19% | 187053 | -19257 | -10.29% | 1. Inverter 1.4 has shading from morning to afternoon. Inverter 1.2, 2.1 has shading from afternoon to evening.
CA: Elk Grove Promenade - Citi | CA | 94955.25 | 99091 | 95.83% | 98303 | -3347.75 | -3.406% | 98305 | -3349.75 | -3.408%
CA: Fresno Sequioa - Citi | CA | 183905 | 186172 | 98.78% | 192052 | -8147 | -4.242% | 184366 | -461 | -0.25%
CA: Fresno MOB - Citi | CA | 67107.5 | 74907 | 89.59% | 70535 | -3427.5 | -4.859% | 75021 | -7913.5 | -10.55% | 1. Inverter 6 was offline from 06/20 and inverter 3 was offline from 06/30. Both inverters are back online on 07/14. | 1. SR103832, SR104264 | SR104264
CA: Modesto Bangs - Citi | CA | 45314.12 | 53493 | 84.71% | 124 | 45190.12 | 36444% | 53232 | -7917.88 | -14.87% | 1. The weather station has been reporting erroneous values from 04/07. Its graph shows continuous fluctuations throughout the day, indicating inconsistent readings.Scheduled to be investigate on 08/06. | 1. SR099861
CA: Napa Data Center - Citi | CA | 45435 | 55306 | 82.15% | 67180 | -21745 | -32.37% | 53188 | -7753 | -14.58% | 1. All inverters experiencing shading issue during evening hours. | 1. SR105795
CA: Petaluma MOB - Citi | CA | 99381.5 | 129113 | 76.97% | 37993 | 61388.5 | 161.6% | 124247 | -24865.5 | -20.01% | 1. Weather station reporting inaccurate values. On 07/24 technician replaced irradiance sensor and started operating correctly. 2. Inverters 5 and 14 are underperforming by 3 kW. On 07/24 Inv 14 replaced LCD board and bus bar, producing in line with peers. Need to replace inv 5 powerhead. | 1. SR100933 2. SR099433, SR104106, SR105254 | SR099433 | SR104106 | SR105254
CA: Pleasanton Tec Ctr - Citi | CA | 148392.5 | 182148 | 81.47% | 181107 | -32714.5 | -18.06% | 180446 | -32053.5 | -17.76% | 1. Inverters 12, 15, and 17 tripped offline on GFCI faults on 07/22 and self-resolved on 07/23. | 1. SR104774
CA: Rancho Cordova - Citi | CA | 236028 | 247104 | 95.52% | 258638 | -22610 | -8.742% | 245625 | -9597 | -3.907% | 1. Inverter 3.4 was tripped offline on 07/27 at 16:50 and remained offline for end of the month. 2. Inverter 3.3 started late on 07/09 at 10:45 and on 07/24 at 10:50 | 1. SR105142 2. SR104189 | SR104189
CA: S Sacramento Wyndham - Citi | CA | 141774.5 | 163639 | 86.64% | 152231 | -10456.5 | -6.869% | 162509 | -20734.5 | -12.76% | 1. Inverter 4.3 was offline from 13:45 to 20:00 on 07/26.
CA: Sacramento Point West - Citi | CA | 283101 | 313299 | 90.36% | 312724 | -29623 | -9.473% | 310558 | -27457 | -8.841%
CA: San Jose FHC - Citi | CA | 56028 | 62467 | 89.69% | 59279 | -3251 | -5.484% | 64025 | -7997 | -12.49% | 1. The meter's phase B CT is 25 amps lower than the phase A and C CTs. There is a 3% variance between the meter and total inverter power. The CT's were replaced and meter started reporting as excepected since 07/28. Site was taken offline on 07/28 from 12:00 to 13:45 to replace CT on meter | 1. SR101694
CA: San Jose MOB - Citi | CA | 86948 | 99033 | 87.8% | 93614 | -6666 | -7.121% | 99878 | -12930 | -12.95% | 1. Inverter 1 is underperforming by 3 kW and is independent mode. Will be investigate in next month. | 1. SR104095, SR099435 | SR099435
CA: Selma - Citi | CA | 52288.87 | 57267 | 91.31% | 59835 | -7546.13 | -12.61% | 56789 | -4500.13 | -7.924% | 1. Inverters 3 and 4 are experiencing shading from morning to midday, while Inverter 1 is experiencing shading from midday to evening. | 1. SR101090
CA: Vacaville Hospital | CA | 183603.5 | 405264 | 45.3% | 438855 | -255251.5 | -58.16% | 399689 | -216085.5 | -54.06% | 1. Inverters 13,18,19 are underperforming by 3kW during high irradiance days. Issue was self-resolved by 07/31. 2. Meter 2 Phase A current is approximately 65 amps lower than the Phase B and C currents, resulting in an 18% variance between total inverter power and meter power. Waiting for parts. | 1. SR104704 2. SR100428 | SR100428
CA: Manteca - KP Manteca Hospital | CA | 116336 | 130192 | 89.36% | 105401 | 10935 | 10.37% | 126640 | -10304 | -8.136% | 1. Weather station is heavily shaded until around 10am each morning. | 1. SR099704
Sacramento - KP South Sacramento HSP | CA | 274742.31 | 0 |  | 0 | 274742.31 |  | 421317 | -146574.69 | -34.79% | 1. Meter 1 had sustained thermal damage. The breaker and feeders connected to the meter were burnt and require replacement. Ameresco construction repairs were ongoing. | 1. SR102064

## Aug
CITI |  |  | PPA Modeled Output | Production VS Acual | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 2436361.58 | 2706108 | 90.03% | 2978561.32 | -542199.74 | -18.2% | 3061726.187 | -625364.607 | -20.43%
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA | 74969.5 | 74036 | 101.3% | 75945.85 | -976.35 | -1.286% | 73471 | 1498.5 | 2.04%
CA: Antioch MC CUP - Citi | CA | 237085 | 252293 | 93.97% | 259019.6 | -21934.6 | -8.468% | 249773 | -12688 | -5.08%
CA: Clovis - Citi | CA | 93874.25 | 107365 | 87.43% | 22666.1 | 71208.15 | 314.2% | 103658 | -9783.75 | -9.438% | 1. The weather station has been reporting erroneous values. Its graph shows continuous fluctuations throughout the day, indicating inconsistent readings. on 08/25 technician replaced Irradiance sensor and it is reporting as expected. 2. Inverters 2, 3 and 6 has tripped offline at 17:15 on 08/23. All inverters are reporting "Steady state GFCI fault" and later back online at 07:00 on 08/24. 3. Inverter 1 has tripped offline at 21:40 on 08/26 and reporting "ARC protection" and remained offline throughout the month. | 1. SR099622 2. SR106793 3. SR107034 | SR106793 | SR107034
CA: Elk Grove MOB - Citi | CA | 171267 | 172569 | 99.25% | 180396.6 | -9129.6 | -5.061% | 171449 | -182 | -0.1062%
CA: Elk Grove Promenade - Citi | CA | 83452.5 | 91788 | 90.92% | 87993.28 | -4540.78 | -5.16% | 91088.234 | -7635.734 | -8.383%
CA: Fresno Sequioa - Citi | CA | 154583 | 179046 | 86.34% | 173772.2 | -19189.2 | -11.04% | 177309 | -22726 | -12.82% | 1. Due to seasonal changes, the performance of Inverter 6 has gradually decreased since August. A similar trend was also observed last year.
CA: Fresno MOB - Citi | CA | 62401.63 | 72218 | 86.41% | 60214.48 | 2187.15 | 3.632% | 72360 | -9958.37 | -13.76% | 1. Inverter 1 has tripped offline at 11:55 on 08/26. during a storm and reporting "GFCI fault" and later back online at 07:00 on 08/27. | 1. SR106951
CA: Modesto Bangs - Citi | CA | 37149.25 | 49248 | 75.43% | 37576.22 | -426.97 | -1.136% | 49007 | -11857.75 | -24.2% | 1. The weather station has been reporting erroneous values from 04/07. Its graph shows continuous fluctuations throughout the day, indicating inconsistent readings. On 08/06 technician recycled the reference cell and it is reporting as expected. | 1. SR099861
CA: Napa Data Center - Citi | CA | 43512.5 | 50233 | 86.62% | 65876.74 | -22364.24 | -33.95% | 48341 | -4828.5 | -9.988% | 1. All inverters experiencing shading issue during evening hours. 2. Inverter 4 has tripped offline at 16:00 on 08/24 and reporting "Bus Differential fault" and later self resolved and back online at 07:00 on 08/25. | 1. SR105795 2. SR106807 | SR106807
CA: Petaluma MOB - Citi | CA | 91072.5 | 119283 | 76.35% | 126782.4 | -35709.9 | -28.17% | 114787 | -23714.5 | -20.66% | 1. Inverters 5 is underperforming by 3 kW. On 07/24 . The powerhead on Inverter 5 needs to be RMA'd. | 1. SR099433, SR104106, SR105254 | SR104106 | SR105254
CA: Pleasanton Tec Ctr - Citi | CA | 147145.5 | 168586 | 87.28% | 169457 | -22311.5 | -13.17% | 167017 | -19871.5 | -11.9% | 1. The site was offline at 22:50 on 08/07 due to potential breaker trip and later back online at 14:05 on 08/08. | 1. SR105911
CA: Rancho Cordova - Citi | CA | 212613 | 236652 | 89.84% | 246152.3 | -33539.3 | -13.63% | 235236 | -22623 | -9.617% | 1. Inverter 3.4 was tripped offline at 16:50 on 07/27 and later back online at 11:15 on 08/13. 2. Inverter 5-1 is down a string (6kW) at 12:00 on 08/14. | 1. SR105142 2. SR107053 | SR107053
CA: S Sacramento Wyndham - Citi | CA | 123325.5 | 149229 | 82.64% | 132435.7 | -9110.2 | -6.879% | 148199 | -24873.5 | -16.78% | 1. Site is producing as expected possibly the issue is with the estimated value.
CA: Sacramento Point West - Citi | CA | 243076 | 286044 | 84.98% | 276686.4 | -33610.4 | -12.15% | 283690 | -40614 | -14.32% | 1. Inverter 5.4 didn't start for production and reporting " ARC Protection" since 02/22/25 and it's under RMA'd. 2. Inverter 1.3 is underperforming by about 10 kW compared to its peers since 03/25/25. | 1. SR097653 2. SR098986 | SR098986
CA: San Jose FHC - Citi | CA | 48008.25 | 57332 | 83.74% | 53385.25 | -5377 | -10.07% | 58762 | -10753.75 | -18.3% | 1. Inverters 4, 6 and 8 have heavy morning shading issue until 10:00 AM.
CA: San Jose MOB - Citi | CA | 74711.25 | 91223 | 81.9% | 84294.44 | -9583.19 | -11.37% | 92001 | -17289.75 | -18.79% | 1. Inverter 1 is underperforming by 3 kW and is independent mode. Will be investigate in next month. 2. Inverter 13 has tripped offline at 12:25 on 08/20 and reporting " 0260 Error Code" and later back online at 15:00 on 08/26. | 1. SR104095, SR099435 2. SR106602 | SR099435 | SR106602
CA: Selma - Citi | CA | 41973.25 | 54361 | 77.21% | 51426.16 | -9452.91 | -18.38% | 53941 | -11967.75 | -22.19% | 1. Inverters 3 and 4 are experiencing shading from morning to midday, while Inverter 1 is experiencing shading from midday to evening. | 1. SR101090
CA: Vacaville Hospital | CA | 142153.5 | 372753 | 38.14% | 387141.7 | -244988.2 | -63.28% | 367738 | -225584.5 | -61.34% | 1. Meter 2 Phase A current is approximately 65 amps lower than the Phase B and C currents, resulting in an 18% variance between total inverter power and meter power. Waiting for parts. 2. inverters 9 to 34 not started for production and reporting "Grid Line Voltage Out of Range" and later self resolved and back online at 11:05 on 08/07. | 1. SR100428, SR104327 2. SR105814 | SR104327 | SR105814
CA: Manteca - KP Manteca Hospital | CA | 102640.13 | 121849 | 84.24% | 104200.4 | -1560.27 | -1.497% | 115631.953 | -12991.823 | -11.24% | 1. Weather station is heavily shaded until around 10am each morning. On 08/19 technician installed replacement cable and sensors and weather station is reporting as expected. | 1. SR099704
Sacramento - KP South Sacramento HSP | CA | 251348.07 | 0 |  | 383138.5 | -131790.43 | -34.4% | 388267 | -136918.93 | -35.26% | 1. Meter 1 had sustained thermal damage. The breaker and feeders connected to the meter were burnt and require replacement. on 08/26 meter 1 and inverters online are back online at 18:25. 2. Inverter 5.3 is intermittently derating in the morning since 08/15. on scheduled during PM on 09/18 | 1. SR102064 2. SR106356 | SR106356

## Sep
CITI |  |  | PPA Modeled Output | Production VS Acual | Q3 Production Vs PPA | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 1986646.63 | 2229628 | 89.1% | 89% | 2273246.25 | -286599.62 | -12.61% | 2540725.938 | -554079.308 | -21.81%
Site | State | Actual |  |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA | 55847.25 | 61034 | 91.5% | 99.09% | 58954.621 | -3107.371 | -5.271% | 60738 | -4890.75 | -8.052%
CA: Antioch MC CUP - Citi | CA | 202819 | 205187 | 98.85% | 96.28% | 198982.146 | 3836.854 | 1.928% | 203137 | -318 | -0.1565%
CA: Clovis - Citi | CA | 78772.75 | 83528 | 94.31% | 93.72% | 88919.439 | -10146.689 | -11.41% | 80644 | -1871.25 | -2.32% | 1. Inverter 1 was offline from 21:45 on 08/26 and came back online at 12:05 on 09/11. | 1. SR107034
CA: Elk Grove MOB - Citi | CA | 122435 | 144942 | 84.47% | 91.16% | 129394.62 | -6959.62 | -5.379% | 144239 | -21804 | -15.12% | 1. Inverter 1.4 has shading from morning to afternoon. Inverter 1.2, 2.1 has shading from afternoon to evening.
CA: Elk Grove Promenade - Citi | CA | 59990 | 78204 | 76.71% | 88.6% | 68141.278 | -8151.278 | -11.96% | 77824.852 | -17834.852 | -22.92% | 1. Inverter 1.4 is underperforming by 3 kW and is in independent mode, possibly relates to MPPTs being unbalanced. | 1.SR099434
CA: Fresno Sequioa - Citi | CA | 129333.5 | 144602 | 89.44% | 91.76% | 143301.242 | -13967.742 | -9.747% | 143200 | -13866.5 | -9.683%
CA: Fresno MOB - Citi | CA | 53728.75 | 57847 | 92.88% | 89.4% | 54424.573 | -695.823 | -1.279% | 57838 | -4109.25 | -7.105%
CA: Modesto Bangs - Citi | CA | 25510.88 | 37763 | 67.56% | 76.85% | 31696.459 | -6185.579 | -19.52% | 37579 | -12068.12 | -32.11% | 1.Weather station fluctuating alternate days on 09/03, 09/10 ,09/ 11 , 09/18 to 09/20 , 09/25,09/26 , 09/30 due to incosistent weather
CA: Napa Data Center - Citi | CA | 34820.25 | 42134 | 82.64% | 83.81% | 52991.802 | -18171.552 | -34.29% | 40640 | -5819.75 | -14.32% | 1. All inverters experiencing shading issue during evening hours. 2. Inverter 4 tripped offline at 10:00 on 09/07 and came back online at 06:30 on 09/08. It tripped offline again at 08:15 on 09/09 and came back online at 07:00 on 09/10. The inverter went offline again on 09/19 and came back online at 07:00 on 09/20, then went offline again on 09/25 and came back online at 07:00 on 09/26. It went offline once more on 09/30. 3. Inverter 5 was offline from 06:30 to 15:30 on 09/07, inverter tripped offline at 14:45 on 09/09 and came back online at 08:00 on 09/10, inverter again tripped offline at 12:15 on 09/10 and came back online at 17:30 on 09/10, inverter went offline on 09/19 and came back online at 10:15 on 09/20, inverter started for production late at 13:45 on 09/26. | 1. SR105795 2. SR106807, SR108584 3. SR108619, SR106807 | SR106807 | SR108584 | SR108619 | SR106807
CA: Petaluma MOB - Citi | CA | 63545 | 97494 | 65.18% | 73.43% | 92354.362 | -28809.362 | -31.19% | 93819 | -30274 | -32.27% | 1. Inverters 5 is underperforming by 3 kW. On 07/24 . The powerhead on Inverter 5 needs to be RMA'd. 2. Inverter 17 tripped offline at 12:10 on 09/09 and came back online at 10:00 on 09/10. Since 09/18, it has been intermittently tripping on and offline daily and remained offline for several hours on 09/23. | 1. SR099433, SR104106, SR105254 2. SR107710 | SR104106 | SR105254 | SR107710
CA: Pleasanton Tec Ctr - Citi | CA | 112420.5 | 134334 | 83.69% | 84.1% | 81305.797 | 31114.703 | 38.27% | 133104 | -20683.5 | -15.54% | 1.Weather sttaion lost communication on 09/05 at 12:05 and came back online on 09/15 at 12:05
CA: Rancho Cordova - Citi | CA | 163345 | 213480 | 76.52% | 87.77% | 184792.964 | -21447.964 | -11.61% | 212202 | -48857 | -23.02% | 1. Inverter 5-1 was down a string from 12:00 on 08/14 and resumed operating along with its peers from 18:10 on 09/24. | 1. SR107053
CA: S Sacramento Wyndham - Citi | CA | 88004 | 125147 | 70.32% | 80.61% | 100006.393 | -12002.393 | -12% | 124283 | -36279 | -29.19% | 1. Site is producing as expected possibly the issue is with the estimated value.
CA: Sacramento Point West - Citi | CA | 166903 | 240439 | 69.42% | 82.53% | 199996.055 | -33093.055 | -16.55% | 238351 | -71448 | -29.98% | 1. Inverter 5.4 didn't start for production and reporting " ARC Protection" since 02/22/25 and it's under RMA'd. 2. Inverter 1.3 is underperforming by about 10 kW compared to its peers since 03/25/25. 3. Inverter 4.2 tripped offline at 12:15 on 09/16 and came back online at 15:00 on 09/24. | 1. SR097653 2. SR098986 3. SR108046 | SR098986 | SR108046
CA: San Jose FHC - Citi | CA | 33532 | 47497 | 70.6% | 82.23% | 41629.609 | -8097.609 | -19.45% | 48681 | -15149 | -31.12% | 1. All inverters experiencing morning shading issue.
CA: San Jose MOB - Citi | CA | 54270.5 | 76541 | 70.9% | 80.93% | 64152.906 | -9882.406 | -15.4% | 77194 | -22923.5 | -29.7% | 1. Inverter 12 experiencing morning to afternoon shading and inverter 14 had evening shading.
CA: Selma - Citi | CA | 33273.75 | 42144 | 78.95% | 82.94% | 41648.86 | -8375.11 | -20.11% | 41994 | -8720.25 | -20.77% | 1. Inverters 3 and 4 had morning shading.
CA: Vacaville Hospital | CA | 193003.25 | 304096 | 63.47% | 47.94% | 267984.292 | -74981.042 | -27.98% | 300743 | -107739.75 | -35.82% | 1. Inverter 3 was offline from 07:00 on 09/13 to 10:00 on 09/14. 2. Inverters 35 through 47 were offline for whole month and the breaker is LOTO's. 3. Meter 2 Phase A current is approximately 65 amps lower than the Phase B and C currents, resulting in an 18% variance between total inverter power and meter power. Waiting for parts. | 1. SR107928 2. SR107287 3. SR100428, SR104327 | SR107287 | SR100428 | SR104327
CA: Manteca - KP Manteca Hospital | CA | 83879.37 | 93215 | 89.98% | 87.72% | 92284.936 | -8405.566 | -9.108% | 96165.086 | -12285.716 | -12.78% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Sacramento - KP South Sacramento HSP | CA | 231212.88 | 0 |  |  | 280283.896 | -49071.016 | -17.51% | 328350 | -97137.12 | -29.58% | 1. Inverter 4.1 was offline from 12:45 on 09/23 to end of the month. 2. Inverter 5.3 was derating intermittently. | 1. SR108432 2. SR106356 | SR106356

## Oct
CITI |  |  | PPA Modeled Output | Production VS Actual | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 1643994.95 | 1739868 | 94.49% | 1769091.984 | -125097.034 | -7.071% | 2249332.283 | -605337.333 | -26.91%
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
CA: Antioch Deer Valley - Citi | CA | 48139.5 | 48791 | 98.66% | 49733.822 | -1594.322 | -3.206% | 48555 | -415.5 | -0.8557%
CA: Antioch MC CUP - Citi | CA | 159015 | 161457 | 98.49% | 162307.979 | -3292.979 | -2.029% | 159844 | -829 | -0.5186% | 1. Inverter 2 was offline from 13:00 to 19:00 on 10/08. | 1. SR109230 | 1. Closed
CA: Clovis - Citi | CA | 73523.57 | 67768 | 108.5% | 67135.724 | 6387.846 | 9.515% | 85899.694 | -12376.124 | -14.41% | 1. Production meter reporting energy spikes due to which actual energy value is affected possibly the issue is due to migration of these site from Locus to AE. Reached out to AlsoEnergy (Case # 623267)
CA: Elk Grove MOB - Citi | CA | 100507 | 107702 | 93.32% | 102964.655 | -2457.655 | -2.387% | 107180 | -6673 | -6.226% | 1. Inverter 1.4 has shading from morning to afternoon. Inverter 1.2, 2.1 has shading from afternoon to evening.
CA: Elk Grove Promenade - Citi | CA | 55013.25 | 59094 | 93.09% | 57268.624 | -2255.374 | -3.938% | 58807.5 | -3794.25 | -6.452% | 1. Inverter 1.4 was underperformed by 5 kW for whole month. | 1. SR108382 | 1. Pending
CA: Fresno Sequioa - Citi | CA | 109714 | 121284 | 90.46% | 114487.967 | -4773.967 | -4.17% | 120362 | -10648 | -8.847%
CA: Fresno MOB - Citi | CA | 42095.25 | 48559 | 86.69% | 44657.814 | -2562.564 | -5.738% | 48457 | -6361.75 | -13.13% | 1. Inverter 7 was offline from 08:35 on 10/20 to 13:15 on 10/27. | 1. SR109754 | 1. Closed
CA: Modesto Bangs - Citi | CA | 23125.5 | 31253 | 73.99% | 26513.214 | -3387.714 | -12.78% | 31100 | -7974.5 | -25.64%
CA: Napa Data Center - Citi | CA | 25421.5 | 32658 | 77.84% | 45546.944 | -20125.444 | -44.19% | 31608 | -6186.5 | -19.57% | 1. Inverter 4 was being RMA. 2. Inverter 5 was underproduced by 5kW for whole month. | 1. SR108584 2. SR108619 | 1. Pending 2. Pending | SR108619
CA: Petaluma MOB - Citi | CA | 42328 | 75096 | 56.37% | 60242 | -17914 | -29.74% | 66005 | -23677 | -35.87% | 1. Inverter 10 and 11 has heavy shading at evening. 2. Inverter 6 being RMA'd. 3. Inverter 17 being RMA'd. 4. Inverter 14 being RMA'd. 5. Meter was not reporting full production of inverters for whole month. | 2. SR108914 3. SR107710 4. SR105254 5. SR106156 | 2. Pending 3. Pending 4. Pending 5. Pending | SR107710 | SR105254 | SR106156
CA: Pleasanton Tec Ctr - Citi | CA | 97157.5 | 104866 | 92.65% | 101301.828 | -4144.328 | -4.091% | 104092 | -6934.5 | -6.662%
CA: Rancho Cordova - Citi | CA | 149343.36 | 171967 | 86.84% | 125328.603 | 24014.757 | 19.16% | 170703.482 | -21360.122 | -12.51% | 1. Production meter reporting energy spikes due to which actual energy value is affected possibly the issue is due to migration of these site from Locus to AE. Reached out to AlsoEnergy (Case # 623267)
CA: S Sacramento Wyndham - Citi | CA | 74591.28 | 92577 | 80.57% | 77696.321 | -3105.041 | -3.996% | 123109.194 | -48517.914 | -39.41% | 1. Production meter reporting energy spikes due to which actual energy value is affected possibly the issue is due to migration of these site from Locus to AE. Reached out to AlsoEnergy (Case # 623267)
CA: Sacramento Point West - Citi | CA | 178762.98 | 178364 | 100.2% | 148586.579 | 30176.401 | 20.31% | 220360.046 | -41597.066 | -18.88% | 1. Inverter 5.4 was offline from 10/01 to 13:30 on 10/08. 2. Production meter reporting energy spikes due to which actual energy value is affected possibly the issue is due to migration of these site from Locus to AE. Reached out to AlsoEnergy (Case # 623267) | 1. SR097653 | 1. Closed
CA: San Jose FHC - Citi | CA | 30703.5 | 37332 | 82.24% | 35592.305 | -4888.805 | -13.74% | 38263 | -7559.5 | -19.76% | 1. All inverters experiencing morning shading issue.
CA: San Jose MOB - Citi | CA | 109510.07 | 61008 | 179.5% | 38122.555 | 71387.515 | 187.3% | 58383.725 | 51126.345 | 87.57% | 1. Production meter reporting energy spikes due to which actual energy value is affected possibly the issue is due to migration of these site from Locus to AE. Reached out to AlsoEnergy (Case # 623267)
CA: Selma - Citi | CA | 14368.19 | 34259 | 41.94% | 27872.149 | -13503.959 | -48.45% | 41389.79 | -27021.6 | -65.29% | 1. Inverters 3 and 4 had morning shading. 2. Production meter reporting energy spikes due to which actual energy value is affected possibly the issue is due to migration of these site from Locus to AE. Reached out to AlsoEnergy (Case # 623267)
CA: Vacaville Hospital | CA | 40628.92 | 237441 | 17.11% | 225674.169 | -185045.249 | -82% | 346755.379 | -306126.459 | -88.28% | 1. Inverters 35 to 47 were offline for whole month and was LOTO'd. 2. Inverter 3 was tripping on and off from 010/07 to 10/16. 3. Production meter reporting energy spikes due to which actual energy value is affected possibly the issue is due to migration of these site from Locus to AE. Reached out to AlsoEnergy (Case # 623267) | 1. SR107287 2. SR109154 | 1. Pending 2. Closed | SR109154
CA: Manteca - KP Manteca Hospital | CA | 68365.38 | 68392 | 99.96% | 66552.11 | 1813.27 | 2.725% | 95941.22 | -27575.84 | -28.74% | 1. Production meter reporting energy spikes due to which actual energy value is affected possibly the issue is due to migration of these site from Locus to AE. Reached out to AlsoEnergy (Case # 623267)
Sacramento - KP South Sacramento HSP | CA | 201681.2 | 0 | #DIV/0! | 191506.622 | 10174.578 | 5.313% | 292516.253 | -90835.053 | -31.05% | 1. Inverter 5.3 was derating intermittently for whole month. 2. Inverter 4.1 was offline for whole month and being RMA'd. 3. Production meter reporting energy spikes due to which actual energy value is affected possibly the issue is due to migration of these site from Locus to AE. Reached out to AlsoEnergy (Case # 623267) | 1. SR106356 2. SR108432 | 1. Pending 2. Pending | SR108432

## Nov
CITI |  |  | PPA Modeled Output | Production VS Acual | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | #DIV/0! | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA |  |  | #DIV/0!
CA: Antioch MC CUP - Citi | CA |  |  | #DIV/0! | [8 empty] | 1. Closed
CA: Clovis - Citi | CA |  |  | #DIV/0!
CA: Elk Grove MOB - Citi | CA |  |  | #DIV/0!
CA: Elk Grove Promenade - Citi | CA |  |  | #DIV/0! | [8 empty] | 1. Pending
CA: Fresno Sequioa - Citi | CA |  |  | #DIV/0!
CA: Fresno MOB - Citi | CA |  |  | #DIV/0! | [8 empty] | 1. Closed
CA: Modesto Bangs - Citi | CA |  |  | #DIV/0!
CA: Napa Data Center - Citi | CA |  |  | #DIV/0! | [8 empty] | 1. Pending 2. Pending
CA: Petaluma MOB - Citi | CA |  |  | #DIV/0! | [8 empty] | 2. Pending 3. Pending 4. Pending 5. Pending
CA: Pleasanton Tec Ctr - Citi | CA |  |  | #DIV/0!
CA: Rancho Cordova - Citi | CA |  |  | #DIV/0!
CA: S Sacramento Wyndham - Citi | CA |  |  | #DIV/0!
CA: Sacramento Point West - Citi | CA |  |  | #DIV/0! | [8 empty] | 1. Closed
CA: San Jose FHC - Citi | CA |  |  | #DIV/0!
CA: San Jose MOB - Citi | CA |  |  | #DIV/0!
CA: Selma - Citi | CA |  |  | #DIV/0!
CA: Vacaville Hospital | CA |  |  | #DIV/0! | [8 empty] | 1. Pending 2. Closed
CA: Manteca - KP Manteca Hospital | CA |  |  | #DIV/0!
Sacramento - KP South Sacramento HSP | CA | [11 empty] | 1. Pending 2. Pending

## Dec
CITI |  |  | PPA Modeled Output | Production VS Acual | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | #DIV/0! | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA |  |  | #DIV/0!
CA: Antioch MC CUP - Citi | CA |  |  | #DIV/0!
CA: Clovis - Citi | CA |  |  | #DIV/0!
CA: Elk Grove MOB - Citi | CA |  |  | #DIV/0!
CA: Elk Grove Promenade - Citi | CA |  |  | #DIV/0!
CA: Fresno Sequioa - Citi | CA |  |  | #DIV/0!
CA: Fresno MOB - Citi | CA |  |  | #DIV/0!
CA: Modesto Bangs - Citi | CA |  |  | #DIV/0!
CA: Napa Data Center - Citi | CA |  |  | #DIV/0!
CA: Petaluma MOB - Citi | CA |  |  | #DIV/0!
CA: Pleasanton Tec Ctr - Citi | CA |  |  | #DIV/0!
CA: Rancho Cordova - Citi | CA |  |  | #DIV/0!
CA: S Sacramento Wyndham - Citi | CA |  |  | #DIV/0!
CA: Sacramento Point West - Citi | CA |  |  | #DIV/0!
CA: San Jose FHC - Citi | CA |  |  | #DIV/0!
CA: San Jose MOB - Citi | CA |  |  | #DIV/0!
CA: Selma - Citi | CA |  |  | #DIV/0!
CA: Vacaville Hospital | CA |  |  | #DIV/0!
CA: Manteca - KP Manteca Hospital | CA |  |  | #DIV/0!
Sacramento - KP South Sacramento HSP | CA

## Sites
Portfolio: | CITI
Site DAS Name | Site | State | Update | DAS
KP6 - Antioch Deer Valley - CN5701 | CA: Antioch Deer Valley - Citi | CA
KP6 - Antioch MC CUP - CN5701 | CA: Antioch MC CUP - Citi | CA
Clovis MOB - CN2950 | CA: Clovis - Citi | CA
Elk Grove MOB - CN73727 | CA: Elk Grove MOB - Citi | CA
Elk Grove Promenade - CN 6950 | CA: Elk Grove Promenade - Citi | CA
Fresno Sequioa Hospital | CA: Fresno Sequioa - Citi | CA
Fresno Medical Offices - CN7201 | CA: Fresno MOB - Citi | CA
Modesto Bangs MOB | CA: Modesto Bangs - Citi | CA
KP - Napa Data Center - CN2250 | CA: Napa Data Center - Citi | CA
Kaiser - Petaluma Medical Office - CN2001 | CA: Petaluma MOB - Citi | CA
Pleasanton PTC - Bldg B - CN470B | CA: Pleasanton Tec Ctr - Citi | CA
Rancho Cordova - Groundmount | CA: Rancho Cordova - Citi | CA
South Sacramento Wyndham CN6014 | CA: S Sacramento Wyndham - Citi | CA
Sacramento Point West MOB | CA: Sacramento Point West - Citi | CA
KP6 - San Jose FHC - CN6320 | CA: San Jose FHC - Citi | CA
KP6 - San Jose MOB - CN6310 | CA: San Jose MOB - Citi | CA
KP6 - Selma Medical Offices - CN8450 | CA: Selma - Citi | CA
Vacaville Hospital - CN6701 | CA: Vacaville Hospital | CA
Kaiser, KP6 - Manteca Hospital | CA: Manteca - KP Manteca Hospital | CA
KP6-South Sacramento Hospital | Sacramento - KP South Sacramento HSP | CA