## Year to Date
Freepoint |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 7669083.0656 | 8956708.374 | -1287625.3084 | -14.38% | 6945406.64 | 723676.4256 | 10.42%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
NY: Coxsackie - State Route 9 West | NY | 7669083.0656 | 8956708.374 | -1287625.3084 | -14.38% | 6945406.64 | 48743.1156 | 0.7018%

## 1st Qtr
Freepoint |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 1566294 | 1784267.686 | -217973.686 | -12.22% | 1812746.14 | -246452.14 | -13.6%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
NY: Coxsackie - State Route 9 West | NY | 1566294 | 1784267.686 | -217973.686 | -12.22% | 1812746.14 | -246452.14 | -13.6%

## 2nd Qtr
Freepoint |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 2515472.9996 | 2866714.041 | -351241.0414 | -12.25% | 2618102.27 | -102629.2704 | -3.92%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
NY: Coxsackie - State Route 9 West | NY | 2515472.9996 | 2866714.041 | -351241.0414 | -12.25% | 2618102.27 | -102629.2704 | -3.92%

## 3rd Qtr
Freepoint |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 2983894 | 3540932.141 | -557038.141 | -15.73% | 1942855.66 | 1041038.34 | 53.58%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
NY: Coxsackie - State Route 9 West | NY | 2983894 | 3540932.141 | -557038.141 | -15.73% | 1942855.66 | 366105.03 | 18.84%

## 4th Qtr
Freepoint |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 603422.066 | 764794.506 | -161372.44 | -21.1% | 571702.57 | 31719.496 | 5.548%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
NY: Coxsackie - State Route 9 West | NY | 603422.066 | 764794.506 | -161372.44 | -21.1% | 571702.57 | 31719.496 | 5.548%

## Jan
Freepoint |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 389555.1223 | 452412.2 | -62857.0777 | -13.89% | 461645.8 | -72090.6777 | -15.62%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
NY: Coxsackie - State Route 9 West | NY | 389555.1223 | 452412.2 | -62857.0777 | -13.89% | 461645.8 | -72090.6777 | -15.62% | 1.Site was offline due to SEL relay open on 01/08 at 00:15 and again back online on 11:30am and again site was offline on 01/08 at 21:15 and technician was able to close the relay, site is back online on 09:45am on 01/09 2.Site was offline due to main switchgear breaker was open on 01/17 at 18:30 and back online at 12:00pm on 01/18 and again site was offline due to breakers open on 01/20 at 06:45am and back online at 12:15pm on 01/21 | 1.SR095386 2.SR095684

## Feb
Freepoint |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 445789.8777 | 493232.2 | -47442.3223 | -9.619% | 585098.4 | -139308.5223 | -23.81%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
NY: Coxsackie - State Route 9 West | NY | 445789.8777 | 493232.2 | -47442.3223 | -9.619% | 585098.4 | -139308.5223 | -23.81% | 1. Site was offline due to SEL relay open on 02/07 at 06:45 and again back online on 15:00 the same day and again site was offline on 02/13 at 09:30 and technician was able to close the relay, site is back online at 14:30 the same day. Site was offline on 02/16 at 21:30 and technician was able to close the relay, site is back online at 14:30 on 02/17/25. 2. Site was offline due to main switchgear breaker was open on 02/17 at 20:00 and back online at 08:30 on 02/18 after technician closed both main switchgear breakers. 3. Site was taken offline for maintenance by Central Hudson at 04:45 on 02/27/25. The technician closed the relay and main switchgear breakers, and the site came back online at 08:15 on 02/28. It went offline again at 10:00 the same day, but the technician closed the relay, and the site was restored at 13:45. 4. Tracker 13 was stuck at 57 degrees throught out the month. | 1. SR096426, SR096887 & SR097178 2. SR097178 3. SR097857 4. SR097989 | SR096887 | SR097178 | SR097178 | SR097857 | SR097989

## Mar
Freepoint |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 730949 | 838623.286 | -107674.286 | -12.84% | 766001.94 | -35052.94 | -4.576%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
NY: Coxsackie - State Route 9 West | NY | 730949 | 838623.286 | -107674.286 | -12.84% | 766001.94 | -35052.94 | -4.576% | 1.Tracker 13 has been stuck since 03/03. On 03/12, technician visited the site and found three trackers stuck. He attempted to power cycle the tracker controller but was unsuccessful and mentioned further troubleshooting is required. 2. Site was offline at 03:40 AM on 03/07. On 03/08 techniain closed the relay and it is back online at 08:30 AM on 03/08. Site was offline again at 07:40 pm on 03/16. On 03/17 techniain closed the relay and it is back online at 12:45pm. 3. Inverter 1.16 is derating at 77kW from 01:30 pm from 03/31. | 1.SR097989 2.SR098252, SR098642 3.SR099223 | SR098252 | SR098642 | SR099223

## Apr
Freepoint |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 858097.832 | 954341.8 | -96243.968 | -10.08% | 835717.68 | 22380.152 | 2.678%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
NY: Coxsackie - State Route 9 West | NY | 858097.832 | 954341.8 | -96243.968 | -10.08% | 835717.68 | 22380.152 | 2.678% | 1. Site was tripped offline on 04/05 at 07:30am and later technician re-energized the site at 10:00am on 04/06. 2. Site was tripped offline on 04/21 at 02:30am and later technician re-energized the site at 09:00am on 04/21. 3. Site was offline from 22:30 on 04/23 and later auto reclosed at 00:00 on 04/24 4. Inverter 1.16 was derating by 77kW compared to its peers for whole month. Tech found a dead fan on inverter so the fan being RMA'd. | 1. SR099441 2. SR100050 3. SR100247 4. SR099223 | SR100050 | SR100247 | SR099223

## May
Freepoint |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 773266.281 | 849092.241 | -75825.96 | -8.93% | 896453.99 | -123187.709 | -13.74%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
NY: Coxsackie - State Route 9 West | NY | 773266.281 | 849092.241 | -75825.96 | -8.93% | 896453.99 | -123187.709 | -13.74% | 1. The site was offline at 09:45 on 05/08 due to Central Hudson had to take the solar site offline to complete emergency repairs. After a technician checked the site on 05/11, closed the relay, and de-energized the site, it came back online at 08:00 on 05/11. 2. Inverter 1.16 was derating by 77 kW compared to its peers. A technician found a dead fan in the inverter, so the fan was RMA'd. Later, on 05/13, a technician returned and replaced the fan. The inverter is now producing with its peer inverters. 3. Inverter 2.12 tripped offline at 13:30 on 05/28, reporting an "Inverter Current Imbalance." The issue has continued throughout the month. | 1. SR101154 2. SR099223 3. SR102046 | SR099223 | SR102046

## Jun
Freepoint |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 884108.8866 | 1063280 | -179171.1134 | -16.85% | 885930.6 | -1821.7134 | -0.2056%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
NY: Coxsackie - State Route 9 West | NY | 884108.8866 | 1063280 | -179171.1134 | -16.85% | 885930.6 | -1821.7134 | -0.2056% | 1. Inverter 1.12 was offline from 18:00 on 06/25 to end of the month. 2. Site was offline from 07:00 on 06/26 to 15:00 on 06/27 due to utility outage. 3. Site was offline from 02:25 on 06/14 to 14:00 on 06/16. 4. Site was offline from 08:00 on 06/03 to 07:00 on 06/04. 5. Site was offline from 00:45 on 06/06 to 09:00 on 06/06. 6. Inverter 2.12 was offline for whole month. | 1. SR103562 2. SR103555 3. SR102981 4. SR102366 5. SR102559 6. SR102046 | SR103555 | SR102981 | SR102366 | SR102559 | SR102046

## Jul
Freepoint |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 932688 | 1163626.111 | -230938.111 | -19.85% | 963211.91 | -30523.91 | -3.169%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
NY: Coxsackie - State Route 9 West | NY | 932688 | 1163626.111 | -230938.111 | -19.85% | 963211.91 | -30523.91 | -3.169% | 1. Inverter 1.12 was offline from 18:00 on 06/25 to end of the month. 2. Inverter 2.12 was offline from 07/01 to 07/03 3.Site tripped offline at 10:00 on 07/04 and came back online at 10:00 07/05 4.Site tripped offline at 15:15 on 07/10 and came back online at 13:00 on 07/11 5.Site tripped offline from 01:00 to 13:15 on 07/15 6.The site tripped offline at 19:24 on 07/17 and came back online at 13:45 on 07/18. It tripped offline again at 17:15 on the same day and was restored at 08:45 on 07/21 7. Inverters 2.1 and 2.2 have tripped offline at 16:30 on 07/25 and inverter 2.2 came back online at 11:15 on 07/28 but inverter 2.1 remained offline. | 1. SR103562 2. SR102046 3. SR104014 4. SR104278 5. SR104428 6. SR104582 7. SR105070 | SR102046 | SR104014 | SR104278 | SR104428 | SR104582 | SR105070

## Aug
Freepoint |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 1141730.79 | 1315221.282 | -173490.492 | -13.19% | 908332.05 | 233398.74 | 25.7%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
NY: Coxsackie - State Route 9 West | NY | 1141730.79 | 1315221.282 | -173490.492 | -13.19% | 908332.05 | 233398.74 | 25.7% | 1.Inverter 2.1 offline from 07/25 2. Inverter 1.12 was offline from 18:00 on 06/25 and came back online at 09:15 on 08/06 3. Inverter 1.3 is derating to 77 kW from 08/18. Displaying External Fan Error fault. Opened case with CPS | 1.SR105070 2.SR103562 , SR105070 3.SR106460 | SR103562 | SR105070 | SR106460

## Sep
Freepoint |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 909475.21 | 1062084.748 | -152609.538 | -14.37% | 746245.01 | 163230.2 | 21.87%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
NY: Coxsackie - State Route 9 West | NY | 909475.21 | 1062084.748 | -152609.538 | -14.37% | 746245.01 | 163230.2 | 21.87% | 1.Inverter 1.3 is derating to 77 kW from 08/18 2.Inverter 2.1 offline from 07/25 | 1.SR106460 2.SR105070 | SR105070

## Oct
Freepoint |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 603422.066 | 764794.506 | -161372.44 | -21.1% | 571702.57 | 31719.496 | 5.548%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
NY: Coxsackie - State Route 9 West | NY | 603422.066 | 764794.506 | -161372.44 | -21.1% | 571702.57 | 31719.496 | 5.548% | 1.Inverter 1.3 is derating to 77 kW from 08/18 2.Inverter 2.1 offline from 07/25 3.Site tripped offline at 13:30 on 10/01 and late back online at 15:30 on 10/02 4.Site has a brief offline from 09:00 to 10:00 on 10/06 | 1.SR106460 2.SR105070 3.SR108824 4.SR109084 | 1.Pending 2.Pending 3.Closed 4.Closed | SR105070 | SR108824 | SR109084

## Nov
Freepoint |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
NY: Coxsackie - State Route 9 West | NY

## Dec
Freepoint |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
NY: Coxsackie - State Route 9 West | NY

## Sites
Portfolio: | Freepoint
Site DAS Name | Site | State | Update | DAS
Coxsackie | NY: Coxsackie - State Route 9 West | NY | AEF | PowerTrack