## Year to Date
Kendall Sustainable Infrastructure, LLC |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 9264551.1987 | 8212634.302 | 1051916.8967 | 12.81% | 9734746.598 | -470195.3993 | -4.83%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Barre - 56 Bridge St | VT | 638914.5 | 646123.593 | -7209.093 | -1.116% | 650285.614 | -11371.114 | -1.749%
Barre - 181 Allen St | VT | 622261 | 640097.745 | -17836.745 | -2.787% | 610263.406 | 0 | 0%
West Greenwich - 200 Robin Hollow Rd | RI | 3511375.5737 | 4490750.939 | -979375.3653 | -21.81% | 4663988.07 | -1152612.4963 | -24.71%
Rockingham - 25 Jackson Rd | VT | 560624.5 | 608035 | -47410.5 | -7.797% | 662269.088 | 0 | 0%
East Hardwick - 55 Arsene Ave | VT | 565134.75 | 602824.71 | -37689.96 | -6.252% | 595762.145 | -30627.395 | -5.141%
Red Hook - 44 MM Ham Memorial Firehouse Ln | NY | 2137958 | 0 | 2137958 |  | 1903094.895 | 0 | 0%
Millbrook - Bacon Triangle (Cary Institute) | NY | 583682 | 575593.66 | 8088.34 | 1.405% | 0 | 252969
Rockingham - 2029 Rockingham Rd | VT | 644600.875 | 649208.655 | -4607.78 | -0.7098% | 649083.38 | 0 | 0%

## 1st Qtr
Kendall Sustainable Infrastructure, LLC |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Barre - 56 Bridge St | VT | 0 | 0 | 0 |  | 0 | 0
Barre - 181 Allen St | VT | 0 | 0 | 0 |  | 0 | 0
West Greenwich - 200 Robin Hollow Rd | RI | 0 | 0 | 0 |  | 0 | 0
Rockingham - 25 Jackson Rd | VT | 0 | 0 | 0 |  | 0 | 0
East Hardwick - 55 Arsene Ave | VT | 0 | 0 | 0 |  | 0 | 0
Red Hook - 44 MM Ham Memorial Firehouse Ln | NY | 0 | 0 | 0 |  | 0 | 0
Millbrook - Bacon Triangle (Cary Institute) | NY | 0 | 0 | 0 |  | 0 | 0
Rockingham - 2029 Rockingham Rd | VT | 0 | 0 | 0 |  | 0 | 0

## 2nd Qtr
Kendall Sustainable Infrastructure, LLC |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 3825247.285 | 3494397.042 | 330850.243 | 9.468% | 4077018.962 | -251771.677 | -6.175%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Barre - 56 Bridge St | VT | 257353.375 | 260273.79 | -2920.415 | -1.122% | 274711.45 | -17358.075 | -6.319%
Barre - 181 Allen St | VT | 252961 | 256404.67 | -3443.67 | -1.343% | 275263.88 | -22302.88 | -8.102%
West Greenwich - 200 Robin Hollow Rd | RI | 1493491.16 | 1919520.6 | -426029.44 | -22.19% | 2161204 | -667712.84 | -30.9%
Rockingham - 25 Jackson Rd | VT | 221205.5 | 275003 | -53797.5 | -19.56% | 262927.521 | -41722.021 | -15.87%
East Hardwick - 55 Arsene Ave | VT | 233072 | 275137.182 | -42065.182 | -15.29% | 239540.318 | -6468.318 | -2.7%
Red Hook - 44 MM Ham Memorial Firehouse Ln | NY | 855646 | 0 | 855646 |  | 570788.303 | 284857.697 | 49.91%
Millbrook - Bacon Triangle (Cary Institute) | NY | 252969 | 250984.89 | 1984.11 | 0.7905% | 0 | 252969
Rockingham - 2029 Rockingham Rd | VT | 258549.25 | 257072.91 | 1476.34 | 0.5743% | 292583.49 | -34034.24 | -11.63%

## 3rd Qtr
Kendall Sustainable Infrastructure, LLC |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 4313564.295 | 3811864.492 | 501699.803 | 13.16% | 4568899.586 | -255335.291 | -5.589%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Barre - 56 Bridge St | VT | 307412.125 | 310707.033 | -3294.908 | -1.06% | 312500.364 | -5088.239 | -1.628%
Barre - 181 Allen St | VT | 297868 | 307592.415 | -9724.415 | -3.161% | 271335.336 | 26532.664 | 9.779%
West Greenwich - 200 Robin Hollow Rd | RI | 1571509.92 | 2093367.139 | -521857.219 | -24.93% | 2038142.77 | -466632.85 | -22.9%
Rockingham - 25 Jackson Rd | VT | 267546.5 | 268114 | -567.5 | -0.2117% | 315670.38 | -48123.88 | -15.24%
East Hardwick - 55 Arsene Ave | VT | 284527.5 | 262488.2 | 22039.3 | 8.396% | 288314.724 | -3787.224 | -1.314%
Red Hook - 44 MM Ham Memorial Firehouse Ln | NY | 1020235 | 0 | 1020235 |  | 1055124.532 | -34889.532 | -3.307%
Millbrook - Bacon Triangle (Cary Institute) | NY | 259077 | 261026.26 | -1949.26 | -0.7468% | 0 | 0
Rockingham - 2029 Rockingham Rd | VT | 305388.25 | 308569.445 | -3181.195 | -1.031% | 287811.48 | 17576.77 | 6.107%

## 4th Qtr
Kendall Sustainable Infrastructure, LLC |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 1125739.6187 | 906372.768 | 219366.8507 | 24.2% | 1088828.05 | 36911.5687 | 3.39%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Barre - 56 Bridge St | VT | 74149 | 75142.77 | -993.77 | -1.323% | 63073.8 | 11075.2 | 17.56%
Barre - 181 Allen St | VT | 71432 | 76100.66 | -4668.66 | -6.135% | 63664.19 | 7767.81 | 12.2%
West Greenwich - 200 Robin Hollow Rd | RI | 446374.4937 | 477863.2 | -31488.7063 | -6.589% | 464641.3 | -18266.8063 | -3.931%
Rockingham - 25 Jackson Rd | VT | 71872.5 | 64918 | 6954.5 | 10.71% | 83671.187 | -11798.687 | -14.1%
East Hardwick - 55 Arsene Ave | VT | 47535.25 | 65199.328 | -17664.078 | -27.09% | 67907.103 | -20371.853 | -30%
Red Hook - 44 MM Ham Memorial Firehouse Ln | NY | 262077 | 0 | 262077 |  | 277182.06 | -15105.06 | -5.45%
Millbrook - Bacon Triangle (Cary Institute) | NY | 71636 | 63582.51 | 8053.49 | 12.67% | 0 | 0
Rockingham - 2029 Rockingham Rd | VT | 80663.375 | 83566.3 | -2902.925 | -3.474% | 68688.41 | 11974.965 | 17.43%

## Jan
Kendall Sustainable Infrastructure, LLC |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barre - 56 Bridge St | VT
Barre - 181 Allen St | VT
West Greenwich - 200 Robin Hollow Rd | RI
Rockingham - 25 Jackson Rd | VT
East Hardwick - 55 Arsene Ave | VT
Red Hook - 44 MM Ham Memorial Firehouse Ln | NY
Millbrook - Bacon Triangle (Cary Institute) | NY
Rockingham - 2029 Rockingham Rd | VT

## Feb
Kendall Sustainable Infrastructure, LLC |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barre - 56 Bridge St | VT
Barre - 181 Allen St | VT
West Greenwich - 200 Robin Hollow Rd | RI
Rockingham - 25 Jackson Rd | VT
East Hardwick - 55 Arsene Ave | VT
Red Hook - 44 MM Ham Memorial Firehouse Ln | NY
Millbrook - Bacon Triangle (Cary Institute) | NY
Rockingham - 2029 Rockingham Rd | VT

## Mar
Kendall Sustainable Infrastructure, LLC |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barre - 56 Bridge St | VT
Barre - 181 Allen St | VT
West Greenwich - 200 Robin Hollow Rd | RI
Rockingham - 25 Jackson Rd | VT
East Hardwick - 55 Arsene Ave | VT
Red Hook - 44 MM Ham Memorial Firehouse Ln | NY
Millbrook - Bacon Triangle (Cary Institute) | NY
Rockingham - 2029 Rockingham Rd | VT

## Apr
Kendall Sustainable Infrastructure, LLC |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 1254689.95 | 1140934.688 | 113755.262 | 9.97% | 1286742.433 | -32052.483 | -2.491%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barre - 56 Bridge St | VT | 83381.375 | 83998.98 | -617.605 | -0.7353% | 83257.64 | 123.735 | 0.1486%
Barre - 181 Allen St | VT | 81697 | 83258.26 | -1561.26 | -1.875% | 87420.52 | -5723.52 | -6.547%
West Greenwich - 200 Robin Hollow Rd | RI | 491626.2 | 634400.1 | -142773.9 | -22.51% | 619543.5 | -127917.3 | -20.65% | 1. Inverter voltages dropped to zero at 5:30AM on 04/29. Relay and meter were not communicating and battery mode activated. Reached out to the utility. ROC remotely reset the site through the AE PT DAS portal and the site was online at 09:00AM on 05/02. | 1.SR100628
Rockingham - 25 Jackson Rd | VT | 74590 | 87042 | -12452 | -14.31% | 89924.717 | -15334.717 | -17.05% | 1.Inverter 8 was not communicating since 3/28. Per the meter, the inverter was offline. Ameresco will address during PM. 2. Inverter 7 was underproducing by 4kw since 7/9/24. As per SR100535 inverter supposed to receive a new powerhead. 3. Inverter 2 was underperformed by approximately 45 kW compared to its peer inverters at 11:30 on 04/30 due to fuses left open during PM. After the technician installed and re-energized the fuses, the inverter resumed production at 16:25 on 05/01 | 1.SR100533 2.SR100535 3.SR100799 | SR100535 | SR100799
East Hardwick - 55 Arsene Ave | VT | 71924.75 | 86982.438 | -15057.688 | -17.31% | 76652.669 | -4727.919 | -6.168% | 1. The site was offline from 6:15AM to 8:30AM on 04/20. 2. Site production was low on 04/03, 04/05, 04/06, 04/08, 04/09, 04/11 due to rain.
Red Hook - 44 MM Ham Memorial Firehouse Ln | NY | 284786 | 0 | 284786 |  | 238260.847 | 46525.153 | 19.53% | 1.IMT BOM sensor stopped communicating on 4/26 at 22:00. Issue persisted for rest of the month. 2.Inverter D is intermittently derating to 75 kW during peak hours due to a "Fan Error" since the site was commissioned. 3. The meter has been experiencing intermittent communication throughout the day since the site was commissioned. | 1.SR100562 2.SR100634 3.SR100663 | SR100634 | SR100663
Millbrook - Bacon Triangle (Cary Institute) | NY | 78915 | 78298 | 617 | 0.788% | 0 | 78915
Rockingham - 2029 Rockingham Rd | VT | 87769.625 | 86954.91 | 814.715 | 0.9369% | 91682.54 | -3912.915 | -4.268%

## May
Kendall Sustainable Infrastructure, LLC |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 1215870.25 | 1079929.554 | 135940.696 | 12.59% | 1222517.289 | -6647.039 | -0.5437%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barre - 56 Bridge St | VT | 76390.375 | 76875.79 | -485.415 | -0.6314% | 100183.6 | -23793.225 | -23.75% | 1. Low production due to rain
Barre - 181 Allen St | VT | 75443 | 76135.21 | -692.21 | -0.9092% | 93152.98 | -17709.98 | -19.01% | 1. Low production due to rain
West Greenwich - 200 Robin Hollow Rd | RI | 501972 | 587438 | -85466 | -14.55% | 748654 | -246682 | -32.95% | 1. The site went offline at 05:45 on 04/29. Later, the ROC remotely reset the site through the AE PT DAS portal, and it came back online at 08:45 on 05/02. 2. The site was taken offline from 07:30 to 09:30 on 05/21 because the main breaker tripped open while the O&M team was working on-site to replace the EMI units. 3. The site was tripped offline at 17:45 on 05/30. | 1. SR100628 2. SR101774 | SR101774
Rockingham - 25 Jackson Rd | VT | 65178 | 93350 | -28172 | -30.18% | 76360.471 | -11182.471 | -14.64% | 1. Inverter 2 was underperforming by approximately 45 kW compared to its peer inverters at 11:30 on 04/30 due to fuses left open during PM. After the technician installed and re-energized the fuses, the inverter resumed production at 16:25 on 05/01. 2. Inverter 8 was offline since 4/28 later back online at 12:45 on 05/22. 3. Inverter 7 is derated by 4kW since 7/9/24. 4.Inveretr 2 was offline at 07:00 on 05/19. later technicion checked into the site on 05/20 he found that breaker was tripped open. Then inverter has been LOTO'd and parts have been Rma'd. | 1. SR100799 2. SR100533 3. SR100535 4. SR101684 | SR100533 | SR100535 | SR101684
East Hardwick - 55 Arsene Ave | VT | 69424.25 | 91507.594 | -22083.344 | -24.13% | 72701.236 | -3276.986 | -4.507% | 1. Low production due to rain
Red Hook - 44 MM Ham Memorial Firehouse Ln | NY | 270029 | 0 | 270029 |  | 32083.952 | 237945.048 | 741.6% | 1. Inverter D is intermittently derating to 75 kW during peak hours due to a "Fan Error" since the site was commissioned. 2. The meter has been experiencing intermittent communication throughout the day since the site was commissioned. 3. Inverter M was derating by 75 kW during peak hours, possibly due to a 'Fan Fault.' A technician checked the site on 05/13 and found one faulty fan, which was then replaced. After the replacement, the inverter resumed producing with its peers. 4. The IMT BOM sensor stopped communicating at 22:00 on 04/26. After rebooting the DAS, the BOM sensor resumed operation on 05/28. | 1. SR100634 2. SR100663 3. SR101394 4. SR100562 | SR100663 | SR101394 | SR100562
Millbrook - Bacon Triangle (Cary Institute) | NY | 82189 | 79568.84 | 2620.16 | 3.293% | 0 | 82189
Rockingham - 2029 Rockingham Rd | VT | 75244.625 | 75054.12 | 190.505 | 0.2538% | 99381.05 | -24136.425 | -24.29% | 1. Low production due to rain

## Jun
Kendall Sustainable Infrastructure, LLC |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 1354687.085 | 1273532.8 | 81154.285 | 6.372% | 1567759.24 | -213072.155 | -13.59%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barre - 56 Bridge St | VT | 97581.625 | 99399.02 | -1817.395 | -1.828% | 91270.21 | 6311.415 | 6.915%
Barre - 181 Allen St | VT | 95821 | 97011.2 | -1190.2 | -1.227% | 94690.38 | 1130.62 | 1.194%
West Greenwich - 200 Robin Hollow Rd | RI | 499892.96 | 697682.5 | -197789.54 | -28.35% | 793006.5 | -293113.54 | -36.96% | 1. The site tripped offline at 17:45 on 06/11 and came back online at 10:15 on 06/12. Again, the site tripped offline at 07:15 on 06/14 and came back online at 13:15 on 06/15 by a remote reset. 2. The site was offline from 05:15 on 06/16 to 10:30 on 06/19 due to a planned outage. 3. The site tripped offline at 02:45 on 06/30 and was restored remotely at 13:30 on the same day. | 1. SR102885 2. SR102890 3. SR103729 | SR102890 | SR103729
Rockingham - 25 Jackson Rd | VT | 81437.5 | 94611 | -13173.5 | -13.92% | 96642.333 | -15204.833 | -15.73% | 1. Inverter 2 went offline at 07:00 on 05/19, and it was found that the breaker had tripped. The inverter has since been LOTO'd, and the parts have been RMA'd. 2. Inverter 8 tripped offline at 15:05 from 06/22 and through out the month 3.Inverter 10 string 5 as offline | 1. SR101684 2. SR100533 3. SR103855 | SR100533 | SR103855
East Hardwick - 55 Arsene Ave | VT | 91723 | 96647.15 | -4924.15 | -5.095% | 90186.413 | 1536.587 | 1.704%
Red Hook - 44 MM Ham Memorial Firehouse Ln | NY | 300831 | 0 | 300831 |  | 300443.504 | 387.496 | 0.129% | 1. Inverter D is intermittently derating to 75 kW during peak hours due to a "Fan Error" since the site was commissioned. 2. The meter has been experiencing intermittent communication throughout the day since the site was commissioned. | 1. SR100634 2. SR100663 | SR100663
Millbrook - Bacon Triangle (Cary Institute) | NY | 91865 | 93118.05 | -1253.05 | -1.346% | 0 | 91865
Rockingham - 2029 Rockingham Rd | VT | 95535 | 95063.88 | 471.12 | 0.4956% | 101519.9 | -5984.9 | -5.895%

## Jul
Kendall Sustainable Infrastructure, LLC |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 1261468.125 | 1341989.47 | -80521.345 | -6% | 1646233.921 | -384765.796 | -23.37%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barre - 56 Bridge St | VT | 104865.875 | 107074.8 | -2208.925 | -2.063% | 115765 | -10899.125 | -9.415% | 1.38 damaged modules were identified during a previous PM. As per PM, assess their current production impact and recommend replacement. | 1.SR103695
Barre - 181 Allen St | VT | 102147 | 103973 | -1826 | -1.756% | 98503.67 | 3643.33 | 3.699%
West Greenwich - 200 Robin Hollow Rd | RI | 322854.75 | 742575.7 | -419720.95 | -56.52% | 758211.4 | -435356.65 | -57.42% | 1. The site has been performing at half of its capacity throughout the month, as MPPT 1 is offline for each inverter. 2. The site was offline from 08:59 to 10:56 on 07/29 while a technician was on site for preventive maintenance work. | 1. SR104086 2. PM14450
Rockingham - 25 Jackson Rd | VT | 83586 | 99172 | -15586 | -15.72% | 107613.881 | -24027.881 | -22.33% | 1. Inverter 7 has been underperforming by 4 kW since 07/09/2024. 2. Inverter 2 went offline at 07:00 on 05/19 and came back online at 11:15 on 07/24. 3. Inverter 10 was underperforming by 4 kW due to a string down from 15:00 on 07/14 and later resumed normal operation along with its peers from 07/17. 4. Inverter 8 tripped offline at 15:05 on 06/22, reporting 'No Grid', and came back online at 16:25 on 07/17. It tripped offline again at 12:10 on 07/18. The inverter 8 breaker was later replaced with the inverter 10 breaker, and inverter 8 came back online at 12:55 on 07/24. Inverter 10 remained offline from 07/24 until the end of the month. 5. Inverter 7 tripped offline due to an 'ACFI Fault' at 16:15 on 07/15 and later came back online at 16:00 on 07/17. | 1. SR100535 2. SR101684 3. SR103855 4. SR104621 5. SR104507 | SR101684 | SR103855 | SR104621 | SR104507
East Hardwick - 55 Arsene Ave | VT | 95980 | 95788.93 | 191.07 | 0.1995% | 96618.018 | -638.018 | -0.6604% | 1. The meter was intermittently not reporting Phase C current throughout the month. | 1. SR103008
Red Hook - 44 MM Ham Memorial Firehouse Ln | NY | 350514 | 0 | 350514 |  | 365070.852 | -14556.852 | -3.987% | 1. Inverter D is intermittently derating to 75 kW during peak hours due to a "Fan Error" since the site was commissioned. 2. The meter has been experiencing intermittent communication since the site was commissioned. | 1. SR100634 2. SR100633 | SR100633
Millbrook - Bacon Triangle (Cary Institute) | NY | 97068 | 89112.14 | 7955.86 | 8.928% | N/A |  |  | 1. Inverter 7 has been underperforming by approximately 15 kW during peak hours throughout the month. 2. Inverter 8 started producing late at 13:10 on 07/02. Again, on 07/10, it started producing late at 13:15. | 1. SR103834 2. SR103907 | SR103907
Rockingham - 2029 Rockingham Rd | VT | 104452.5 | 104292.9 | 159.6 | 0.153% | 104451.1 | 1.4 | 0.00134%

## Aug
Kendall Sustainable Infrastructure, LLC |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 1643492.87 | 1378570.98 | 264921.89 | 19.22% | 1585587.095 | 57905.775 | 3.652%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barre - 56 Bridge St | VT | 106299.75 | 107149.1 | -849.35 | -0.7927% | 108723.5 | -2423.75 | -2.229% | 1.38 damaged modules were identified during a previous PM. As per PM, assess their current production impact and recommend replacement. | 1.SR103695
Barre - 181 Allen St | VT | 103067 | 106877.3 | -3810.3 | -3.565% | 94975.52 | 8091.48 | 8.52%
West Greenwich - 200 Robin Hollow Rd | RI | 679164.62 | 772035.1 | -92870.48 | -12.03% | 703956.8 | -24792.18 | -3.522% | 1. Site is producing with its full capacity from 08/05 2.Site tripped offline at 00:15 on 08/20 and later back online at 08:30 on 08/20 and again site tripped offline from 05:00 to 17:30 on 08/21 | 1.SR104086 2.SR106528 | SR106528
Rockingham - 25 Jackson Rd | VT | 97846 | 93447 | 4399 | 4.707% | 111494.659 | -13648.659 | -12.24% | 1.Inverter 2 has tripped offline at 12:35 on 08/12 and back online at 10:15 on 08/15 2. Inverter 7 has been underperforming by 4 kW since 07/09/2024. 3.Inverter 4 tripped offline at 11:35 on 08/21 4. Inverter 9 tripped offline at 11:45 on 08/30 and reporting "No Grid" in Locus. AC voltages dropped to zero, possibly disconnected from grid. | 1.SR106167 2.SR100535 3.SR106663 | SR100535 | SR106663
East Hardwick - 55 Arsene Ave | VT | 102067.5 | 94755.17 | 7312.33 | 7.717% | 100920.056 | 1147.444 | 1.137%
Red Hook - 44 MM Ham Memorial Firehouse Ln | NY | 358400 | 0 | 358400 |  | 364874.06 | -6474.06 | -1.774% | 1. Inverter D is intermittently derating to 75 kW during peak hours due to a "Fan Error" since the site was commissioned. 2. The meter has been experiencing intermittent communication since the site was commissioned. | 1.SR100634 2. SR100633 | SR100633
Millbrook - Bacon Triangle (Cary Institute) | NY | 89317 | 95092.31 | -5775.31 | -6.073% | N/A |  |  | 1. Inverter 7 has been underperforming by approximately 15 kW during peak hours throughout the month. 2.Meter Phase - 1 power dropping intermittently possibly due to CT heating issues, which is preventing the meter from capturing the total inverter production. | 1.SR103834 2. SR107214 | SR107214
Rockingham - 2029 Rockingham Rd | VT | 107331 | 109215 | -1884 | -1.725% | 100642.5 | 6688.5 | 6.646%

## Sep
Kendall Sustainable Infrastructure, LLC |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 1408603.3 | 1091304.042 | 317299.258 | 29.08% | 1337078.57 | 71524.73 | 5.349%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barre - 56 Bridge St | VT | 96246.5 | 96483.133 | -236.633 | -0.2453% | 88011.864 | 8234.636 | 9.356%
Barre - 181 Allen St | VT | 92654 | 96742.115 | -4088.115 | -4.226% | 77856.146 | 14797.854 | 19.01% | 1.Site was producing as expected and Actual vs forecasted delta is showing 19% due to forecatsed energy recording low possibly due to data glitch (similar event observe last years).
West Greenwich - 200 Robin Hollow Rd | RI | 569490.55 | 578756.339 | -9265.789 | -1.601% | 575974.57 | -6484.02 | -1.126%
Rockingham - 25 Jackson Rd | VT | 86114.5 | 75495 | 10619.5 | 14.07% | 96561.84 | -10447.34 | -10.82% | 1. Inverter 7 was underproducing by 5kW for whole month. 2. Inverter 7 tripped offline at 12:45 on 09/28 | 1. SR107532 2. SR108700 | SR108700
East Hardwick - 55 Arsene Ave | VT | 86480 | 71944.1 | 14535.9 | 20.2% | 90776.65 | -4296.65 | -4.733% | 1. The meter is not reporting the full production of the inverters because the Phase C current has dropped to 3 amps since 11:45 on 09/26. | 1. SR108749
Red Hook - 44 MM Ham Memorial Firehouse Ln | NY | 311321 | 0 | 311321 |  | 325179.62 | -13858.62 | -4.262% | 1. Inverter D is intermittently derating to 75 kW during peak hours due to a "Fan Error" since the site was commissioned. 2. The meter has been experiencing intermittent communication since the site was commissioned. | 1.SR100634 2. SR100633 | SR100633
Millbrook - Bacon Triangle (Cary Institute) | NY | 72692 | 76821.81 | -4129.81 | -5.376% | N/A |  |  | 1. Inverter 7 was derating by 10kW for whole month. 2.Meter Phase - 1 power dropping intermittently possibly due to CT heating issues, which is preventing the meter from capturing the total inverter production. On 09/10 technician Underperformance appears linked to high vegetation. | 1. SR108729 2. SR103834 | SR103834
Rockingham - 2029 Rockingham Rd | VT | 93604.75 | 95061.545 | -1456.795 | -1.532% | 82717.88 | 10886.87 | 13.16% | 1.Site was producing as expected and Actual vs forecasted delta is showing 13% due to forecatsed energy recording low possibly due to data glitch (similar event observe last years).

## Oct
Kendall Sustainable Infrastructure, LLC |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 1125739.6187 | 906372.768 | 219366.8507 | 24.2% | 1088828.05 | 36911.5687 | 3.39%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Barre - 56 Bridge St | VT | 74149 | 75142.77 | -993.77 | -1.323% | 63073.8 | 11075.2 | 17.56%
Barre - 181 Allen St | VT | 71432 | 76100.66 | -4668.66 | -6.135% | 63664.19 | 7767.81 | 12.2%
West Greenwich - 200 Robin Hollow Rd | RI | 446374.4937 | 477863.2 | -31488.7063 | -6.589% | 464641.3 | -18266.8063 | -3.931%
Rockingham - 25 Jackson Rd | VT | 71872.5 | 64918 | 6954.5 | 10.71% | 83671.187 | -11798.687 | -14.1% | 1. Inverter 7 was derated by 5kW on high irradiance day. Inverters 5, 6 and 7 were offline from 15:05 on 10/09 to 11:35 on 10/14 and inverter 7 remained offline through out the month. | 1. SR109012, SR109329 | 1.Pending | SR109329
East Hardwick - 55 Arsene Ave | VT | 47535.25 | 65199.328 | -17664.078 | -27.09% | 67907.103 | -20371.853 | -30% | 1.The meter is not reporting the full production of the inverters because the Phase C current has dropped to 3 amps since 11:45 on 09/26. Resolved 10/22. 2. Inverter 8 was offline from 10/17. | 1. SR108749 2. SR109703 | 1.Closed 2.Pending
Red Hook - 44 MM Ham Memorial Firehouse Ln | NY | 262077 | 0 | 262077 |  | 277182.06 | -15105.06 | -5.45%
Millbrook - Bacon Triangle (Cary Institute) | NY | 71636 | 63582.51 | 8053.49 | 12.67% | N/A
Rockingham - 2029 Rockingham Rd | VT | 80663.375 | 83566.3 | -2902.925 | -3.474% | 68688.41 | 11974.965 | 17.43%

## Nov
Kendall Sustainable Infrastructure, LLC |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barre - 56 Bridge St | VT
Barre - 181 Allen St | VT
West Greenwich - 200 Robin Hollow Rd | RI
Rockingham - 25 Jackson Rd | VT
East Hardwick - 55 Arsene Ave | VT
Red Hook - 44 MM Ham Memorial Firehouse Ln | NY
Millbrook - Bacon Triangle (Cary Institute) | NY
Rockingham - 2029 Rockingham Rd | VT

## Dec
Kendall Sustainable Infrastructure, LLC |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barre - 56 Bridge St | VT
Barre - 181 Allen St | VT
West Greenwich - 200 Robin Hollow Rd | RI
Rockingham - 25 Jackson Rd | VT
East Hardwick - 55 Arsene Ave | VT
Red Hook - 44 MM Ham Memorial Firehouse Ln | NY
Millbrook - Bacon Triangle (Cary Institute) | NY
Rockingham - 2029 Rockingham Rd | VT

## Sites
Portfolio: | Kendall Sustainable Infrastructure, LLC
Site DAS Name | Site | State | Update | DAS
8.02) Novus Bridge Solar, LLC | Barre - 56 Bridge St | VT | AEF | PowerTrack
8.03) Novus Allen Solar, LLC | Barre - 181 Allen St | VT | AEF | PowerTrack
5.03) University Solar 2, LLC | West Greenwich - 200 Robin Hollow Rd | RI | AEF | PowerTrack
1.02) Novus Rockingham Solar, LLC | Rockingham - 25 Jackson Rd | VT |  | LocusNOC
3.01) Novus Hardwick | East Hardwick - 55 Arsene Ave | VT |  | LocusNOC
3.02) Red Hook Solar | Red Hook - 44 MM Ham Memorial Firehouse Ln | NY |  | LocusNOC
2.05) Bacon Triangle (YSG Cary) | Millbrook - Bacon Triangle (Cary Institute) | NY |  | Meto Control
10.02) Novus Rock Pit Solar LLC | Rockingham - 2029 Rockingham Rd | VT | AEF | PowerTrack