## Year to Date
Wells Fargo |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total | 18297673.2396 | 17754702.1678 | 542971.0718 | 3.058% | 19304452.0801 | -1006778.8405 | -5.215%
Site | Actual | Expected | Delta | % | Forecasted | Delta | %
CA | 1244156.1186 | 1119361.153 | 124794.9656 | 11.15% | 1339542.35 | -95386.2314 | -7.121%
CO | 248727.9007 | 0 | 248727.9007 |  | 254567.073 | -5839.1723 | -2.294%
CT | 12615.4397 | 14675 | -2059.5603 | -14.03% | 16175.0992 | -3559.6595 | -22.01%
FL | 12301.9964 | 41801.923 | -29499.9266 | -70.57% | 47905 | -35603.0036 | -74.32%
IA | 2435900 | 2536585.37 | -100685.37 | -3.969% | 2544382.94 | -108482.94 | -4.264%
NC | 2932381 | 3096606.652 | -164225.652 | -5.303% | 2996646.918 | -64265.918 | -2.145%
NJ | 757317.6969 | 743779.1498 | 13538.5471 | 1.82% | 824540.1509 | -67222.454 | -8.153%
TX | 6358173.6858 | 6284625.585 | 73548.1008 | 1.17% | 7009393.449 | -651219.7632 | -9.291%
AZ | 4296099.4016 | 3917267.335 | 378832.0666 | 9.671% | 4208968.1 | 87131.3016 | 2.07%
62% of the sites (41 of the 66 sites from 2024; 81 sites as of September) outperformed vs September 2024 information.
17% of the sites (14 of the 81 sites) appear to have inaccurate modeling information. I will be reviewing the PVsyst information, assuming it was made available to O&M.
Sites with positive performance (actual vs expected):
N Black Canyon Hwy, Phoenix - North
AZ: Tucson - RINCON
CA: Ventura - BUENAVENTURA
NJ: Barnegat - WF
Sites with under-performance issues (actual vs. expected):
|  | FL:Hialeah Gardens |  |  | SR098791 - re-power
|  | TX: San Antonio - Ops Ctr GM |  |  | SR108958 - pending return visit
|  | NJ: Holmdel - WF |  |  | SR100979 - pending return visit
|  | NJ: Mahwah |  |  | SR100593 -pending return visit
|  | NJ: Middletown |  |  | SR100592 -pending return visit
|  | CA: Sacramento - Arden Fair Mall |  |  | Nothing mechanical
Most common issues seen:
Communication issues on equipment (meters, weather stations, etc). - Followed up with AE Support. Will address next time onsite.
String issues on several inverters of various capacities.
Plan to remediate:
Operations is reviewing all open SRs and prioritizing accordingly.
|  | 81 sites | 2025
|  |  | Actual | Expected | Delta | % | Forecasted | Delta | %
|  |  | 2009886 | 1966799 | 43087 | 2% | 2174763 | -164877 | -8%
|  | 66 Sites | 2024
|  |  | Actual | Expected | Delta | % | Forecasted | Delta | %
|  |  | 1566588 | 1547344 | 19244 | 1% | 1863295 | -296707 | -16%

## 1st Qtr
Wells Fargo |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total | 4617003.6626 | 4690988.346 | -73984.6834 | -1.577% | 4770066.956 | -153063.2934 | -3.209%
State | Actual | Expected | Delta | % | Forecasted | Delta | %
CA | 323915.6626 | 315455.346 | 8460.3166 | 2.682% | 335470.956 | -11555.2934 | -3.444%
CO | 54979 | 0 | 54979 |  | 55712 | -733 | -1.316%
CT | 1851 | 5169 | -3318 | -64.19% | 2894 | -1043 | -36.04%
FL | 6795 | 10103 | -3308 | -32.74% | 12194 | -5399 | -44.28%
IA | 613482 | 684039 | -70557 | -10.31% | 584112 | 29370 | 5.028%
NC | 815835 | 857586 | -41751 | -4.868% | 817329 | -1494 | -0.1828%
NJ | 170720 | 178697 | -7977 | -4.464% | 163693 | 7027 | 4.293%
TX | 1715281 | 1848664 | -133383 | -7.215% | 1849861 | -134580 | -7.275%
AZ | 914145 | 791275 | 122870 | 15.53% | 948801 | -34656 | -3.653%

## 2nd Qtr
Wells Fargo |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total | 6006772.0843 | 5524974.265 | 481797.8193 | 8.72% | 6241087.437 | -234315.3527 | -3.754%
State | Actual | Expected | Delta | % | Forecasted | Delta | %
CA | 454465.441 | 384953.35 | 69512.091 | 18.06% | 468977.558 | -14512.117 | -3.094%
CO | 86882 | 0 | 86882 |  | 91827 | -4945 | -5.385%
CT | 4927 | 5259 | -332 | -6.313% | 6003 | -1076 | -17.92%
FL | 2625 | 13157 | -10532 | -80.05% | 16185 | -13560 | -83.78%
IA | 832182 | 787358 | 44824 | 5.693% | 856428 | -24246 | -2.831%
NC | 1111186 | 1158864 | -47678 | -4.114% | 1153402 | -42216 | -3.66%
NJ | 247246 | 248112 | -866 | -0.349% | 297565 | -50319 | -16.91%
TX | 1671673.6433 | 1446898.915 | 224774.7283 | 15.53% | 1825798.879 | -154125.2357 | -8.442%
AZ | 1595585 | 1480372 | 115213 | 7.783% | 1524901 | 70684 | 4.635%

## 3rd Qtr
Wells Fargo |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total | 5987266.11 | 5805494 | 181772.11 | 3.131% | 6414877.666 | -427611.556 | -6.666%
State | Actual | Expected | Delta | % | Forecasted | Delta | %
CA | 376889.11 | 337724 | 39165.11 | 11.6% | 429928.666 | -53039.556 | -12.34%
CO | 84768 | 0 | 84768 |  | 85474 | -706 | -0.826%
CT | 5110 | 3670 | 1440 | 39.24% | 5963 | -853 | -14.3%
FL | 2210 | 13583 | -11373 | -83.73% | 15389 | -13179 | -85.64%
IA | 795280 | 838660 | -43380 | -5.173% | 872315 | -77035 | -8.831%
NC | 734629 | 782827 | -48198 | -6.157% | 717095 | 17534 | 2.445%
NJ | 276182 | 260813 | 15369 | 5.893% | 295284 | -19102 | -6.469%
TX | 2281623 | 2255734 | 25889 | 1.148% | 2611327 | -329704 | -12.63%
AZ | 1430575 | 1312483 | 118092 | 8.998% | 1382102 | 48473 | 3.507%

## 4th Qtr
Wells Fargo |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total | 1686631.3827 | 1733245.5568 | -46614.1741 | -2.689% | 1816089.0211 | -129457.6384 | -7.128%
State | Actual | Expected | Delta | % | Forecasted | Delta | %
CA | 88885.905 | 81228.457 | 7657.448 | 9.427% | 105165.17 | -16279.265 | -15.48%
CO | 22098.9007 | 0 | 22098.9007 |  | 21554.073 | 544.8277 | 2.528%
CT | 727.4397 | 577 | 150.4397 | 26.07% | 1315.0992 | -587.6595 | -44.69%
FL | 671.9964 | 4958.923 | -4286.9266 | -86.45% | 4137 | -3465.0036 | -83.76%
IA | 194956 | 226528.37 | -31572.37 | -13.94% | 231527.94 | -36571.94 | -15.8%
NC | 270731 | 297329.652 | -26598.652 | -8.946% | 308820.918 | -38089.918 | -12.33%
NJ | 63169.6969 | 56157.1498 | 7012.5471 | 12.49% | 67998.1509 | -4828.454 | -7.101%
TX | 689596.0425 | 733328.67 | -43732.6275 | -5.964% | 722406.57 | -32810.5275 | -4.542%
AZ | 355794.4016 | 333137.335 | 22657.0666 | 6.801% | 353164.1 | 2630.3016 | 0.7448%

## Jan
Wells Fargo |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 546415.9626 | 600064.256 | -53648.2934 | -8.94% | 538220.177 | 8195.7856 | 1.523% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 501.8 | 0 | 501.8 |  | 661 | -159.2 | -24.08% | 1.Low generation due to weather/snow.
Otay Mesa | CA | 39.49 | 0 | 39.49 |  | 0 | 39.49 |  | 1. Production data taken from consumption meter.
San Leandro | CA | 25601 | 35709.12 | -10108.12 | -28.31% | 22352.73 | 3248.27 | 14.53% | 1.Inverter 4 underperforming by 7kW since 06/11, down 2 strings. Dispatch has been scheduled. Inverter 2 underperforming by 3kW since 05/10, down 1 string. Dispatch has been scheduled. Inverter 7 underperforming by 3kW since 09/09, down 1 string. Dispatch has been scheduled. 2.The inverter 3 has a history of wire box damage, so a complete inverter and wire box upgrade was required. The current wire box string fuse configuration was not acceptable. So, Inverter 3 has been undergoing an RMA process since 07/26/24. | 1.SR091496 2.SR088261 | SR088261
Van Nuys | CA | 914 | 0 | 914 |  | 1320.568 | -406.568 | -30.79%
Lodi - Lodi Vineyard | CA | 20951.2188 | 21734.83 | -783.6113 | -3.605% | 17814 | 3137.2188 | 17.61%
Arden Fair Mall | CA | 10599.6562 | 12935.16 | -2335.5037 | -18.06% | 10608 | -8.3438 | -0.07866%
Modesto - Modesto Main | CA | 7933.9531 | 10825.7 | -2891.7469 | -26.71% | 10268.68 | -2334.7269 | -22.74% | 1. The Ambient Temperature sensor was not communicating | 1.SR091735
Stevens Creek | CA | 3096.2009 | 2594.087 | 502.1139 | 19.36% | 2416 | 680.2009 | 28.15%
Covina Main | CA | 2141.7 | 1912.706 | 228.994 | 11.97% | 2134 | 7.7 | 0.3608%
Old Ranch Town Center | CA | 642.6062 | 0 | 642.6062 |  | 910 | -267.3938 | -29.38% | 1.Low generation due to weather/snow.
Mountain Gate Plaza | CA | 5252.3032 | 0 | 5252.3032 |  | 6591 | -1338.6968 | -20.31% | 1.Low generation due to weather/snow.
Arcadia Main | CA | 1679.0975 | 0 | 1679.0975 |  | 3550 | -1870.9025 | -52.7% | 1.Site stopped communicating from 01/28, communication card was need to be replaced and dispatch was scheduled for February. | 1.SR096085
Fairfield | CA | 2185.723 | 2398.052 | -212.329 | -8.854% | 2037 | 148.723 | 7.301%
Los Gatos | CA | 1247.8238 | 1112.865 | 134.9588 | 12.13% | 0 | 1247.8238
San Marino | CA | 2293.8 | 2367.908 | -74.108 | -3.13% | 2895.003 | -601.203 | -20.77% | 1.Low generation due to weather/snow.
Buenaventura | CA | 3155.5898 | 2389.828 | 765.7618 | 32.04% | 3932.196 | -776.6062 | -19.75% | 1.Low generation due to weather/snow.
BE 199502 - Westgate | CA
98th & Grant | CO | 468 | 0 | 468 |  | 1170 | -702 | -60%
Arapahoe Crossings | CO | 1869 | 0 | 1869 |  | 2128 | -259 | -12%
Aurora City Center | CO | 976 | 0 | 976 |  | 1050 | -74 | -7%
Dry Creek | CO | 1117 | 0 | 1117 |  | 1261 | -144 | -11%
Highlands Ranch S. | CO | 875 | 0 | 875 |  | 1109 | -234 | -21% | 1.Low generation due to weather/snow.
Lone Tree | CO | 1475 | 0 | 1475 |  | 2554 | -1079 | -42% | 1.Low generation due to weather/snow.
Meridian | CO | 1504 | 0 | 1504 |  | 1505 | -1 | 0%
Southglenn | CO | 1413 | 0 | 1413
Standley Lake | CO | 1429 | 0 | 1429 |  | 2142 | -713 | -33% | 1.Low generation due to weather/snow.
Havana Gardens | CO | 1606 | 0 | 1606 |  | 839 | 767 | 91%
East Hartford | CT | 207 | 702 | -494 | -70% | 271 | -64 | -23% | 1.Low generation due to weather/snow.
Norwalk | CT | -48 | 1301 | -1349 | -104% | 380 | -428 | -113% | 1.Weather station reporting erroneous values from 07/04/2024. Will investigate next time onsite. 2.The meter's Phase C current/power factor was experiencing intermittent glitches, which are affecting the reported energy production, but there was no impact on actual production. Will investigate next time onsite. | 1.SR088667 2.SR077700
Hialeah Gardens | FL | 2375 | 2837 | -462 | -16% | 3416 | -1041 | -30% | 1.Low generation due to weather/snow.
W. Des Moines Campus EAST | IA | 118781 | 137812 | -19031 | -14% | 103900 | 14881 | 14%
W. Des Moines Campus SW | IA | 62763 | 76926 | -14164 | -18% | 54918 | 7845 | 14% | 1.Low generation due to weather/snow.
WF - CIC | NC | 116508 | 113753 | 2755 | 2% | 106712 | 9796 | 9%
Charlotte - Wells Fargo - DUC | NC | 110087 | 128961 | -18874 | -15% | 129978 | -19891 | -15% | 1.Low generation due to weather/snow.
East Windsor | NJ | 395 | 635 | -241 | -38% | 406 | -12 | -3% | 1.Low generation due to weather/snow.
Burlington | NJ | 1271 | 1261 | 10 | 1% | 1087 | 185 | 17%
Bayonne | NJ | 1509 | 1667 | -159 | -10% | 2001 | -493 | -25% | 1.Low generation due to weather/snow.
Clifton | NJ | 1389 | 2166 | -777 | -36% | 2510 | -1120 | -45% | 1.Low generation due to weather/snow.
North Elizabeth | NJ | 1258 | 1301 | -43 | -3% | 1349 | -92 | -7% | 1. Low generation due to weather/snow.
Haddon Westmont Plaza | NJ | 745 | 1161 | -416 | -36% | 961 | -217 | -23% | 1.Low generation due to weather/snow.
Parsippany | NJ | 1080 | 2126 | -1046 | -49% | 1075 | 5 | 0% | 1.Low generation due to weather/snow.
Clark | NJ | 905 | 1198 | -293 | -24% | 916 | -11 | -1% | 1.Low generation due to weather/snow.
Closter | NJ | 184 | 274 | -90 | -33% | 462 | -279 | -60% | 1.Low generation due to weather/snow.
Holmdel | NJ | 761 | 3879 | -3118 | -80% | 804 | -42 | -5% | 1.Low generation due to weather/snow.
Ellisburg Circle Center | NJ | 357 | 562 | -205 | -36% | 451 | -94 | -21% | 1.Low generation due to weather/snow.
Nutley | NJ | 1174 | 1685 | -512 | -30% | 1647 | -473 | -29% | 1.Low generation due to weather/snow.
Marlton | NJ | 1399 | 1471 | -72 | -5% | 1600 | -202 | -13%
Middletown | NJ | 1803 | 1488 | 314 | 21% | 1621 | 182 | 11%
Whiting Crestwood | NJ | 2647 | 2943 | -296 | -10% | 2442 | 205 | 8%
Barnegat | NJ | 2474 | 2068 | 406 | 20% | 2008 | 466 | 23%
Manchester | NJ | 1526 | 1805 | -279 | -15% | 2136 | -610 | -29% | 1.Low generation due to weather/snow.
West Deptford - Woodbury | NJ | 2282 | 2179 | 103 | 5% | 1943 | 339 | 17%
Edison | NJ | 1779 | 1552 | 227 | 15% | 1464 | 315 | 22%
Flemington | NJ | 1189 | 1601 | -413 | -26% | 1235 | -47 | -4% | 1.Low generation due to weather/snow.
Route 22 | NJ | 1569 | 1450 | 119 | 8% | 1385 | 184 | 13%
Laurelton | NJ | 831 | 1040 | -209 | -20% | 1168 | -337 | -29% | 1.Low generation due to weather/snow.
Mahwah | NJ | 807 | 1393 | -586 | -42% | 1017 | -210 | -21% | 1.Low generation due to weather/snow.
Franklin Township WF | NJ | 1187 | 1355 | -169 | -12% | 1713 | -527 | -31% | 1.Low generation due to weather/snow.
Bordentown | NJ | 1339 | 1122 | 217 | 19% | 1122 | 218 | 19%
South Plainfield | NJ | 771 | 766 | 5 | 1% | 744 | 27 | 4%
Somerset | NJ | 1156 | 2084 | -928 | -45% | 1056 | 100 | 9% | 1.Low generation due to weather/snow.
Clinton Main Relo | NJ | 988 | 1560 | -572 | -37% | 1074 | -86 | -8% | 1.Low generation due to weather/snow.
North Brunswick | NJ | 1330 | 1367 | -37 | -3% | 1384 | -54 | -4% | 1.Inverter 1’s String 4 RSD was being RMA’d from 12/12/24. Dispatch has been scheduled for February. | 1.SR090252
Cherry Hill | NJ | 953 | 1172 | -220 | -19% | 910 | 43 | 5% | 1. Meter Phase B current intermittently underreporting, but inverter production remains unaffected. Reported energy loss may be retroactively corrected once the meter/CT issue is resolved | 1.SR077660
Hainesport | NJ | 1266 | 1241 | 25 | 2% | 988 | 278 | 28%
San Antonio - Ops Ctr (Bldg 106) | TX | 29279 | 35496 | -6217 | -18% | 34683 | -5404 | -16% | 1. Underperformance due to morning hours shading
San Antonio - Ops Ctr GM | TX | 242775 | 278247 | -35472 | -13% | 286543 | -43768 | -15% | 1. Underperformance due to morning hours shading
San Antonio - Ctr (Bldg 201) | TX | 30240 | 35143 | -4902 | -14% | 35426 | -5185 | -15% | 1. Underperformance due to morning hours shading
San Antonio - Ops Ctr (Bldg 203) | TX | 32108 | 31335 | 773 | 2% | 36479 | -4371 | -12% | 1. Underperformance due to morning hours shading
San Antonio - Ops Ctr (Bldg 205) | TX | 27955 | 32092 | -4137 | -13% | 32995 | -5040 | -15% | 1. Underperformance due to morning hours shading
San Antonio - Ops Ctr (Bldg 307) | TX | 29449 | 34830 | -5380 | -15% | 34193 | -4743 | -14% | 1. Underperformance due to morning hours shading
San Antonio - Ctr (Bldg 308) | TX | 30174 | 34056 | -3882 | -11% | 33833 | -3659 | -11% | 1. Underperformance due to morning hours shading
San Antonio - Ops Ctr (Bldg 104) | TX | 7770 | 10657 | -2887 | -27% | 10100 | -2330 | -23% | 1. Underperformance due to morning hours shading
San Antonio - Ops Ctr (Bldg 102) | TX | 32749 | 31328 | 1420 | 5% | 37504 | -4755 | -13% | 1. Underperformance due to morning hours shading
N Black Canyon Hwy, Phoenix - North | AZ | 61065 | 57627 | 3438 | 6% | 57066 | 3999 | 7%
N Black Canyon Hwy, Phoenix - South | AZ | 65447 | 63092 | 2355 | 4% | 63382 | 2065 | 3%
Building 2222, Rose Garden Ln, Phoenix | AZ | 38005 | 39145 | -1140 | -3% | 65567 | -27562 | -42% | 1.The site went offline at 07:45 MST on 12/16/24. The technician arrived and found the SES-A breaker switch tripped . After re-energizing the system, the site was back online at 10:30 MST on 01/14/25. | 1.SR094853
Building 2202, Rose Garden Ln, Phoenix | AZ | 62409 | 32578 | 29831 | 92% | 50223 | 12186 | 24% | 1. The Virtual weather station resumed communication on 01/14.
99TH Ave & BELL | AZ | 10492 | 8208 | 2284 | 28% | 13506 | -3014 | -22% | 1.Low generation due to weather/snow.
Rincon | AZ | 5660 | 4142 | 1518 | 37% | 4593 | 1067 | 23%
Tucson Main Parking Garage | AZ | 7711 | 9305 | -1594 | -17% | 8400 | -689 | -8% | 1.Low generation due to weather/snow.

## Feb
Wells Fargo |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 1283462.7 | 1301889.74 | -18427.04 | -1.415% | 1468474.048 | -185011.348 | -12.6% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 715.3 | 0 | 715.3 |  | 734 | -18.7 | -2.548%
Otay Mesa | CA | 35.7 | 0 | 35.7 |  | 0 | 35.7 |  | 1. Production data taken from consumption meter.
San Leandro | CA | 23817.5 | 28486.74 | -4669.24 | -16.39% | 25171.85 | -1354.35 | -5.38% | 1.Inverter 4 is underperforming by 7KW from 06/13/24 due to 2 non-operational strings. Inverter 2 underperforming by 3kW since 05/10/24 due to a string down and after technician replaced blown fuse on 02/20/25 inverter is producing in line with peers. Inverter 7 underperforming by 3kW since 09/09/24 due to a string down and after technician replaced blown fuse on 02/20/25 inverter is producing in line with peers. Inverter 5 underperforming by 4kW since 02/08/2 due to a string down. 2. Inverter 3 has a history of wire box damage, necessitating a complete inverter and wire box upgrade. The current wire box string fuse configuration was not acceptable. As a result, Inverter 3 has been undergoing the RMA process since 07/26/24. After the technician installed a new wire box, an arc fault was detected due to a damaged negative home run, which needs to be replaced. 3. SIte stopped communicating at 17:00 on 02/14 and regained communication at 8AM on 02/16 energy was not backfilled. | 1.SR091496 2.SR088261, SR097801 3.SR097144 | SR088261 | SR097801 | SR097144
Van Nuys | CA | 1286.2 | 0 | 1286.2 |  | 1479.198 | -192.998 | -13.05% | 1. Low generation due to weather/snow.
Lodi - Lodi Vineyard | CA | 23034 | 24427 | -1393 | -5.703% | 21975 | 1059 | 4.819%
Arden Fair Mall | CA | 11150 | 12202 | -1052 | -8.622% | 12337 | -1187 | -9.621%
Modesto - Modesto Main | CA | 8051 | 9829 | -1778 | -18.09% | 12423 | -4372 | -35.19% | 1. The Ambient Temperature sensor was not communicating . 2.The site lost communication at 7:30 AM on 02/02 and regained at 9:45 AM on 02/06. | 1.SR091735 2.SR096229
Stevens Creek | CA | 2694 | 2448 | 246 | 10.05% | 2894 | -200 | -6.911% | 1.On 02/18, the technician de-energized the inverter from 09:46 AM to 10:15 AM to replace the comms card. After replacing it, the inverter was re-energized. 2.The site went offline at 06:45 AM on 02/21. Upon arrival, the technician found that the breaker had tripped and reset it. The site was back online by 09:30 AM on 02/24. | 1.SR091107 2.SR097627
Covina Main | CA | 2712 | 2191 | 521 | 23.78% | 2174 | 538 | 24.75%
Old Ranch Town Center | CA | 862 | 0 | 862 |  | 990 | -128 | -12.93% | 1. Low generation due to weather/snow.
Mountain Gate Plaza | CA | 6050 | 0 | 6050 |  | 6590 | -540 | -8.194%
Arcadia Main | CA | 2375 | 0 | 2375 |  | 3533 | -1158 | -32.78% | 1.Site stopped communicating from 01/28 and back online at 03:30PM on 02/07 . | 1.SR096085
Fairfield | CA | 2178 | 2211 | -33 | -1.493% | 2330 | -152 | -6.524%
Los Gatos | CA | 1180 | 1108 | 72 | 6.498% | 0 | 1180
San Marino | CA | 2792 | 2686 | 106 | 3.946% | 3237 | -445 | -13.75% | 1. Low generation due to weather/snow.
Buenaventura | CA | 3680 | 2669 | 1011 | 37.88% | 3947 | -267 | -6.765%
BE 199502 - Westgate | CA
98th & Grant | CO | 686 | 0 | 686 |  | 1280 | -594 | -46.41% | 1. Low generation due to weather/snow.
Arapahoe Crossings | CO | 2274 | 0 | 2274 |  | 2351 | -77 | -3.275%
Aurora City Center | CO | 1252 | 0 | 1252 |  | 1140 | 112 | 9.825%
Dry Creek | CO | 1268 | 0 | 1268 |  | 1386 | -118 | -8.514%
Highlands Ranch S. | CO | 1188 | 0 | 1188 |  | 1265 | -77 | -6.087%
Lone Tree | CO | 1907 | 0 | 1907 |  | 2891 | -984 | -34.04% | 1. Low generation due to weather/snow.
Meridian | CO | 2004 | 0 | 2004 |  | 1699 | 305 | 17.95%
Southglenn | CO | 1877 | 0 | 1877
Standley Lake | CO | 1987 | 0 | 1987 |  | 2371 | -384 | -16.2% | 1. Low generation due to weather/snow.
Havana Gardens | CO | 2177 | 0 | 2177 |  | 926 | 1251 | 135.1% | 1. Low generation due to weather/snow.
East Hartford | CT | 203 | 980 | -777 | -79.29% | 429 | -226 | -52.68% | 1. Low generation due to weather/snow.
Norwalk | CT | 220 | 427 | -207 | -48.48% | 488 | -268 | -54.92% | 1.Weather station reporting erroneous values from 07/04/2024. Will investigate next time onsite. 2.The meter's Phase C current/power factor was experiencing intermittent glitches, which are affecting the reported energy production, but there was no impact on actual production. Will investigate next time onsite. | 1.SR088667 2.SR077700
Hialeah Gardens | FL | 2565 | 3094 | -529 | -17.1% | 3739 | -1174 | -31.4% | 1. Low generation due to weather/snow.
W. Des Moines Campus EAST | IA | 116148 | 129057 | -12909 | -10% | 124800 | -8652 | -6.933%
W. Des Moines Campus SW | IA | 49019 | 70698 | -21679 | -30.66% | 62858 | -13839 | -22.02% | 1. Low generation due to weather/snow.
WF - CIC | NC | 121252 | 120286 | 966 | 0.8031% | 116371 | 4881 | 4.194%
Charlotte - Wells Fargo - DUC | NC | 115950 | 130576 | -14626 | -11.2% | 128349 | -12399 | -9.66%
East Windsor | NJ | 572 | 629 | -57 | -9.062% | 479 | 93 | 19.42%
Burlington | NJ | 1564 | 1361 | 203 | 14.92% | 1358 | 206 | 15.17%
Bayonne | NJ | 1884 | 1982 | -98 | -4.945% | 2311 | -427 | -18.48% | 1. Low generation due to weather/snow.
Clifton | NJ | 2261 | 2568 | -307 | -11.95% | 3023 | -762 | -25.21% | 1. Low generation due to weather/snow.
North Elizabeth | NJ | 1699 | 1480 | 219 | 14.8% | 1908 | -209 | -10.95% | 1. Low generation due to weather/snow.
Haddon Westmont Plaza | NJ | 1316 | 1301 | 15 | 1.153% | 1318 | -2 | -0.1517%
Parsippany | NJ | 1672 | 1810 | -138 | -7.624% | 1721 | -49 | -2.847%
Clark | NJ | 1390 | 1360 | 30 | 2.206% | 1373 | 17 | 1.238%
Closter | NJ | 355 | 417 | -62 | -14.87% | 767 | -412 | -53.72% | 1. Low generation due to weather/snow.
Holmdel | NJ | 1230 | 4382 | -3152 | -71.93% | 996 | 234 | 23.49% | 1. Low generation due to weather/snow.
Ellisburg Circle Center | NJ | 600 | 614 | -14 | -2.28% | 612 | -12 | -1.961%
Nutley | NJ | 1891 | 1982 | -91 | -4.591% | 2488 | -597 | -24% | 1. Low generation due to weather/snow.
Marlton | NJ | 2317 | 1706 | 611 | 35.81% | 2205 | 112 | 5.079% | 1. Low generation due to weather/snow.
Middletown | NJ | 2084 | 1650 | 434 | 26.3% | 1901 | 183 | 9.627% | 1. Low generation due to weather/snow.
Whiting Crestwood | NJ | 2873 | 2824 | 49 | 1.735% | 2953 | -80 | -2.709%
Barnegat | NJ | 3221 | 2723 | 498 | 18.29% | 2731 | 490 | 17.94% | 1. Low generation due to weather/snow.
Manchester | NJ | 1478 | 1829 | -351 | -19.19% | 2367 | -889 | -37.56% | 1. Low generation due to weather/snow.
West Deptford - Woodbury | NJ | 2430 | 2315 | 115 | 4.968% | 2342 | 88 | 3.757% | 1.Inverter 1 was offline on 02/09 due to a loss of main fault and self-resolved at 2:30 PM on 02/10. | 1.SR096618
Edison | NJ | 2143 | 1706 | 437 | 25.62% | 2080 | 63 | 3.029% | 1. Low generation due to weather/snow.
Flemington | NJ | 1791 | 1628 | 163 | 10.01% | 1847 | -56 | -3.032%
Route 22 | NJ | 1870 | 2004 | -134 | -6.687% | 1908 | -38 | -1.992%
Laurelton | NJ | 1087 | 1514 | -427 | -28.2% | 1507 | -420 | -27.87% | 1. Low generation due to weather/snow.
Mahwah | NJ | 1288 | 1576 | -288 | -18.27% | 1464 | -176 | -12.02% | 1. Low generation due to weather/snow.
Franklin Township WF | NJ | 1622 | 1492 | 130 | 8.713% | 2146 | -524 | -24.42% | 1. Low generation due to weather/snow.
Bordentown | NJ | 1432 | 1137 | 295 | 25.95% | 1253 | 179 | 14.29% | 1. Low generation due to weather/snow.
South Plainfield | NJ | 1015 | 852 | 163 | 19.13% | 939 | 76 | 8.094%
Somerset | NJ | 1472 | 2124 | -652 | -30.7% | 1440 | 32 | 2.222% | 1. Low generation due to weather/snow.
Clinton Main Relo | NJ | 1600
North Brunswick | NJ | 1728 | 1526 | 202 | 13.24% | 1843 | -115 | -6.24% | 1. Inverter 1's String 4 RSD was sent for RMA on 12/12/24. On 02/10/25, the technician installed a new RSD and inserted the fuse for String 5. The inverter came back online and is producing as expected | 1.SR090252
Cherry Hill | NJ | 1142 | 1226 | -84 | -6.852% | 1192 | -50 | -4.195% | 1. Meter Phase B current intermittently underreporting, but inverter production remains unaffected. Reported energy loss may be retroactively corrected once the meter/CT issue is resolved | 1.SR077660
Hainesport | NJ | 1391 | 1336 | 55 | 4.117% | 1156 | 235 | 20.33%
San Antonio - Ops Ctr (Bldg 106) | TX | 32009 | 36208 | -4199 | -11.6% | 37511 | -5502 | -14.67% | 1. Underperformance due to morning hours shading
San Antonio - Ops Ctr GM | TX | 239671 | 272681 | -33010 | -12.11% | 304922 | -65251 | -21.4% | 1. Underperformance due to morning hours shading
San Antonio - Ctr (Bldg 201) | TX | 32332 | 35890 | -3558 | -9.914% | 37272 | -4940 | -13.25% | 1. Underperformance due to morning hours shading
San Antonio - Ops Ctr (Bldg 203) | TX | 33952 | 33074 | 878 | 2.655% | 38423 | -4471 | -11.64% | 1. Underperformance due to morning hours shading
San Antonio - Ops Ctr (Bldg 205) | TX | 30207 | 32734 | -2527 | -7.72% | 35606 | -5399 | -15.16% | 1.Inverter 4 is underperforming by 5kW since 02/16, down 1 string. Dispatch has been scheduled for next PM on 10/10/25. | 1.SR097581
San Antonio - Ops Ctr (Bldg 307) | TX | 31864 | 35565 | -3701 | -10.41% | 36605 | -4741 | -12.95% | 1. Underperformance due to morning hours shading
San Antonio - Ctr (Bldg 308) | TX | 31694 | 34762 | -3068 | -8.826% | 35499 | -3805 | -10.72% | 1. Underperformance due to morning hours shading
San Antonio - Ops Ctr (Bldg 104) | TX | 8831 | 10884 | -2053 | -18.86% | 10911 | -2080 | -19.06% | 1. Underperformance due to morning hours shading
San Antonio - Ops Ctr (Bldg 102) | TX | 34984 | 32568 | 2416 | 7.418% | 39742 | -4758 | -11.97% | 1. Underperformance due to morning hours shading
N Black Canyon Hwy, Phoenix - North | AZ | 63308 | 60958 | 2350 | 3.855% | 61016 | 2292 | 3.756%
N Black Canyon Hwy, Phoenix - South | AZ | 68222 | 66700 | 1522 | 2.282% | 67660 | 562 | 0.8306% | 1.Inverter 16 is down 1 string. Dispatch has been scheduled for next PM on 05/26/25. | 1.SR097838
Building 2222, Rose Garden Ln, Phoenix | AZ | 13324 | 15183 | -1859 | -12.24% | 73696 | -60372 | -81.92% | 1.The site went offline at 5:32 PM on 01/31/25. On 02/24, a technician arrived and found that the SES-A breaker switch had tripped. After re-energizing the system, the site was back online at 10:20 AM on 02/24. | 1.SR096213
Building 2202, Rose Garden Ln, Phoenix | AZ | 69360 | 13434 | 55926 | 416.3% | 57349 | 12011 | 20.94% | 1. The site stopped communication at 06:00PM on 02/08 and back at 03:45AM on 02/09. 2.The Virtual weather station resumed communication on 01/31 and back on 02/24. | 1.SR096533
99TH Ave & BELL | AZ | 13291 | 11366 | 1925 | 16.94% | 14489 | -1198 | -8.268%
Rincon | AZ | 6553 | 4885 | 1668 | 34.15% | 5215 | 1338 | 25.66% | 1. Low generation due to weather/snow.
Tucson Main Parking Garage | AZ | 8853 | 10568 | -1715 | -16.23% | 8772 | 81 | 0.9234% | 1. Production meter is underreporting compared to the inverters, with B-phase current reading low compared to A & C. The meter is reporting lower by approximately 7kW. | 1. SR099589

## Mar
Wells Fargo |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 2070288 | 2047973.35 | 22314.65 | 1.09% | 1955597.731 | 114690.269 | 5.865%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 1011.1 | 0 | 1011.1 |  | 1060 | -48.9 | -4.613%
Otay Mesa | CA | 39.7 | 0 | 39.7 |  | 0 | 39.7 |  | 1. Production data taken from consumption meter.
San Leandro | CA | 38680.5 | 42926.35 | -4245.85 | -9.891% | 37122.59 | 1557.91 | 4.197% | 1.Inverter 4 and 6 are underperforming by 7KW from 06/13/24 due to 2 non-operational strings. Inverter 5 underperforming by 4kW since 02/08/2 due to a string down. 2. Inverter 3 has a history of wire box damage, necessitating a complete inverter and wire box upgrade. The current wire box string fuse configuration was not acceptable. As a result, Inverter 3 has been undergoing the RMA process since 07/26/24. After the technician installed a new wire box, an arc fault was detected due to a damaged negative home run, which needs to be replaced. CPS Team is preparing quote for 36kW powerhead compatible with he V2 wirebox | 1.SR091496 2.SR097801 | SR097801
Van Nuys | CA | 1659.7 | 0 | 1659.7 |  | 2116.141 | -456.441 | -21.57% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Lodi - Lodi Vineyard | CA | 35356 | 38013 | -2657 | -7% | 32370 | 2986 | 9%
Arden Fair Mall | CA | 16843 | 17634 | -791 | -4% | 19350 | -2507 | -13% | 1.Inverters 1 and 2 were offline from 06:30 PST to 14:50 PST on 03/06 | 1.SR098213
Modesto - Modesto Main | CA | 13610 | 15389 | -1779 | -12% | 18601 | -4991 | -27% | 1.The site remained offline from 22:45 PDT on 03/16 until 14:45 PDT on 03/17.Issue got self resolved | 1.SR098649
Stevens Creek | CA | 4575 | 4275 | 300 | 7% | 4937 | -362 | -7%
Covina Main | CA | 3456 | 2874 | 582 | 20% | 3109 | 347 | 11%
Old Ranch Town Center | CA | 1246 | 0 | 1246 |  | 1294 | -48 | -4%
Mountain Gate Plaza | CA | 8125 | 0 | 8125 |  | 9526 | -1401 | -15% | 1. Compared to last year’s (November and December) delta values, we still see a negative variance for this site, which suggests an issue with the forecasted value. Additionally, we do not have inverter communications for this site.
Arcadia Main | CA | 3900 | 0 | 3900 |  | 4681 | -781 | -17% | 1. Compared to last year’s (November and December) delta values, we still see a negative variance for this site, which suggests an issue with the forecasted value. Additionally, we do not have inverter communications for this site.
Fairfield | CA | 3354 | 3360 | -6 | 0% | 3588 | -234 | -7%
Los Gatos | CA | 1728 | 1681 | 47 | 3% | 0 | 1728
San Marino | CA | 2913 | 3623 | -710 | -20% | 4867 | -1954 | -40% | 1.Inverter 1 was offline from 06:45 PDT to 16:45 PDT on 03/09 and self resolved and we don't have SR for this issue.
Buenaventura | CA | 4848 | 3442 | 1406 | 41% | 5544 | -696 | -13% | 1. Compared to last year’s (November and December) delta values, we still see a negative variance for this site, which suggests an issue with the forecasted value.
BE 199502 - Westgate | CA | 1722 | 0 | 1722 |  | 0 | 1722 |  | 1. Site underperforming by ~15 kW since 03/12. Will investigate next time onsite. | 1.SR098782
98th & Grant | CO | 1113 | 0 | 1113 |  | 1984 | -871 | -43.9% | 1. Compared to last year’s delta values, we still see a negative variance for this site, which suggests an issue with the forecasted value. Additionally, we do not have inverter communications for this site.
Arapahoe Crossings | CO | 2757 | 0 | 2757 |  | 3647 | -890 | -24.4% | 1. Compared to last year’s delta values, we still see a negative variance for this site, which suggests an issue with the forecasted value. Additionally, we do not have inverter communications for this site.
Aurora City Center | CO | 1941 | 0 | 1941 |  | 1727 | 214 | 12.39%
Dry Creek | CO | 2338 | 0 | 2338 |  | 2153 | 185 | 8.593%
Highlands Ranch S. | CO | 1852 | 0 | 1852 |  | 2006 | -154 | -7.677%
Lone Tree | CO | 2868 | 0 | 2868 |  | 4580 | -1712 | -37.38% | 1. Compared to last year’s delta values, we still see a negative variance for this site, which suggests an issue with the forecasted value. Additionally, we do not have inverter communications for this site.
Meridian | CO | 2937 | 0 | 2937 |  | 2667 | 270 | 10.12%
Southglenn | CO | 3092 | 0 | 3092 |  | 2762 | 330 | 11.95%
Standley Lake | CO | 3175 | 0 | 3175 |  | 3683 | -508 | -13.79% | 1. Compared to last year’s delta values, we still see a negative variance for this site, which suggests an issue with the forecasted value. Additionally, we do not have inverter communications for this site.
Havana Gardens | CO | 3554 | 0 | 3554 |  | 1436 | 2118 | 147.5%
East Hartford | CT | 615 | 1498 | -883 | -59% | 596 | 19 | 3% | 1. Site production was low 03/05, 03/06, 03/15 to 03/17, 03/24, 03/29 to 03/31 due to rain.
Norwalk | CT | 654 | 261 | 393 | 150% | 730 | -76 | -10% | 1. Weather station reporting erroneous values from 07/04/2024. Will investigate while next time onsite 2.The meter's Phase C current/power factor was experiencing intermittent glitches, which are affecting the reported energy production, but there was no impact on actual production. Will investigate next time onsite. | 1. SR088667 2.SR077700
Hialeah Gardens | FL | 1855 | 4172 | -2317 | -56% | 5039 | -3184 | -63% | 1. Site underperforming by ~15 kW since 03/12. Will investigate next time onsite. | 1.SR098782
W. Des Moines Campus EAST | IA | 178354 | 177208 | 1146 | 1% | 159000 | 19354 | 12%
W. Des Moines Campus SW | IA | 88417 | 92338 | -3921 | -4% | 78636 | 9781 | 12%
WF - CIC | NC | 178134 | 175836 | 2298 | 1% | 171329 | 6805 | 4%
Charlotte - Wells Fargo - DUC | NC | 173904 | 188174 | -14270 | -8% | 164590 | 9314 | 6%
East Windsor | NJ | 940 | 940 | 0 | 0% | 754 | 186 | 24.67%
Burlington | NJ | 2515 | 2272 | 243 | 10.7% | 1965 | 550 | 27.99%
Bayonne | NJ | 3042 | 2939 | 103 | 3.505% | 3069 | -27 | -0.8798%
Clifton | NJ | 3722 | 3688 | 34 | 0.9219% | 3861 | -139 | -3.6%
North Elizabeth | NJ | 3124 | 2304 | 820 | 35.59% | 2667 | 457 | 17.14%
Haddon Westmont Plaza | NJ | 2327 | 2206 | 121 | 5.485% | 1892 | 435 | 22.99%
Parsippany | NJ | 2753 | 2605 | 148 | 5.681% | 2192 | 561 | 25.59%
Clark | NJ | 2315 | 2107 | 208 | 9.872% | 1834 | 481 | 26.23%
Closter | NJ | 845 | 818 | 27 | 3.301% | 1036 | -191 | -18.44% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Holmdel | NJ | 2025 | 5443 | -3418 | -62.8% | 1588 | 437 | 27.52% | 1. Site production was low on 03/05, 03/15, 03/17, 03/24, 03/30 due to bad weather.
Ellisburg Circle Center | NJ | 1051 | 1015 | 36 | 3.547% | 869 | 182 | 20.94%
Nutley | NJ | 3197 | 2931 | 266 | 9.075% | 3119 | 78 | 2.501%
Marlton | NJ | 3884 | 3145 | 739 | 23.5% | 3126 | 758 | 24.25%
Middletown | NJ | 3205 | 2594 | 611 | 23.55% | 2619 | 586 | 22.37%
Whiting Crestwood | NJ | 4261 | 4144 | 117 | 2.823% | 3747 | 514 | 13.72%
Barnegat | NJ | 5280 | 4551 | 729 | 16.02% | 4382 | 898 | 20.49%
Manchester | NJ | 2410 | 2673 | -263 | -9.839% | 3157 | -747 | -23.66% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
West Deptford - Woodbury | NJ | 3757 | 3633 | 124 | 3.413% | 2958 | 799 | 27.01%
Edison | NJ | 3228 | 2730 | 498 | 18.24% | 2487 | 741 | 29.79%
Flemington | NJ | 2843 | 2391 | 452 | 18.9% | 2325 | 518 | 22.28%
Route 22 | NJ | 2825 | 2664 | 161 | 6.044% | 2326 | 499 | 21.45%
Laurelton | NJ | 1726 | 2453 | -727 | -29.64% | 2155 | -429 | -19.91% | 1. Site production was low on 03/05, 03/13, 03/15 to 03/17, 03/20, 03/24 due to rain.
Mahwah | NJ | 2167 | 1804 | 363 | 20.12% | 1895 | 272 | 14.35% | 1.Weather station is reporting 0 during production hours even on a good irradiance day
Franklin Township WF | NJ | 2673 | 2388 | 285 | 11.93% | 2729 | -56 | -2.052%
Bordentown | NJ | 2243 | 1824 | 419 | 22.97% | 1708 | 535 | 31.32%
South Plainfield | NJ | 1548 | 1343 | 205 | 15.26% | 1221 | 327 | 26.78%
Somerset | NJ | 2368 | 3126 | -758 | -24.25% | 1883 | 485 | 25.76% | 1. Site production was low on 03/05, 03/13, 03/15 to 03/17, 03/24, 03/30 due to bad weather.
Clinton Main Relo | NJ | 2711 | 2698 | 13 | 0.4818% | 2152 | 559 | 25.98%
North Brunswick | NJ | 2795 | 2440 | 355 | 14.55% | 2416 | 379 | 15.69%
Cherry Hill | NJ | 1993 | 1969 | 24 | 1.219% | 1649 | 344 | 20.86% | 1.Meter Phase B current was intermittently underreporting, but inverter production remained unaffected. On 03/06, a technician identified an issue with Phase B and swapped the CT for Phase B with the CT for Phase C. The issue was resolved after the technician's visit. | 1.SR077660
Hainesport | NJ | 2205 | 2233 | -28 | -1.254% | 1605 | 600 | 37.38%
San Antonio - Ops Ctr (Bldg 106) | TX | 52377 | 52442 | -65 | -0.1239% | 50659 | 1718 | 3.391%
San Antonio - Ops Ctr GM | TX | 392242 | 429672 | -37430 | -8.711% | 366154 | 26088 | 7.125%
San Antonio - Ctr (Bldg 201) | TX | 53579 | 52004 | 1575 | 3.029% | 50695 | 2884 | 5.689%
San Antonio - Ops Ctr (Bldg 203) | TX | 54984 | 53459 | 1525 | 2.853% | 51279 | 3705 | 7.225%
San Antonio - Ops Ctr (Bldg 205) | TX | 48894 | 47420 | 1474 | 3.108% | 47944 | 950 | 1.981%
San Antonio - Ops Ctr (Bldg 307) | TX | 52224 | 51531 | 693 | 1.345% | 49100 | 3124 | 6.363%
San Antonio - Ctr (Bldg 308) | TX | 51650 | 50369 | 1281 | 2.543% | 47705 | 3945 | 8.27%
San Antonio - Ops Ctr (Bldg 104) | TX | 14428 | 15771 | -1343 | -8.516% | 14699 | -271 | -1.844%
San Antonio - Ops Ctr (Bldg 102) | TX | 56860 | 48446 | 8414 | 17.37% | 53379 | 3481 | 6.521% | 1.Inverter 3 stopped communicating at 12:00 CDT on 03/31, and production cannot be confirmed at the meter level. It has not regained communication since then. | 1.SR099238
N Black Canyon Hwy, Phoenix - North | AZ | 85411 | 77197 | 8214 | 10.64% | 80919 | 4492 | 5.551%
N Black Canyon Hwy, Phoenix - South | AZ | 90957 | 84695 | 6262 | 7.394% | 89640 | 1317 | 1.469%
Building 2222, Rose Garden Ln, Phoenix | AZ | 104420 | 103296 | 1124 | 1.088% | 104525 | -105 | -0.1005%
Building 2202, Rose Garden Ln, Phoenix | AZ | 104380 | 94117 | 10263 | 10.9% | 84591 | 19789 | 23.39%
99TH Ave & BELL | AZ | 18692 | 18683 | 9 | 0.04817% | 19248 | -556 | -2.889% | 1.Inverter 2 tripped offline at 14:25 MDT on 03/18 and back online at 14:55 MDT on the same day.It tripped offline at 13:00 MDT on 03/19 and back online at 14:45 MDT on 03/19.
Rincon | AZ | 8415 | 6682 | 1733 | 25.94% | 7610 | 805 | 10.58%
Tucson Main Parking Garage | AZ | 8170 | 9414 | -1244 | -13.21% | 11334 | -3164 | -27.92% | 1.Site stopped communicating at 18:30 on 03/22,Unable to confirm production and Site did not regain the communication for the rest of the month. 2.Production meter is underreporting compared to the inverters, with B-phase current reading low compared to A & C. The meter is reporting lower by approximately 7kW | 1.SR098897 2.SR099589

## Apr
Wells Fargo |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 1500390.9933 | 1400910.265 | 99480.7283 | 7.101% | 1543739.214 | -43348.2207 | -2.808%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 1178.7 | NA |  |  | 1189 | -10.3 | -0.8663%
Otay Mesa | CA | 38.2 | NA | [5 empty] | 1. Production data taken from consumption meter.
San Leandro | CA | 10927.75 | 11196.35 | -268.6 | -2.399% | 44719.21 | -33791.46 | -75.56% | 1. Inverter 3 has a history of wire box damage, necessitating a complete inverter and wire box upgrade. The current wire box string fuse configuration was not acceptable. As a result, Inverter 3 has been undergoing the RMA process since 07/26/24. After the technician installed a new wire box, an arc fault was detected due to a damaged negative home run, which needs to be replaced. CPS Team is preparing quote for 36kW powerhead compatible with he V2 wirebox 2. Site was stopped communicating on 04/08 at 07:30am. The site was down for EPC testing on nearby project. 3. Inverter 4 and 6 are underperforming by 7KW from 06/13/24 due to 2 non-operational strings. Inverter 5 underperforming by 4kW since 02/08/2 due to a string down. | 1. SR097801 2. SR099548 3. SR091496 | SR099548 | SR091496
Van Nuys | CA | 1914.7 | NA |  |  | 2371.125 | -456.425 | -19.25% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Lodi - Lodi Vineyard | CA | 46040 | 49502 | -3462 | -6.994% | 36362 | 9678 | 26.62%
Arden Fair Mall | CA | 22644 | 22917 | -273 | -1.191% | 23272 | -628 | -2.699%
Modesto - Modesto Main | CA | 17813 | 19239 | -1426 | -7.412% | 21715 | -3902 | -17.97% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Stevens Creek | CA | 5771 | 5580 | 191 | 3.423% | 5993 | -222 | -3.704%
Covina Main | CA | 3922 | 3411 | 511 | 14.98% | 3350 | 572 | 17.07%
Old Ranch Town Center | CA | 1397 | NA |  |  | 1468 | -71 | -4.837%
Mountain Gate Plaza | CA | 9496 | NA |  |  | 9942 | -446 | -4.486%
Arcadia Main | CA | 3914 | NA |  |  | 5021 | -1107 | -22.05% | 1. Compared to last year’s (November and December) delta values, we still see a negative variance for this site, which suggests an issue with the forecasted value. Additionally, we do not have inverter communications for this site.
Fairfield | CA | 4272 | 4181 | 91 | 2.177% | 4343 | -71 | -1.635%
Los Gatos | CA | 2202 | 2210 | -8 | -0.362% | 0 | 2202
San Marino | CA | 3742 | 4309 | -567 | -13.16% | 5485 | -1743 | -31.78% | 1.Inverter 2 is down a string from 04/25 | 1.SR100421
Buenaventura | CA | 5514 | 3923 | 1591 | 40.56% | 5951 | -437 | -7.343%
BE 199502 - Westgate | CA | 2024 | NA |  |  | 2120 | -95 | -4%
98th & Grant | CO | 1132 | NA |  |  | 2136 | -1004 | -47% | 1. Compared to last year’s delta values, we still see a negative variance for this site, which suggests an issue with the forecasted value. Additionally, we do not have inverter communications for this site.
Arapahoe Crossings | CO | 2890 | NA |  |  | 3938 | -1048 | -26.61% | 1. Compared to last year’s (November and December) delta values, we still see a negative variance for this site, which suggests an issue with the forecasted value. Additionally, we do not have inverter communications for this site.
Aurora City Center | CO | 1928 | NA |  |  | 1830 | 98 | 5.355%
Dry Creek | CO | 2239 | NA |  |  | 2326 | -87 | -3.74%
Highlands Ranch S. | CO | 1893 | NA |  |  | 2208 | -315 | -14.27% | 1. Compared to last year’s (November and December) delta values, we still see a negative variance for this site, which suggests an issue with the forecasted value. Additionally, we do not have inverter communications for this site.
Lone Tree | CO | 2930 | NA |  |  | 5022 | -2092 | -41.66% | 1.Inverter 2 was offline for the entire month due to 'Fault State 401: Communication Fault.' The inverter needs to be replaced, but the client has not approved it. | 1. SR084532, SR088671, PM4252
Meridian | CO | 3211 | NA |  |  | 2914 | 297 | 10.19%
Southglenn | CO | 3125 | NA |  |  | 2987 | 138 | 4.62%
Standley Lake | CO | 3215 | NA |  |  | 3982 | -767 | -19.26% | 1. Compared to last year’s delta values, we still see a negative variance for this site, which suggests an issue with the forecasted value. Additionally, we do not have inverter communications for this site.
Havana Gardens | CO | 3617 | NA |  |  | 1550 | 2067 | 133.4%
East Hartford | CT | 723 | 1739 | -1016 | -58.42% | 797 | -74 | -9.285% | 1. Site production was low on 04/03, 04/05, 04/07, 04/11 and 04/12 due to rain.
Norwalk | CT | 900 | 96 | 804 | 837.5% | 989 | -89 | -8.999% | 1.Weather station reporting erroneous values from 07/04/2024 | 1.SR088667
Hialeah Gardens | FL | 912 | 4623 | -3711 | -80.27% | 5532 | -4620 | -83.51% | 1.Site underperforming by ~15 kW since 03/12. Will investigate next time onsite | 1.SR098782
W. Des Moines Campus EAST | IA | 171304 | 165349 | 5955 | 3.601% | 177300 | -5996 | -3.382%
W. Des Moines Campus SW | IA | 85147 | 83404 | 1743 | 2.09% | 87570 | -2423 | -2.767%
WF - CIC | NC | 181200 | 181100 | 100 | 0.05522% | 194273 | -13073 | -6.729%
Charlotte - Wells Fargo - DUC | NC | 182298 | 197108 | -14810 | -7.514% | 175059 | 7239 | 4.135%
East Windsor | NJ | 951 | 828 | 123 | 14.86% | 1083 | -132 | -12.19% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Burlington | NJ | 2419 | 2340 | 79 | 3.376% | 2738 | -319 | -11.65% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Bayonne | NJ | 3164 | 3019 | 145 | 4.803% | 3302 | -138 | -4.179%
Clifton | NJ | 3850 | 3906 | -56 | -1.434% | 4380 | -530 | -12.1% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
North Elizabeth | NJ | 3380 | 2552 | 828 | 32.45% | 3644 | -264 | -7.245%
Haddon Westmont Plaza | NJ | 2352 | 2273 | 79 | 3.476% | 2652 | -300 | -11.31% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Parsippany | NJ | 2855 | 2683 | 172 | 6.411% | 3019 | -164 | -5.432%
Clark | NJ | 2377 | 2258 | 119 | 5.27% | 2525 | -148 | -5.861%
Closter | NJ | 1232 | 999 | 233 | 23.32% | 1502 | -270 | -17.98% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Holmdel | NJ | 2006 | 5819 | -3813 | -65.53% | 2179 | -173 | -7.939% | 1. Weather station constantly reporting a fixed value of 1237.22 W/m2 01/09. | 1. SR100979
Ellisburg Circle Center | NJ | 1046 | 1035 | 11 | 1.063% | 1216 | -170 | -13.98% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Nutley | NJ | 4065 | 3305 | 760 | 23% | 4263 | -198 | -4.645%
Marlton | NJ | 3782 | 3337 | 445 | 13.34% | 4177 | -395 | -9.457%
Middletown | NJ | 2972 | 2414 | 558 | 23.12% | 3484 | -512 | -14.7% | 1. Weather station is frequently reporting erroneous values since 04/14. | 1. SR100592
Whiting Crestwood | NJ | 3893 | 3672 | 221 | 6.019% | 4680 | -787 | -16.82% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Barnegat | NJ | 5389 | 4836 | 553 | 11.44% | 6060 | -671 | -11.07% | 1. The site went offline at 18:05 on 04/22 later self resolved and back online at 15:15 on 04/22. | 1. SR100186
Manchester | NJ | 2211 | 2486 | -275 | -11.06% | 3946 | -1735 | -43.97% | 1. Site production was low on 04/07, 04/11 and 04/12 due to rain.
West Deptford - Woodbury | NJ | 3415 | 3542 | -127 | -3.586% | 3775 | -360 | -9.536%
Edison | NJ | 3047 | 2910 | 137 | 4.708% | 3309 | -262 | -7.918%
Flemington | NJ | 2898 | 2720 | 178 | 6.544% | 3284 | -386 | -11.75% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Route 22 | NJ | 2799 | 2987 | -188 | -6.294% | 3173 | -374 | -11.79% | 1.The site tripped offline at 11:37 AM on 04/25 due to "Loss of Main - GridV.OutLim" but was back online by 12:00 PM. The outage was brief with minimal production loss | 1.SR100412
Laurelton | NJ | 1172 | 1737 | -565 | -32.53% | 2845 | -1673 | -58.8% | 1.The site lost communication at 20:00 EDT on 04/23. Production cannot be confirmed, and the issue remains unresolved for rest of the month. | 1.SR100432
Mahwah | NJ | 2351 | 1144 | 1207 | 105.5% | 2592 | -241 | -9.298% | 1.Weather station is frequently reporting erroneous values ( 0 w/m^2) during mid days from 03/10. | 1.SR100593
Franklin Township WF | NJ | 2616 | 2522 | 94 | 3.727% | 3132 | -516 | -16.48% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Bordentown | NJ | 2019 | 1809 | 210 | 11.61% | 2245 | -226 | -10.07% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
South Plainfield | NJ | 1501 | 1442 | 59 | 4.092% | 1588 | -87 | -5.479%
Somerset | NJ | 2357 | 2364 | -7 | -0.2961% | 2652 | -295 | -11.12% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Clinton Main Relo | NJ | 2804 | 2794 | 10 | 0.3579% | 3050 | -246 | -8.066%
North Brunswick | NJ | 2819 | 2556 | 263 | 10.29% | 3314 | -495 | -14.94% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Cherry Hill | NJ | 1940 | 1866 | 74 | 3.966% | 2159 | -219 | -10.14% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Hainesport | NJ | 2019 | 2197 | -178 | -8.102% | 2179 | -160 | -7.343%
San Antonio - Ops Ctr (Bldg 106) | TX | 3922 | 3411.209 | 510.791 | 14.97% | 3350 | 572 | 17.07%
San Antonio - Ops Ctr GM | TX | 1396.8203 | NA |  |  | 1468 | -71.1797 | -4.849%
San Antonio - Ctr (Bldg 201) | TX | 9495.5 | NA |  |  | 9942 | -446.5 | -4.491%
San Antonio - Ops Ctr (Bldg 203) | TX | 3914.4594 | NA |  |  | 5021 | -1106.5406 | -22.04% | 1. Compared to last year’s (November and December) delta values, we still see a negative variance for this site, which suggests an issue with the forecasted value. Additionally, we do not have inverter communications for this site.
San Antonio - Ops Ctr (Bldg 205) | TX | 4272.1207 | 4180.985 | 91.1357 | 2.18% | 4343 | -70.8793 | -1.632%
San Antonio - Ops Ctr (Bldg 307) | TX | 2202.1374 | 2210.178 | -8.0406 | -0.3638% | 0 | 2202.1374
San Antonio - Ctr (Bldg 308) | TX | 3742 | 4308.516 | -566.516 | -13.15% | 5485.241 | -1743.241 | -31.78% | 1.Inverter 2 is down a string from 04/25 | 1.SR100421
San Antonio - Ops Ctr (Bldg 104) | TX | 5513.7305 | 3923.227 | 1590.5035 | 40.54% | 5950.638 | -436.9075 | -7.342%
San Antonio - Ops Ctr (Bldg 102) | TX | 96811.875 | 84016.8 | 12795.075 | 15.23% | 95505 | 1306.875 | 1.368%
N Black Canyon Hwy, Phoenix - North | AZ | 96812 | 84017 | 12795 | 15.23% | 95505 | 1307 | 1.369%
N Black Canyon Hwy, Phoenix - South | AZ | 102327 | 92222 | 10105 | 10.96% | 105383 | -3056 | -2.9% | 1.Inverter-16 is down a string and PM event was scheduled for 05/26/24 | 1.SR097838
Building 2222, Rose Garden Ln, Phoenix | AZ | 127173 | 122285 | 4888 | 3.997% | 129398 | -2225 | -1.72%
Building 2202, Rose Garden Ln, Phoenix | AZ | 127273 | 117897 | 9376 | 7.953% | 100842 | 26431 | 26.21%
99TH Ave & BELL | AZ | 22919 | 22548 | 371 | 1.645% | 22764 | 155 | 0.6809%
Rincon | AZ | 9308 | 7691 | 1617 | 21.02% | 8846 | 462 | 5.223%
Tucson Main Parking Garage | AZ | 10133 | 11960 | -1827 | -15.28% | 12075 | -1942 | -16.08% | 1.Inverters 1&3 were tripped offline at 11:30AM on 04/20 repoting ""Grid Phase Voltage Out of Range - GridV.OutLim""and were back online at 17:45 on 04/20 2.Site stopped communicating at 18:30 on 03/22,unable to confirm voltages.SIte came back online at 10:00MDT on 04/09 but energy was not backfilled 3.Production meter is reporting lower by approximately 7KW with B-phase current reading low compared to A&C. | 1.SR100039 2.SR098897 3.SR099589

## May
Wells Fargo |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 2214606.19 | 2048063 | 166543.19 | 8.132% | 2329515.801 | -114909.611 | -4.933%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 1195.5 | NA |  |  | 1376 | -180.5 | -13.12% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Otay Mesa | CA | 39.39 | NA |  |  | NA |  |  | 1. Production data taken from consumption meter.
San Leandro | CA | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site was offline throughout the month for EPC testing on nearby project and informed that site may remain offline until PTO of new project | 1.SR099548
Van Nuys | CA | 2061.3 | NA |  |  | 2794.801 | -733.501 | -26.25% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Lodi - Lodi Vineyard | CA | 55588 | 55517 | 71 | 0.1279% | 41391 | 14197 | 34.3%
Arden Fair Mall | CA | 27816 | 28227 | -411 | -1.456% | 26985 | 831 | 3.079%
Modesto - Modesto Main | CA | 21456 | 23407 | -1951 | -8.335% | 25073 | -3617 | -14.43% | 1. Inverters 1, 4, and 5 have some afternoon shading. Inverter 5 is underperforming by 3kW; likely soiling. | 1. SR101247
Stevens Creek | CA | 7317 | 7255 | 62 | 0.8546% | 7072 | 245 | 3.464%
Covina Main | CA | 4076 | 3614 | 462 | 12.78% | 3616 | 460 | 12.72%
Old Ranch Town Center | CA | 1461 | NA |  |  | 1587 | -126 | -7.94%
Mountain Gate Plaza | CA | 10399 | NA |  |  | 10810 | -411 | -3.802%
Arcadia Main | CA | 4670 | NA |  |  | 5150 | -480 | -9.32%
Fairfield | CA | 5152 | 5046 | 106 | 2.101% | 4903 | 249 | 5.079%
Los Gatos | CA | 2858 | 2850 | 8 | 0.2807% | 0 | 2858
San Marino | CA | 3835 | 4618 | -783 | -16.96% | 6185 | -2350 | -38% | 1.Inverter 2 is down a string from 04/25 | 1. SR100421
Buenaventura | CA | 5898 | 4301 | 1597 | 37.13% | 6331 | -433 | -6.839%
BE 199502 - Westgate | CA | 2686 | NA |  |  | 2413 | 273 | 11%
98th & Grant | CO | 1300 | NA |  |  | 2339 | -1039 | -44.42% | 1. Compared to last year’s delta values, we still see a negative variance for this site, which suggests an issue with the forecasted value. Additionally, we do not have inverter communications for this site.
Arapahoe Crossings | CO | 3270 | NA |  |  | 4307 | -1037 | -24.08% | 1. On 05/19 technican was onsite for preventive maintenance. Tech found inverter 3 has a derating issue that will need more troubleshooting and additionally the POA needs more troubleshooting to report accurately. | 1. PM8080
Aurora City Center | CO | 2110 | NA |  |  | 1972 | 138 | 6.998%
Dry Creek | CO | 2696 | NA |  |  | 2551 | 145 | 5.684%
Highlands Ranch S. | CO | 1925 | NA |  |  | 2417 | -492 | -20.36% | 1. The site was offline from 10:31 to 10:54 on 05/21 due to technician was onsite for preventive maintenance work. | 1. PM8141
Lone Tree | CO | 3677 | NA |  |  | 5500 | -1823 | -33.15% | 1.Inverter 2 has been offline since 05/20 and is currently in the process of being replaced. | 1.SR101743
Meridian | CO | 3650 | NA |  |  | 3150 | 500 | 15.87%
Southglenn | CO | 3663 | NA |  |  | 3267 | 396 | 12.12%
Standley Lake | CO | 4329 | NA |  |  | 4357 | -28 | -0.6426%
Havana Gardens | CO | 4144 | NA |  |  | 1695 | 2449 | 144.5%
East Hartford | CT | 712 | 1656 | -944 | -57% | 1047 | -335 | -32% | 1. Site production was low on 05/05, 05/06, 05/21 to 05/23, 05/31 due to rain.
Norwalk | CT | 844 | 2 | 842 | 42100% | 1235 | -391 | -31.66% | 1.An intermittent issue with Meter Phase C/Power Factor is slightly affecting the reported energy production. A case has been created with AlsoEnergy, and they have confirmed a site visit for further investigation 2.Weather station reporting erroneous values from 07/04/2024.This issue is to be investigated next time onsite | 1.SR077700 2.SR088667
Hialeah Gardens | FL | 957 | 4535 | -3578 | -78.9% | 5552 | -4595 | -82.76% | 1. Site underperforming by ~15 kW. Production appears capped at 1.6 kW on high irradiance days, with brief spikes. Will be investigating during next site visit. | 1.SR098782
W. Des Moines Campus EAST | IA | 196673 | 184996 | 11677 | 6.312% | 192800 | 3873 | 2.009%
W. Des Moines Campus SW | IA | 97841 | 90857 | 6984 | 7.687% | 94941 | 2900 | 3.055%
WF - CIC | NC | 169288 | 171249 | -1961 | -1.145% | 206727 | -37439 | -18.11% | 1.Inverter 13 tripped offline at 17:00 on 05/03,possibly due to bad weather and back online on 05/04 | 1.SR100975
Charlotte - Wells Fargo - DUC | NC | 170113 | 186468 | -16355 | -8.771% | 184494 | -14381 | -7.795%
East Windsor | NJ | 976 | 781 | 195 | 24.97% | 1295 | -319 | -24.63% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Burlington | NJ | 2447 | 2403 | 44 | 1.831% | 3332 | -885 | -26.56% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Bayonne | NJ | 3160 | 2969 | 191 | 6.433% | 3776 | -616 | -16.31% | 1. Site production was low on 05/04, 05/05, 05/09, 05/13, 05/22, 05/28 due to rain.
Clifton | NJ | 3723 | 3823 | -100 | -2.616% | 4453 | -730 | -16.39% | 1. Site production was low on 05/04, 05/05, 05/09, 05/13, 05/22, 05/28 due to rain.
North Elizabeth | NJ | 2522 | 1918 | 604 | 31.49% | 4136 | -1614 | -39.02% | 1.The site was offline from 14:30 on 05/15 to 13:00 on 05/19 and again from 08:15 on 05/25 to 11:15 on 05/27. The issue occurred because the disconnect lock was opened by the fire department. The site was restored after a CBRE technician closed the disconnect | 1.SR101597,SR101928
Haddon Westmont Plaza | NJ | 2492 | 2439 | 53 | 2.173% | 3063 | -571 | -18.64% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Parsippany | NJ | 2730 | 2519 | 211 | 8.376% | 3536 | -806 | -22.79% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Clark | NJ | 173 | 2290 | -2117 | -92.45% | 2878 | -2705 | -93.99% | 1.Inverter 1 tripped offline due to an insolation error at 13:15 on 05/02 and remained offline throughout the month. | 1.SR100951
Closter | NJ | 1220 | 1006 | 214 | 21.27% | 1802 | -582 | -32.3% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Holmdel | NJ | 2065 | 6305 | -4240 | -67.25% | 2540 | -475 | -18.7% | 1.Weather station constantly reporting a fixed value of 1237.22 W/m2 during production hours.Reached out to AlsoEnergy for remote assistance and waiting for their response | 1.SR100979
Ellisburg Circle Center | NJ | 1101 | 1095 | 6 | 0.5479% | 1417 | -316 | -22.3% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Nutley | NJ | 4066 | 3291 | 775 | 23.55% | 4964 | -898 | -18.09% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Marlton | NJ | 3815 | 3516 | 299 | 8.504% | 4949 | -1134 | -22.91% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Middletown | NJ | 2881 | 2489 | 392 | 15.75% | 4026 | -1145 | -28.44% | 1.Weather station is frequently reporting erroneous values ( 0 w/m^2). Has been happening intermittently since 4/14 | 1.SR100592
Whiting Crestwood | NJ | 3679 | 3506 | 173 | 4.934% | 5307 | -1628 | -30.68% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Barnegat | NJ | 5837 | 5283 | 554 | 10.49% | 7665 | -1828 | -23.85% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Manchester | NJ | 2102 | 2379 | -277 | -11.64% | 4398 | -2296 | -52.21% | 1. Site production was low on 05/04, 05/05, 05/13, 05/14, 05/22, 05/28, 05/30 due to rain.
West Deptford - Woodbury | NJ | 3352 | 3605 | -253 | -7.018% | 4204 | -852 | -20.27% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Edison | NJ | 2955 | 2967 | -12 | -0.4044% | 3787 | -832 | -21.97% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Flemington | NJ | 2911 | 2994 | -83 | -2.772% | 3786 | -875 | -23.11% | 1.Inverter 1 tripped offline at 11:15 on 05/16 and back online at 12:45 on 05/16 likely due to bad weather | 1.SR101587
Route 22 | NJ | 2754 | 2990 | -236 | -7.893% | 3533 | -779 | -22.05% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Laurelton | NJ | 1713 | 2647 | -934 | -35.29% | 3329 | -1616 | -48.54% | 1. Site production was low on 05/04, 05/05, 05/13, 05/14, 05/22, 05/28, 05/30 due to rain.
Mahwah | NJ | 2185 | 390 | 1795 | 460.3% | 3198 | -1013 | -31.68% | 1. Weather station is frequently reporting erroneous values ( 0 w/m^2) during mid days.We have reached out to AlsoEnergy for remote assistance and waiting for their response | 1.SR100593
Franklin Township WF | NJ | 2602 | 2630 | -28 | -1.065% | 3295 | -693 | -21.03% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Bordentown | NJ | 1966 | 1836 | 130 | 7.081% | 2562 | -596 | -23.26% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
South Plainfield | NJ | 1437 | 1454 | -17 | -1.169% | 1804 | -367 | -20.34% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Somerset | NJ | 2349 | 2309 | 40 | 1.732% | 3043 | -694 | -22.81% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Clinton Main Relo | NJ | 2835 | 2845 | -10 | -0.3515% | 3388 | -553 | -16.32% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
North Brunswick | NJ | 2828 | 2666 | 162 | 6.077% | 3910 | -1082 | -27.67% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Cherry Hill | NJ | 1977 | 1909 | 68 | 3.562% | 2562 | -585 | -22.83% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Hainesport | NJ | 1961 | 2236 | -275 | -12.3% | 2590 | -629 | -24.29% | 1. Site production was low on 05/04, 05/05, 05/13, 05/14, 05/22, 05/28, 05/30 due to rain.
San Antonio - Ops Ctr (Bldg 106) | TX | 56872 | 41952 | 14920 | 35.56% | 57873 | -1001 | -1.73% | 1.Inverter 4 has been derating to 40 kW due to a fan fault on intermittent days since 04/01.Reached out to CPS for RMA of fans | 1.SR099750
San Antonio - Ops Ctr GM | TX | 377299 | 414548 | -37249 | -8.985% | 419951 | -42652 | -10.16% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
San Antonio - Ctr (Bldg 201) | TX | 56619 | 41658 | 14961 | 35.91% | 56256 | 363 | 0.6453%
San Antonio - Ops Ctr (Bldg 203) | TX | 56545 | 54798 | 1747 | 3.188% | 56838 | -293 | -0.5155%
San Antonio - Ops Ctr (Bldg 205) | TX | 52663 | 37950 | 14713 | 38.77% | 54582 | -1919 | -3.516%
San Antonio - Ops Ctr (Bldg 307) | TX | 45090 | 41272 | 3818 | 9.251% | 55343 | -10253 | -18.53% | 1. The inverter was offline from 09:30 CDT on 04/20. The technician later replaced the inverter's powerhead on 05/29, and it came back online at 11:00 CDT on the same day. | 1. SR100040
San Antonio - Ctr (Bldg 308) | TX | 53189 | 40327 | 12862 | 31.89% | 52695 | 494 | 0.9375%
San Antonio - Ops Ctr (Bldg 104) | TX | 12162 | 12637 | -475 | -3.759% | 16753 | -4591 | -27.4% | 1. The meter had no communication starting from 05/01. Technician later found water intrusion in an unused enclosure, disconnected the unused wiring, and the meter resumed normal communication at 11:00 CDT on 05/20. 2. Inverter 104.1 underperforming from 05/20 since meter rewiring performed on SR101240 (unused wiring disconnected). Capacity appears to be down about 2/3, may be 2 MPPTs offline. Possibility of wiring disconnected on SR101240 causing underperformance. | 1.SR101240 2.SR101804
San Antonio - Ops Ctr (Bldg 102) | TX | 59387 |  |  |  | 59470 | -83 | -0.1396%
N Black Canyon Hwy, Phoenix - North | AZ | 104374 | 90017 | 14357 | 15.95% | 103734 | 640 | 0.617%
N Black Canyon Hwy, Phoenix - South | AZ | 109631 | 98743 | 10888 | 11.03% | 114142 | -4511 | -3.952% | 1. Inverter 16 is derating at 32 kW on 05/22, 05/24, 05/28, 05/29 and reporting "External Fan Err - ExtFanerr". | 1. SR101864
Building 2222, Rose Garden Ln, Phoenix | AZ | 141166 | 135638 | 5528 | 4.076% | 145680 | -4514 | -3.099%
Building 2202, Rose Garden Ln, Phoenix | AZ | 141413 | 135365 | 6048 | 4.468% | 115501 | 25912 | 22.43%
99TH Ave & BELL | AZ | 25162 | 24369 | 793 | 3.254% | 25018 | 144 | 0.5756% | 1. Inverter 2 is tripping on and offline frequently through out the month. | 1. SR101434
Rincon | AZ | 9598 | 8335 | 1263 | 15.15% | 10052 | -454 | -4.517%
Tucson Main Parking Garage | AZ | 10922 | 14366 | -3444 | -23.97% | 13062 | -2140 | -16.38% | 1. Production meter is reporting lower by approximately 7KW with B-phase current reading low compared to A&C. 2. Inverter 1 tripping on and off frequently on 05/17, 05/19, 05/20, 05/24, 05/25 due to "Grid Phase Voltage Out of Range - GridV.OutLim". | 1. SR99589 2.SR101626

## Jun
Wells Fargo |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 2291774.901 | 2076001 | 215773.901 | 10.39% | 2367832.422 | -76057.521 | -3.212%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 1280.8 | N/A |  |  | 1338 | -57.2 | -4.275%
Otay Mesa | CA | 38.201 | N/A |  |  | N/A |  |  | 1. Production data taken from consumption meter.
San Leandro | CA | 0 | N/A |  |  | 0 | 0 |  | 1. Site was not communicated for whole month. | 1. SR099548
Van Nuys | CA | 2144.9 | N/A |  |  | 2731.422 | -586.522 | -21.47% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Lodi - Lodi Vineyard | CA | 53971 | 45437 | 8534 | 18.78% | 42651 | 11320 | 26.54%
Arden Fair Mall | CA | 27404 | 27208 | 196 | 0.7204% | 28033 | -629 | -2.244%
Modesto - Modesto Main | CA | 21371 | 22792 | -1421 | -6.235% | 25471 | -4100 | -16.1% | 1. Inverters 1, 4, and 5 have some afternoon shading issues. | 1. SR101247
Stevens Creek | CA | 7085 | 7193 | -108 | -1.501% | 7609 | -524 | -6.887%
Covina Main | CA | 4528 | 4150 | 378 | 9.108% | 3875 | 653 | 16.85%
Old Ranch Town Center | CA | 1466 | N/A |  |  | 1683 | -217 | -12.89% | The plant is performing as expected. The forecasted (theoretical) values may appear higher because they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance.
Mountain Gate Plaza | CA | 11481 | N/A |  |  | 11092 | 389 | 3.507%
Arcadia Main | CA | 5118 | N/A |  |  | 5550 | -432 | -7.784%
Fairfield | CA | 5079 | 5001 | 78 | 1.56% | 5137 | -58 | -1.129%
Los Gatos | CA | 2809 | 2833 | -24 | -0.8472% | 0 | 2809
San Marino | CA | 3651 | 5234 | -1583 | -30.24% | 6390 | -2739 | -42.86% | 1. Inverter 1 is underperforming by 13kW and inverter 2 by 10kW. Pending quote for return visit. | 1. SR100421
Buenaventura | CA | 5133 | 3802 | 1331 | 35.01% | 5944 | -811 | -13.64% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
BE 199502 - Westgate | CA | 2587 | N/A |  |  | 2485 | 102 | 4%
98th & Grant | CO | 1895 | N/A |  |  | 2315 | -420 | -18.14% | 1. Compared to last year’s delta values, we still see a negative variance for this site, which suggests an issue with the forecasted value. Additionally, we do not have inverter communications for this site.
Arapahoe Crossings | CO | 3184 | N/A |  |  | 4281 | -1097 | -25.62% | 1. Tech found inverter 3 has a derating issue that will need more troubleshooting and additionally the POA needs more troubleshooting to report accurately. | 1. PM8080
Aurora City Center | CO | 2154 | N/A |  |  | 1950 | 204 | 10.46%
Dry Creek | CO | 2659 | N/A |  |  | 2528 | 131 | 5.182%
Highlands Ranch S. | CO | 2194 | N/A |  |  | 2420 | -226 | -9.339%
Lone Tree | CO | 3085 | N/A |  |  | 5490 | -2405 | -43.81% | 1. Inverter 2 was offline for the entire month and will be investigated in 2026 | 1. SR101743
Meridian | CO | 3588 | N/A |  |  | 3132 | 456 | 14.56%
Southglenn | CO | 3486 | N/A |  |  | 3248 | 238 | 7.328%
Standley Lake | CO | 3540 | N/A |  |  | 4331 | -791 | -18.26% | 1. The site was offline from 10:15 to 11:30 on 06/13 due to technician was onsite for preventive maintenance. | 1. PM9554
Havana Gardens | CO | 4153 | N/A |  |  | 1684 | 2469 | 146.6% | The plant is performing as expected. The forecasted (theoretical) values may appear lower and they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance.
East Hartford | CT | 797 | 1756 | -959 | -54.61% | 892 | -95 | -10.65% | 1. Site production was low on 06/07, 06/10, 06/14, 06/15, 06/17 due to cloudy weather and rain.
Norwalk | CT | 951 | 10 | 941 | 9410% | 1043 | -92 | -8.821% | 1. Weather station reporting erroneous values from 07/04/2024. Will investigate next time onsite 2. An intermittent issue with Meter Phase C/Power Factor is slightly affecting the reported energy production. A case has been created with AlsoEnergy, and they have confirmed a site visit for further investigation | 1. SR088667 2. SR066760 SR077700
Hialeah Gardens | FL | 756 | 3999 | -3243 | -81.1% | 5101 | -4345 | -85.18% | 1. Site underperforming by ~15 kW. Production appears capped at 1.6 kW on high irradiance days, with brief spikes. Will be investigating during next site visit. | 1.SR098782
W. Des Moines Campus EAST | IA | 187573 | 177056 | 10517 | 5.94% | 203700 | -16127 | -7.917%
W. Des Moines Campus SW | IA | 93644 | 85696 | 7948 | 9.275% | 100117 | -6473 | -6.465%
WF - CIC | NC | 203688 | 201034 | 2654 | 1.32% | 209637 | -5949 | -2.838%
Charlotte - Wells Fargo - DUC | NC | 204599 | 221905 | -17306 | -7.799% | 183212 | 21387 | 11.67%
East Windsor | NJ | 1055 | 852 | 203 | 23.83% | 1071 | -16 | -1.494%
Burlington | NJ | 2641 | 2575 | 66 | 2.563% | 2790 | -149 | -5.341%
Bayonne | NJ | 3371 | 3113 | 258 | 8.288% | 3828 | -457 | -11.94% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Clifton | NJ | 4028 | 4072 | -44 | -1.081% | 4873 | -845 | -17.34% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
North Elizabeth | NJ | 3565 | 3117 | 448 | 14.37% | 3589 | -24 | -0.6687%
Haddon Westmont Plaza | NJ | 2647 | 2590 | 57 | 2.201% | 2641 | 6 | 0.2272%
Parsippany | NJ | 2995 | 2732 | 263 | 9.627% | 2915 | 80 | 2.744%
Clark | NJ | 1916 | 2402 | -486 | -20.23% | 2493 | -577 | -23.14% | 1. Site was offline from 05/02 to 12:00 on 06/05 and 2 strings were isolated on inverter on 06/05. | 1. SR100951
Closter | NJ | 1395 | 1110 | 285 | 25.68% | 1543 | -148 | -9.592%
Holmdel | NJ | 2200 | 5955 | -3755 | -63.06% | 2178 | 22 | 1.01% | 1. Weather station constantly reporting a fixed value of 1237.22 W/m2 since 01/09. Will investigate next time onsite | 1. SR100979
Ellisburg Circle Center | NJ | 1081 | 1162 | -81 | -6.971% | 1215 | -134 | -11.03% | 1. Inverter 1 tripped offline on 06/23, 06/24, and 06/25, but self-resolved on the following days. | 1. SR103327
Nutley | NJ | 4384 | 3449 | 935 | 27.11% | 4329 | 55 | 1.271%
Marlton | NJ | 4146 | 3758 | 388 | 10.32% | 4268 | -122 | -2.858%
Middletown | NJ | 3092 | 2419 | 673 | 27.82% | 3415 | -323 | -9.458%
Whiting Crestwood | NJ | 4009 | 3793 | 216 | 5.695% | 4573 | -564 | -12.33% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Barnegat | NJ | 5927 | 5281 | 646 | 12.23% | 6461 | -534 | -8.265% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Manchester | NJ | 2276 | 2476 | -200 | -8.078% | 3828 | -1552 | -40.54% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
West Deptford - Woodbury | NJ | 3520 | 3766 | -246 | -6.532% | 3623 | -103 | -2.843%
Edison | NJ | 3125 | 3126 | -1 | -0.03199% | 3153 | -28 | -0.888%
Flemington | NJ | 3075 | 3292 | -217 | -6.592% | 3292 | -217 | -6.592%
Route 22 | NJ | 2902 | 3142 | -240 | -7.638% | 3042 | -140 | -4.602%
Laurelton | NJ | 1749 | 2830 | -1081 | -38.2% | 2902 | -1153 | -39.73% | 1. Inverter 1 tripped offline at 11am on 06/26 and displaying fault Grid Phase Voltage Out of Range - GridV.OutLim and back online at 8:00am on 06/27 | 1. SR103607
Mahwah | NJ | 2469 | 280 | 2189 | 781.8% | 2689 | -220 | -8.181% | 1. Weather station is frequently reporting erroneous values ( 0 w/m^2) during mid days.We have reached out to AlsoEnergy for remote assistance and waiting for their response | 1.SR100593
Franklin Township WF | NJ | 2765 | 2769 | -4 | -0.1445% | 3329 | -564 | -16.94% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Bordentown | NJ | 2109 | 1980 | 129 | 6.515% | 2070 | 39 | 1.884%
South Plainfield | NJ | 1526 | 1550 | -24 | -1.548% | 1529 | -3 | -0.1962%
Somerset | NJ | 2531 | 2376 | 155 | 6.524% | 2548 | -17 | -0.6672%
Clinton Main Relo | NJ | 3000 | 2994 | 6 | 0.2004% | 3072 | -72 | -2.344%
North Brunswick | NJ | 3047 | 2832 | 215 | 7.592% | 3311 | -264 | -7.973%
Cherry Hill | NJ | 2089 | 2001 | 88 | 4.398% | 2189 | -100 | -4.568%
Hainesport | NJ | 2096 | 2476 | -380 | -15.35% | 2131 | -35 | -1.642% | 1. Site production was low on 06/08 to 06/10 and 06/15 due to rain.
San Antonio - Ops Ctr (Bldg 106) | TX | 57144 | 36923 | 20221 | 54.77% | 60352 | -3208 | -5.315% | 1.Inverter 4 has been derating to 40 kW due to a fan fault on intermittent days since 04/01.Reached out to CPS for RMA of fans | 1.SR099750
San Antonio - Ops Ctr GM | TX | 364099 | 414699 | -50600 | -12.2% | 435826 | -71727 | -16.46% | 1. The weather station data indicates normal irradiance levels, and no major issues were observed on site. Based on the available information, the system performance appears consistent with typical operating conditions.
San Antonio - Ctr (Bldg 201) | TX | 56116 | 36662 | 19454 | 53.06% | 59408 | -3292 | -5.541% | The virtual weather station has experienced intermittent communication issues, in contrast to the actual weather station at Building 203, San Antonio Ops Center (S64346), which is reporting without any issues. A case (#595841) has been opened with AlsoEnergy to reconfigure the virtual weather station accordingly.
San Antonio - Ops Ctr (Bldg 203) | TX | 56352 | 55054 | 1298 | 2.358% | 59706 | -3354 | -5.618%
San Antonio - Ops Ctr (Bldg 205) | TX | 53064 | 33415 | 19649 | 58.8% | 57104 | -4040 | -7.075% | The virtual weather station has experienced intermittent communication issues, in contrast to the actual weather station at Building 203, San Antonio Ops Center (S64346), which is reporting without any issues. A case (#595841) has been opened with AlsoEnergy to reconfigure the virtual weather station accordingly.
San Antonio - Ops Ctr (Bldg 307) | TX | 55200 | 36347 | 18853 | 51.87% | 57923 | -2723 | -4.701% | The virtual weather station has experienced intermittent communication issues, in contrast to the actual weather station at Building 203, San Antonio Ops Center (S64346), which is reporting without any issues. A case (#595841) has been opened with AlsoEnergy to reconfigure the virtual weather station accordingly.
San Antonio - Ctr (Bldg 308) | TX | 53178 | 35480 | 17698 | 49.88% | 55158 | -1980 | -3.59% | The virtual weather station has experienced intermittent communication issues, in contrast to the actual weather station at Building 203, San Antonio Ops Center (S64346), which is reporting without any issues. A case (#595841) has been opened with AlsoEnergy to reconfigure the virtual weather station accordingly.
San Antonio - Ops Ctr (Bldg 104) | TX | 15904 | 11126 | 4778 | 42.94% | 17500 | -1596 | -9.12% | The virtual weather station has experienced intermittent communication issues, in contrast to the actual weather station at Building 203, San Antonio Ops Center (S64346), which is reporting without any issues. A case (#595841) has been opened with AlsoEnergy to reconfigure the virtual weather station accordingly.
San Antonio - Ops Ctr (Bldg 102) | TX | 59520 | N/A |  |  | 61996 | -2476 | -3.994%
N Black Canyon Hwy, Phoenix - North | AZ | 105478 | 88938 | 16540 | 18.6% | 103056 | 2422 | 2.35%
N Black Canyon Hwy, Phoenix - South | AZ | 102640 | 97431 | 5209 | 5.346% | 113359 | -10719 | -9.456%
Building 2222, Rose Garden Ln, Phoenix | AZ | 146172 | 138948 | 7224 | 5.199% | 146011 | 161 | 0.1103%
Building 2202, Rose Garden Ln, Phoenix | AZ | 146183 | 140917 | 5266 | 3.737% | 113317 | 32866 | 29%
99TH Ave & BELL | AZ | 25488 | 23304 | 2184 | 9.372% | 24928 | 560 | 2.246% | 1. Inverter 2 is tripping on and offline frequently through out the month. | 1. SR101434
Rincon | AZ | 9521 | 8355 | 1166 | 13.96% | 9607 | -86 | -0.8952%
Tucson Main Parking Garage | AZ | 21892 | 17026 | 4866 | 28.58% | 12621 | 9271 | 73.46% | 1. Production meter is reporting lower by approximately 7KW with B-phase current reading low compared to A&C. | 1.SR098897

## Jul
Wells Fargo |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 2231473.101 | 2110475 | 120998.101 | 5.733% | 2397902.231 | -166429.13 | -6.941% |  |  |  | Performance vs Prior Year | Notes
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests |  | + or -
Adams & Broadway | CA | 1342.5 | N/A |  |  | 1364 | -21.5 | -1.576% |  |  | No weather station on the Legacy sites
Otay Mesa | CA | 39.301 | N/A |  |  | N/A |  |  | 1. Production data taken from consumption meter.
San Leandro | CA | 0 | N/A |  |  | 0 | 0 |  | 1. Site was not communicated for whole month. | 1.SR099548
Van Nuys | CA | 2166.3 | N/A |  |  | 2735.231 | -568.931 | -20.8% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Lodi - Lodi Vineyard | CA | 51556 | 46484 | 5072 | 10.91% | 44559 | 6997 | 15.7%
Arden Fair Mall | CA | 26900 | 27313 | -413 | -1.512% | 28718 | -1818 | -6.331% |  |  |  | -
Modesto - Modesto Main | CA | 20579 | 22391 | -1812 | -8.093% | 26304 | -5725 | -21.76% | 1. Inverters 1, 4, and 5 have some afternoon shading issues. | 1.SR101247 |  | -
Stevens Creek | CA | 6675 | 7096 | -421 | -5.933% | 7887 | -1212 | -15.37% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance. |  |  | +
Covina Main | CA | 4616 | 4541 | 75 | 1.652% | 4147 | 469 | 11.31%
Old Ranch Town Center | CA | 1532 | N/A |  |  | 1742 | -210 | -12.06% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Mountain Gate Plaza | CA | 11390 | N/A |  |  | 11486 | -96 | -0.8358%
Arcadia Main | CA | 5221 | N/A |  |  | 6209 | -988 | -15.91% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Fairfield | CA | 4973 | 4885 | 88 | 1.801% | 5311 | -338 | -6.364%
Los Gatos | CA | 2733 | 2795 | -62 | -2.218% | 0 | 2733 |  |  |  |  | - | Forecasted model might be inaccurate.
San Marino | CA | 4254 | 5790 | -1536 | -26.53% | 6929 | -2675 | -38.61% | 1. Inverter 1 is underperforming by 13kW and inverter 2 by 10kW. Pending quote for return visit. | 1.SR104629 |  | - | SR087054 stems from the 2024 PM
Buenaventura | CA | 5733 | 4263 | 1470 | 34.48% | 6207 | -474 | -7.637% |  |  |  | -
BE 199502 - Westgate | CA | 2478 | 0 | 2478 |  | 2634 | -156 | -5.923% |  |  |  | - | Still waiting on a response from Wells Fargo dating back to 2023
98th & Grant | CO | 2432 | N/A |  |  | 2218 | 214 | 9.648% |  |  |  | +
Arapahoe Crossings | CO | 3164 | N/A |  |  | 4185 | -1021 | -24.4% | 1. Meter B and C phase currents are half of A phase current for whole month | 1.SR105604 |  | - | Up 2% from 2024 weather adj. (expected)
Aurora City Center | CO | 632 | N/A |  |  | 1923 | -1291 | -67.13% | 1. Site was offline from 07/09 through out the month. | 1.SR103075 |  | +
Dry Creek | CO | 2620 | N/A |  |  | 2426 | 194 | 7.997%
Highlands Ranch S. | CO | 2185 | N/A |  |  | 2380 | -195 | -8.193% |  |  |  | + | Up 9% from 2024 weather adj. (expected)
Lone Tree | CO | 3439 | N/A |  |  | 5432 | -1993 | -36.69% | 1.Meter stopped communicating at 07/30 at 10:45pm till end of the month 2. Inverter 2 was offline for the entire month and will be investigated in 2026 | 1.SR105436 2.SR101743 |  | +
Meridian | CO | 3524 | N/A |  |  | 3145 | 379 | 12.05% |  |  |  | +
Southglenn | CO | 3464 | N/A |  |  | 3174 | 290 | 9.137% |  |  |  | - | Nothing mechanical
Standley Lake | CO | 4110 | N/A |  |  | 4231 | -121 | -2.86% | 1.Meter C phase current dropped 20 amps from 7/13/25. | 1.SR105517 |  | + | Up 4% from 2024 weather adj. (expected)
Havana Gardens | CO | 4125 | N/A |  |  | 1646 | 2479 | 150.6% | The plant is performing as expected. The forecasted (theoretical) values may appear lower and they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance. |  |  | +
East Hartford | CT | 895 | 1945 | -1050 | -53.98% | 929 | -34 | -3.66% | 1.BOM sensor fell off. Will repair next time onsite | 1.SR087054 |  | + | Up 6% from 2024 weather adj. (expected)
Norwalk | CT | 1031 | 0 | 1031 |  | 1142 | -111 | -9.72% | 1. Weather station reporting erroneous values from 07/04/2024. Will investigate next time onsite 2. An intermittent issue with Meter Phase C/Power Factor is slightly affecting the reported energy production. A case has been created with AlsoEnergy, and they have confirmed a site visit for further investigation | 1.SR088667 2.SR077700 |  | +
Hialeah Gardens | FL | 833 | 4925 | -4092 | -83.09% | 5675 | -4842 | -85.32% | 1. Site underperforming by ~15 kW. Production appears capped at 1.6 kW on high irradiance days, with brief spikes. Will be investigating during next site visit. | 1.SR098782 |  | + | Up 3% from 2024 weather adj. (expected); forecasted model might be inaccurate.
W. Des Moines Campus EAST | IA | 198640 | 192284 | 6356 | 3.306% | 204900 | -6260 | -3.055% |  |  |  | - | Weather station issue is negatively impacting the weather adj. (expected)
W. Des Moines Campus SW | IA | 90104 | 93694 | -3590 | -3.832% | 100519 | -10415 | -10.36% | 1.Inverter 1 underperforming by 8kW (1 string) from 7/28/25. 2. Inverter 2 tripped offline at 08:45CDT on 07/20 | 1.SR105483 2.SR105331 |  | + | Up 3% from 2024 weather adj. (expected)
WF - CIC | NC | 204468 | 203434 | 1034 | 0.5083% | 210055 | -5587 | -2.66% |  |  |  | + | Up 26% from 2024 weather adj. (expected)
Charlotte - Wells Fargo - DUC | NC | 201246 | 221443 | -20197 | -9.121% | 179547 | 21699 | 12.09% | 1. Inverter 12 appears to be down at least one string, maybe two, when compared with peers | 1.SR099323 |  | + | Up 3% from 2024 weather adj. (expected)
East Windsor | NJ | 1198 | 1054 | 144 | 13.66% | 1203 | -5 | -0.4156% |  |  |  |  | Weather station issue is positively impacting the weather adj. (expected)
Burlington | NJ | 2957 | 2853 | 104 | 3.645% | 3072 | -115 | -3.743% |  |  |  | NC
Bayonne | NJ | 3984 | 3676 | 308 | 8.379% | 3875 | 109 | 2.813% |  |  |  | +
Clifton | NJ | 4727 | 4797 | -70 | -1.459% | 5091 | -364 | -7.15% |  |  |  | - | Forecasted model might be inaccurate.
North Elizabeth | NJ | 4079 | 3757 | 322 | 8.571% | 3903 | 176 | 4.509% |  |  |  | NC
Haddon Westmont Plaza | NJ | 2901 | 2798 | 103 | 3.681% | 2876 | 25 | 0.8693% |  |  |  | NC
Parsippany | NJ | 3548 | 3275 | 273 | 8.336% | 3439 | 109 | 3.17% |  |  |  | NC
Clark | NJ | 2938 | 2835 | 103 | 3.633% | 2809 | 129 | 4.592% |  |  |  | -
Closter | NJ | 1549 | 1199 | 350 | 29.19% | 1739 | -190 | -10.93% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Holmdel | NJ | 2513 | 6085 | -3572 | -58.7% | 2332 | 181 | 7.762% | 1. Weather station constantly reporting a fixed value of 1237.22 W/m2 since 01/09. Will investigate next time onsite | 1.SR100979 |  |  | Weather adj. (expected) impacted by Weather station issue.
Ellisburg Circle Center | NJ | 1325 | 1274 | 51 | 4.003% | 1332 | -7 | -0.5255%
Nutley | NJ | 5189 | 4003 | 1186 | 29.63% | 4918 | 271 | 5.51%
Marlton | NJ | 4549 | 4095 | 454 | 11.09% | 4583 | -34 | -0.7419%
Middletown | NJ | 3657 | 1826 | 1831 | 100.3% | 3679 | -22 | -0.598% | Weather station is frequently reporting erroneous values ( 0 w/m^2). Has been happening intermittently since 4/14 | 1.SR100592
Whiting Crestwood | NJ | 4614 | 4551 | 63 | 1.384% | 4974 | -360 | -7.238%
Barnegat | NJ | 6803 | 6005 | 798 | 13.29% | 6872 | -69 | -1.004%
Manchester | NJ | 2590 | 2825 | -235 | -8.319% | 4195 | -1605 | -38.26% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
West Deptford - Woodbury | NJ | 4008 | 4210 | -202 | -4.798% | 3884 | 124 | 3.193%
Edison | NJ | 3650 | 3666 | -16 | -0.4364% | 3608 | 42 | 1.164% |  |  |  | + | Up 5% from 2024 weather adj. (expected)
Flemington | NJ | 3518 | 3715 | -197 | -5.303% | 3731 | -213 | -5.709% |  |  |  | - | Up 3% from 2024 weather adj. (expected). Possible issue with the data used to calculate the expected; inquiry with AE Support.
Route 22 | NJ | 2982 | 3286 | -304 | -9.251% | 3517 | -535 | -15.21% | 1. Site was offline frm 07/07 and back online on 07/09 at 16:00 | 1.SR104082 |  | + | Forecasted model might be inaccurate.
Laurelton | NJ | 1985 | 3045 | -1060 | -34.81% | 3103 | -1118 | -36.03% | 1.Production meter phase A volts are offline | 1.SR075812 |  | + | Forecasted model might be inaccurate.
Mahwah | NJ | 2839 | 347 | 2492 | 718.2% | 3083 | -244 | -7.914% | 1. Weather station is frequently reporting erroneous values ( 0 w/m^2) during mid days.We have reached out to AlsoEnergy for remote assistance and waiting for their response | 1.SR100593 |  | + | Forecasted model might be inaccurate.
Franklin Township WF | NJ | 3185 | 3168 | 17 | 0.5366% | 3453 | -268 | -7.761% |  |  |  | + | Forecasted model might be inaccurate.
Bordentown | NJ | 2418 | 2227 | 191 | 8.577% | 2340 | 78 | 3.333% |  |  |  | + | Forecasted model might be inaccurate.
South Plainfield | NJ | 1796 | 1772 | 24 | 1.354% | 1698 | 98 | 5.771% |  |  |  | + | Forecasted model might be inaccurate.
Somerset | NJ | 2945 | 2752 | 193 | 7.013% | 2908 | 37 | 1.272% |  |  |  | + | Forecasted model might be inaccurate.
Clinton Main Relo | NJ | 3447 | 3490 | -43 | -1.232% | 3434 | 13 | 0.3786% |  |  |  | +
North Brunswick | NJ | 3501 | 3177 | 324 | 10.2% | 3738 | -237 | -6.34% |  |  |  | -
Cherry Hill | NJ | 2331 | 2230 | 101 | 4.529% | 2349 | -18 | -0.7663% |  |  |  | -
Hainesport | NJ | 2405 | 2847 | -442 | -15.53% | 2309 | 96 | 4.158% |  |  |  | - | Forecasted model might be inaccurate.
San Antonio - Ops Ctr (Bldg 106) | TX | 51871 | 46883 | 4988 | 10.64% | 63073 | -11202 | -17.76% | 1.Inverter 4 is derating at 40 kW through out the month | 1.SR099750 |  | +
San Antonio - Ops Ctr GM | TX | 349532 | 388728 | -39196 | -10.08% | 461978 | -112446 | -24.34% |  |  |  |  | Forecasted model might be inaccurate.
San Antonio - Ctr (Bldg 201) | TX | 52526 | 46502 | 6024 | 12.95% | 62303 | -9777 | -15.69%
San Antonio - Ops Ctr (Bldg 203) | TX | 52306 | 50501 | 1805 | 3.574% | 62578 | -10272 | -16.41% |  |  |  |  | Forecasted model might be inaccurate.
San Antonio - Ops Ctr (Bldg 205) | TX | 48677 | 42369 | 6308 | 14.89% | 59706 | -11029 | -18.47%
San Antonio - Ops Ctr (Bldg 307) | TX | 50988 | 46074 | 4914 | 10.67% | 60626 | -9638 | -15.9%
San Antonio - Ctr (Bldg 308) | TX | 48110 | 45025 | 3085 | 6.852% | 57851 | -9741 | -16.84% | 1.Inverter 4 tripped offline at 11:20 cdt on 07/29 and remained the same throughout the month. | 1.SR105312 |  | - | Forecasted model might be inaccurate.
San Antonio - Ops Ctr (Bldg 104) | TX | 14452 | 14120 | 332 | 2.351% | 18302 | -3850 | -21.04% |  |  |  | +
San Antonio - Ops Ctr (Bldg 102) | TX | 54507 | N/A |  |  | 64945 | -10438 | -16.07% |  |  |  | + | Sites live Jan 2025
N Black Canyon Hwy, Phoenix - North | AZ | 101492 | 83570 | 17922 | 21.45% | 98348 | 3144 | 3.197% |  |  |  | + | Sites live Jan 2025
N Black Canyon Hwy, Phoenix - South | AZ | 104766 | 91413 | 13353 | 14.61% | 108066 | -3300 | -3.054% |  |  |  |  | Sites live Jan 2025
Building 2222, Rose Garden Ln, Phoenix | AZ | 137056 | 134328 | 2728 | 2.031% | 137881 | -825 | -0.5983% |  |  |  | + | Sites live Jan 2025
Building 2202, Rose Garden Ln, Phoenix | AZ | 136806 | 134691 | 2115 | 1.57% | 105149 | 31657 | 30.11% |  |  |  | + | Sites live Jan 2025
99TH Ave & BELL | AZ | 24380 | 23446 | 934 | 3.984% | 23804 | 576 | 2.42% |  |  |  | + | Sites live Jan 2025
Rincon | AZ | 8822 | 7591 | 1231 | 16.22% | 8452 | 370 | 4.378% |  |  |  | + | Used inverter data (meter data requires a data correction)
Tucson Main Parking Garage | AZ | 15951 | 15111 | 840 | 5.559% | 11034 | 4917 | 44.56% | 1. Production meter is reporting lower by approximately 7KW with B-phase current reading low compared to A&C. 2. Meter A and C phase are underreporting. Meter A and B power factor are less than 1. | 1. SR098897 2. SR104705

## Aug
| Wells Fargo |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
| Total |  | 1866755.202 | 1805891 | 60864.202 | 3.37% | 1982577.997 | -115822.795 | -5.842% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
| Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
1 | Adams & Broadway | CA | 1193.3 | N/A |  |  | 1312 | -118.7 | -9.047%
2 | Otay Mesa | CA | 39.102 | N/A |  |  | N/A |  |  | 1. Production data taken from consumption meter.
3 | San Leandro | CA | 0 | N/A |  |  | 0 | 0 |  | 1. Site was not communicated for whole month. | 1.SR099548
4 | Van Nuys | CA | 1834.8 | N/A |  |  | 2594.997 | -760.197 | -29.29% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
5 | Lodi - Lodi Vineyard | CA | 43768 | 50160 | -6392 | -12.74% | 42061 | 1707 | 4.058% | 1. Inverter 1 and 7 have morning to afternoon shading
6 | Arden Fair Mall | CA | 23270 | 24626 | -1356 | -5.506% | 27363 | -4093 | -14.96% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
7 | Modesto - Modesto Main | CA | 16281 | 18634 | -2353 | -12.63% | 24713 | -8432 | -34.12% | 1. Inverters 1, 4, and 5 have some afternoon shading. Inverter 5 is underperforming by 3kW; likely soiling. | 1.SR101247 2.SR106393
8 | Stevens Creek | CA | 5848 | 6344 | -496 | -7.818% | 7034 | -1186 | -16.86% | 2.Site stopped communicating at 23:15 on 08/16 and later back online at 08/18 at 09:00
9 | Covina Main | CA | 3966 | 4035 | -69 | -1.71% | 3959 | 7 | 0.1768% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
10 | Old Ranch Town Center | CA | 1450 | N/A |  |  | 1682 | -232 | -13.79%
11 | Mountain Gate Plaza | CA | 9379 | N/A |  |  | 11380 | -2001 | -17.58% | The plant is performing as expected. The forecasted (theoretical) values may appear higher because they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance.
12 | Arcadia Main | CA | 4359 | N/A |  |  | 6193 | -1834 | -29.61% | The plant is performing as expected. I compared the results with last year’s forecasted data for July and August. July aligns well, but from August there is a deviation of -15%, which may be due to inaccuracies in the forecasted values, as these are theoretical
13 | Fairfield | CA | 4371 | 4243 | 128 | 3.017% | 4986 | -615 | -12.33% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
14 | Los Gatos | CA | 2393 | 2502 | -109 | -4.357% | 0 | 2393 |  | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
15 | San Marino | CA | 3888 | 5291 | -1403 | -26.52% | 6480 | -2592 | -40%
16 | Buenaventura | CA | 5384 | 3897 | 1487 | 38.16% | 6070 | -686 | -11.3% | 1. Inverter 1 is underperforming by 13kW and inverter 2 by 10kW. Pending quote for return visit.
17 | BE 199502 - Westgate | CA | 2103 | 0 | 2103 |  | 2520 | -417 | -16.55% | The plant is performing as expected. The forecasted (theoretical) values may appear higher because they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance.
18 | 98th & Grant | CO | 2313 | N/A |  |  | 2124 | 189 | 8.898%
19 | Arapahoe Crossings | CO | 3030 | N/A |  |  | 3982 | -952 | -23.91% | 1. No communication to the inverters, As per technician visit on 08/08 inverter 3 is offline and inverter 1 is underperforming. | 1.SR105604
20 | Aurora City Center | CO | 1840 | N/A |  |  | 1840 | 0 | 0% | 1. Site is back online at 10:00 on 08/04 | 1.SR103075
21 | Dry Creek | CO | 2456 | 0 | 2456 |  | 2319 | 137 | 5.908%
22 | Highlands Ranch S. | CO | 2055 | N/A |  |  | 2235 | -180 | -8.054%
23 | Lone Tree | CO | - | N/A |  |  | 5091 |  |  | 1. Site stopped communicating at 7/30 at 10:45 to till date and production cannot be confirmed. | 1.SR105436
24 | Meridian | CO | - | N/A |  |  | 2948 |  |  | 1. Site stopped communicating at 7/30 at 10:45 to till date and production cannot be confirmed. | 1.SR105437
25 | Southglenn | CO | 3255 | N/A |  |  | 3016 | 239 | 7.924%
26 | Standley Lake | CO | 4330 | N/A |  |  | 4022 | 308 | 7.658% | 1.Meter C phase current dropped 20 amps from 7/13/25.
27 | Havana Gardens | CO | 3739 | N/A |  |  | 1565 | 2174 | 138.9% | The plant is performing as expected. The forecasted (theoretical) values may appear lower and they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance.
28 | East Hartford | CT | 878 | 953 | -75 | -7.87% | 957 | -79 | -8.255%
29 | Norwalk | CT | 985 | 0 | 985 |  | 1224 | -239 | -19.53% | 1. Weather station reporting erroneous values from 07/04/2024. Will investigate next time onsite 2. An intermittent issue with Meter Phase C/Power Factor is slightly affecting the reported energy production. A case has been created with AlsoEnergy, and they have confirmed a site visit for further investigation | 1.SR088667 2.SR077700
30 | Hialeah Gardens | FL | 754 | 4769 | -4015 | -84.19% | 5217 | -4463 | -85.55% | 1. Site underperforming by ~15 kW. Production appears capped at 1.6 kW on high irradiance days, with brief spikes. Will be investigating during next site visit. 2. Site de-energized 08/15/25; site needs to be re-engineered. | 1.SR098782, SR098791
31 | W. Des Moines Campus EAST | IA | 201998 | 197228 | 4770 | 2.419% | 197900 | 4098 | 2.071%
32 | W. Des Moines Campus SW | IA | 73065 | 98477 | -25412 | -25.81% | 97149 | -24084 | -24.79% | 1.Inverter 1 underperforming by 8kW (2 string) from 7/28/25. Inverter 3 down 1 string from 8/7 (8kW) 2. Inverter 2 tripped offline at 08:45CDT on 07/20 | 1.SR105483 2.SR105331
33 | WF - CIC | NC | 3966 | 4035 | -69 | -1.71% | 3959 | 7 | 0.1768%
34 | Charlotte - Wells Fargo - DUC | NC | 1146 | 1030 | 116 | 11.26% | 1251 | -105 | -8.393%
35 | East Windsor | NJ | 1146 | 1030 | 116 | 11.26% | 1251 | -105 | -8.393%
36 | Burlington | NJ | 2802 | 2609 | 193 | 7.397% | 3195 | -393 | -12.3% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
37 | Bayonne | NJ | 3829 | 3523 | 306 | 8.686% | 3654 | 175 | 4.789%
38 | Clifton | NJ | 4745 | 4825 | -80 | -1.658% | 4539 | 206 | 4.538%
39 | North Elizabeth | NJ | 4012 | 3426 | 586 | 17.1% | 4162 | -150 | -3.604% | 1. Weather station was not communicated on 08/03 from 11:45 to 13:45.
40 | Haddon Westmont Plaza | NJ | 2740 | 2637 | 103 | 3.906% | 2999 | -259 | -8.636%
41 | Parsippany | NJ | 3499 | 3268 | 231 | 7.069% | 3475 | 24 | 0.6906%
42 | Clark | NJ | 2889 | 2722 | 167 | 6.135% | 2899 | -10 | -0.3449%
43 | Closter | NJ | 1294 | 1159 | 135 | 11.65% | 1818 | -524 | -28.82% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
44 | Holmdel | NJ | 2427 | 4053 | -1626 | -40.12% | 2524 | -97 | -3.843% | 1. Weather station constantly reporting a fixed value of 1237.22 W/m2 since 01/09. Will investigate next time onsite | 1.SR100979
45 | Ellisburg Circle Center | NJ | 1251 | 1176 | 75 | 6.378% | 1368 | -117 | -8.553%
46 | Nutley | NJ | 5101 | 3902 | 1199 | 30.73% | 5068 | 33 | 0.6511%
47 | Marlton | NJ | 4394 | 3869 | 525 | 13.57% | 4750 | -356 | -7.495%
48 | Middletown | NJ | 3559 | 2248 | 1311 | 58.32% | 3949 | -390 | -9.876% | 1.Weather station is frequently reporting erroneous values ( 0 w/m^2). Has been happening intermittently since 4/14 | 1.SR100592
49 | Whiting Crestwood | NJ | 4490 | 4379 | 111 | 2.535% | 5491 | -1001 | -18.23% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
50 | Barnegat | NJ | 6198 | 5506 | 692 | 12.57% | 6840 | -642 | -9.386%
51 | Manchester | NJ | 2624 | 2886 | -262 | -9.078% | 4703 | -2079 | -44.21% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
52 | West Deptford - Woodbury | NJ | 3862 | 3937 | -75 | -1.905% | 4101 | -239 | -5.828%
53 | Edison | NJ | 3610 | 3454 | 156 | 4.517% | 3818 | -208 | -5.448%
54 | Flemington | NJ | 3430 | 3216 | 214 | 6.654% | 3911 | -481 | -12.3% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
55 | Route 22 | NJ | 3469 | 3507 | -38 | -1.084% | 3644 | -175 | -4.802%
56 | Laurelton | NJ | 2015 | 3005 | -990 | -32.95% | 3309 | -1294 | -39.11% | 1.Production meter phase A volts are offline | 1.SR075812
57 | Mahwah | NJ | 2761 | 734 | 2027 | 276.2% | 3131 | -370 | -11.82% | 1. Weather station is frequently reporting erroneous values ( 0 w/m^2) during mid days.We have reached out to AlsoEnergy for remote assistance and waiting for their response | 1.SR100593
58 | Franklin Township WF | NJ | 3051 | 2966 | 85 | 2.866% | 3195 | -144 | -4.507%
59 | Bordentown | NJ | 2360 | 2103 | 257 | 12.22% | 2528 | -168 | -6.646%
60 | South Plainfield | NJ | 1766 | 1696 | 70 | 4.127% | 1790 | -24 | -1.341%
61 | Somerset | NJ | 2822 | 2731 | 91 | 3.332% | 2990 | -168 | -5.619%
62 | Clinton Main Relo | NJ | 3298 | 3329 | -31 | -0.9312% | 3450 | -152 | -4.406%
63 | North Brunswick | NJ | 3223 | 2922 | 301 | 10.3% | 3856 | -633 | -16.42% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
64 | Cherry Hill | NJ | 2229 | 2186 | 43 | 1.967% | 2434 | -205 | -8.422%
65 | Hainesport | NJ | 2306 | 2570 | -264 | -10.27% | 2471 | -165 | -6.677% | The site is producing as expected. When compared with the same month in previous years, there is always a deviation of 10%, which may be related to minor seasonal shading effects.
66 | San Antonio - Ops Ctr (Bldg 106) | TX | 57417 | 53442 | 3975 | 7.438% | 64182 | -6765 | -10.54% | 1.Inverter 4 is derating at 40 kW through out the month | 1.SR106961
67 | San Antonio - Ops Ctr GM | TX | 415928 | 452363 | -36435 | -8.054% | 460683 | -44755 | -9.715%
68 | San Antonio - Ctr (Bldg 201) | TX | 59555 | 53047 | 6508 | 12.27% | 64017 | -4462 | -6.97% | The virtual weather station has experienced intermittent communication issues, in contrast to the actual weather station at Building 203, San Antonio Ops Center (S64346), which is reporting without any issues. A case (#595841) has been opened with AlsoEnergy to reconfigure the virtual weather station accordingly.
69 | San Antonio - Ops Ctr (Bldg 203) | TX | 57716 | 54820 | 2896 | 5.283% | 64293 | -6577 | -10.23% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
70 | San Antonio - Ops Ctr (Bldg 205) | TX | 52705 | 48341 | 4364 | 9.028% | 60793 | -8088 | -13.3% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
71 | San Antonio - Ops Ctr (Bldg 307) | TX | 57100 | 52570 | 4530 | 8.617% | 61953 | -4853 | -7.833%
72 | San Antonio - Ctr (Bldg 308) | TX | 54252 | 51367 | 2885 | 5.616% | 59510 | -5258 | -8.835%
73 | San Antonio - Ops Ctr (Bldg 104) | TX | 15976 | 16098 | -122 | -0.7579% | 18629 | -2653 | -14.24% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
74 | San Antonio - Ops Ctr (Bldg 102) | TX | 61403 | 51225 | 10178 | 19.87% | 66658 | -5255 | -7.884% | 1. San Antonio 102 is a virtual weather station. On 08/23, San Antonio 203 lost communication, which caused San Antonio 102 to stop receiving data from 07:00 to 16:45 | 1. SR106784
75 | N Black Canyon Hwy, Phoenix - North | AZ | 97248 | 79216 | 18032 | 22.76% | 95432 | 1816 | 1.903%
76 | N Black Canyon Hwy, Phoenix - South | AZ | 103082 | 86572 | 16510 | 19.07% | 105078 | -1996 | -1.9% | 1.Inverter 16 is derating at 33kW in the afternoon starting on 07/18. | 1.SR104656
77 | Building 2222, Rose Garden Ln, Phoenix | AZ | 128294 | 124184 | 4110 | 3.31% | 130682 | -2388 | -1.827%
78 | Building 2202, Rose Garden Ln, Phoenix | AZ | 127759 | 121462 | 6297 | 5.184% | 96396 | 31363 | 32.54%
79 | 99TH Ave & BELL | AZ | 22657 | 22131 | 526 | 2.377% | 22945 | -288 | -1.255%
80 | Rincon | AZ | 8356 | 7038 | 1318 | 18.73% | 8019 | 337 | 4.203%
81 | Tucson Main Parking Garage | AZ | 14768 | 14217 | 551 | 3.876% | 10848 | 3920 | 36.14% | 1.Meter A and C phase are underreporting. Meter A and B power factor are less than 1 and on 08/21 phase C currents are showing more amps additional troubleshoot required Actual energy is taken from total inverters data | 1.SR104705
Actual vs weather adjusted (August 2025)
| Negative | 23 | 28.4%
| No Change | 18 | 22.22%
| Positive | 40 | 49.38%
Actual vs forecasted (August 2025)
| Negative | 58 | 71.6%
| No Change | 8 | 9.88%
| Positive | 15 | 18.52%

## Sep
Wells Fargo |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 1889037.807 | 1889128 | -90.193 | -0.004774% | 2034397.438 | -145359.631 | -7.145%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 939.9 | N/A |  |  | 1067 | -127.1 | -11.91% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Otay Mesa | CA | 37.907 | N/A |  |  | N/A |  |  | 1. Production data taken from consumption meter.
San Leandro | CA | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was not communicated for whole month. | 1.SR099548
Van Nuys | CA | 1504 | N/A |  |  | 2136.438 | -632.438 | -29.6% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Lodi - Lodi Vineyard | CA | 31166 | 38966 | -7800 | -20.02% | 36116 | -4950 | -13.71% | 1. Inverter 1 and 7 have morning to afternoon shading.
Arden Fair Mall | CA | 15989 | 18017 | -2028 | -11.26% | 22974 | -6985 | -30.4% | 1. Site production was low on 09/19, 09/28 and 09/29 due to cloudy weather.
Modesto - Modesto Main | CA | 11449 | 15592 | -4143 | -26.57% | 21109 | -9660 | -45.76% | 1. Inverters 1, 4, and 5 have some afternoon shading. Inverter 5 is underperforming by 3kW; likely soiling. | 1. SR101247
Stevens Creek | CA | 4597 | 4563 | 34 | 0.7451% | 5507 | -910 | -16.52% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Covina Main | CA | 3233 | 3058 | 175 | 5.723% | 3348 | -115 | -3.435%
Old Ranch Town Center | CA | 1228 | N/A |  |  | 1389 | -161 | -11.59% | 1. The plant is performing as expected. The forecasted (theoretical) values may appear higher because they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance.
Mountain Gate Plaza | CA | 7460 | N/A |  |  | 9596 | -2136 | -22.26% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Arcadia Main | CA | 3412 | N/A |  |  | 5139 | -1727 | -33.61% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Fairfield | CA | 3281 | 3374 | -93 | -2.756% | 4277 | -996 | -23.29% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Los Gatos | CA | 1769 | 1843 | -74 | -4.015% | 0 | 1769
San Marino | CA | 3093 | 3886 | -793 | -20.41% | 5185 | -2092 | -40.35% | 1. Inverter 1 is underperforming by 13kW and inverter 2 by 10kW. Pending quote for return visit. | 1.SR104629
Buenaventura | CA | 4318 | 3135 | 1183 | 37.74% | 5391 | -1073 | -19.9% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
BE 199502 - Westgate | CA | 1697 | 0 | 1697 |  | 2114 | -417 | -19.73% | 1. The plant is performing as expected. The forecasted (theoretical) values may appear higher because they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance.
98th & Grant | CO | 1974 | N/A |  |  | 1914 | 60 | 3.135%
Arapahoe Crossings | CO | 2475 | N/A |  |  | 3508 | -1033 | -29.45% | 1. No communication to the inverters, As per technician visit on 08/08 inverter 3 is offline and inverter 1 is underperforming. | 1.SR105604
Aurora City Center | CO | 1662 | N/A |  |  | 1642 | 20 | 1.218%
Dry Creek | CO | 2167 | 0 | 2167 |  | 2079 | 88 | 4.233%
Highlands Ranch S. | CO | 1814 | N/A |  |  | 1934 | -120 | -6.205%
Lone Tree | CO | 5748 | N/A |  |  | 4395 | 1353 | 30.78% | 1. Site regained its communication at 10:15 on 09/18. | 1.SR105436
Meridian | CO | 6254 | N/A |  |  | 2534 | 3720 | 146.8% | 1. Site regained its communication at 15:30 on 09/10. | 1. SR105437
Southglenn | CO | 2921 | N/A |  |  | 2652 | 269 | 10.14%
Standley Lake | CO | 3822 | N/A |  |  | 3536 | 286 | 8.088%
Havana Gardens | CO | 3218 | N/A |  |  | 1378 | 1840 | 133.5% | 1. The plant is performing as expected. The forecasted (theoretical) values may appear lower and they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance.
East Hartford | CT | 697 | 772 | -75 | -9.715% | 782 | -85 | -10.87% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Norwalk | CT | 624 | 0 | 624 |  | 929 | -305 | -32.83% | 1. Weather station reporting erroneous values from 07/04/2024. Will investigate next time onsite 2. An intermittent issue with Meter Phase C/Power Factor is slightly affecting the reported energy production. A case has been created with AlsoEnergy, and they have confirmed a site visit for further investigation | 1.SR107668 2.SR077700
Hialeah Gardens | FL | 623 | 3889 | -3266 | -83.98% | 4497 | -3874 | -86.15% | 1. Site underperforming by ~15 kW. Production appears capped at 1.6 kW on high irradiance days, with brief spikes. Will be investigating during next site visit. | 1.SR098782
W. Des Moines Campus EAST | IA | 170618 | 169170 | 1448 | 0.8559% | 182300 | -11682 | -6.408%
W. Des Moines Campus SW | IA | 60855 | 87807 | -26952 | -30.69% | 89547 | -28692 | -32.04% | 1.Inverter 1 underperforming by 8kW (2 string) from 7/28/25. Inverter 3 down 1 string from 8/7 (8kW) 2. Inverter 2 tripped offline at 08:45CDT on 07/20 and remained offline throughout the month | 1.SR105483 2.SR105331
WF - CIC | NC | 156184 | 165962 | -9778 | -5.892% | 165450 | -9266 | -5.6%
Charlotte - Wells Fargo - DUC | NC | 167619 | 186923 | -19304 | -10.33% | 156833 | 10786 | 6.877% | 1. Site production was low on 09/25 to 09/29 due to cloudy weather and rain.
East Windsor | NJ | 928 | 876 | 52 | 5.936% | 920 | 8 | 0.8696%
Burlington | NJ | 2311 | 2104 | 207 | 9.838% | 2390 | -79 | -3.305% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Bayonne | NJ | 3131 | 2949 | 182 | 6.172% | 3027 | 104 | 3.436%
Clifton | NJ | 3730 | 3756 | -26 | -0.6922% | 3932 | -202 | -5.137%
North Elizabeth | NJ | 3193 | 2532 | 661 | 26.11% | 3185 | 8 | 0.2512% | 1. Site stopped comms at 12:35 on 09/07 and restored at 14:30 on 09/07, energy backfilled.
Haddon Westmont Plaza | NJ | 2165 | 2029 | 136 | 6.703% | 2253 | -88 | -3.906%
Parsippany | NJ | 2752 | 2581 | 171 | 6.625% | 2840 | -88 | -3.099%
Clark | NJ | 2284 | 2097 | 187 | 8.918% | 2220 | 64 | 2.883%
Closter | NJ | 780 | 844 | -64 | -7.583% | 1434 | -654 | -45.61% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Holmdel | NJ | 1976 | 2725 | -749 | -27.49% | 1943 | 33 | 1.698% | 1. The weather station has been constantly reporting a fixed value of 1237.22 W/m² since 01/09. POA*, the POA sensor, and GHI have all been reporting 0 W/m² since 08/28. This will be investigated during the next site visit. | 1. SR100979
Ellisburg Circle Center | NJ | 980 | 938 | 42 | 4.478% | 1040 | -60 | -5.769%
Nutley | NJ | 4057 | 3011 | 1046 | 34.74% | 4022 | 35 | 0.8702%
Marlton | NJ | 3552 | 3014 | 538 | 17.85% | 3601 | -49 | -1.361%
Middletown | NJ | 3035 | 1818 | 1217 | 66.94% | 3131 | -96 | -3.066% | 1.Weather station is frequently reporting erroneous values ( 0 w/m^2). Has been happening intermittently since 4/14 | 1. SR100592
Whiting Crestwood | NJ | 3878 | 3792 | 86 | 2.268% | 4176 | -298 | -7.136% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Barnegat | NJ | 4856 | 4262 | 594 | 13.94% | 5003 | -147 | -2.938%
Manchester | NJ | 2265 | 2469 | -204 | -8.262% | 3603 | -1338 | -37.14% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
West Deptford - Woodbury | NJ | 3322 | 3304 | 18 | 0.5448% | 3347 | -25 | -0.7469%
Edison | NJ | 3046 | 2715 | 331 | 12.19% | 3072 | -26 | -0.8464%
Flemington | NJ | 2772 | 2406 | 366 | 15.21% | 2945 | -173 | -5.874%
Route 22 | NJ | 2806 | 2761 | 45 | 1.63% | 2807 | -1 | -0.03563%
Laurelton | NJ | 1558 | 2261 | -703 | -31.09% | 2464 | -906 | -36.77% | 1.Production meter phase A volts are offline. | 1. SR075812
Mahwah | NJ | 2139 | 577 | 1562 | 270.7% | 2397 | -258 | -10.76% | 1. Weather station is frequently reporting erroneous values ( 0 w/m^2) during mid days.We have reached out to AlsoEnergy for remote assistance and waiting for their response | 1. SR100593
Franklin Township WF | NJ | 2562 | 2359 | 203 | 8.605% | 2801 | -239 | -8.533%
Bordentown | NJ | 2039 | 1704 | 335 | 19.66% | 2039 | 0 | 0%
South Plainfield | NJ | 1479 | 1349 | 130 | 9.637% | 1465 | 14 | 0.9556%
Somerset | NJ | 2314 | 2307 | 7 | 0.3034% | 2375 | -61 | -2.568%
Clinton Main Relo | NJ | 2657 | 2686 | -29 | -1.08% | 2729 | -72 | -2.638%
North Brunswick | NJ | 2626 | 2328 | 298 | 12.8% | 2989 | -363 | -12.14% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Cherry Hill | NJ | 1776 | 1742 | 34 | 1.952% | 1870 | -94 | -5.027%
Hainesport | NJ | 1880 | 2103 | -223 | -10.6% | 1904 | -24 | -1.261% | 1. The site is producing as expected. When compared with the same month in previous years, there is always a deviation of 10%, which may be related to minor seasonal shading effects.
San Antonio - Ops Ctr (Bldg 106) | TX | 50709 | 47603 | 3106 | 6.525% | 56068 | -5359 | -9.558% | 1.Inverter 4 has been derating at 40 kW since 04/13 and was reporting 'External Fan Err - ExtFanerr'. After installing a new fan on 09/25, Inverter 4 is now producing as expected. | 1. SR106961
San Antonio - Ops Ctr GM | TX | 358065 | 403955 | -45890 | -11.36% | 376464 | -18399 | -4.887% | 1. Site was offline at 07:00 on 09/13 and back online at 00:30 on 09/14. 2. Inverter 4 was offline at 07:00 on 09/18 and reporting Loss of Main - GridV.OutLim. | 1. SR107931 2. SR108243
San Antonio - Ctr (Bldg 201) | TX | 50635 | 47255 | 3380 | 7.153% | 55560 | -4925 | -8.864% | 1. Site was offline at 04:30 on 09/13 and back online at 20:15 on 09/13. | 1. SR107930
San Antonio - Ops Ctr (Bldg 203) | TX | 51537 | 48846 | 2691 | 5.509% | 56467 | -4930 | -8.731% | 1. Site was offline at 06:30 on 09/13 and back online at 20:15 on 09/13. | 1. SR107932
San Antonio - Ops Ctr (Bldg 205) | TX | 47692 | 43060 | 4632 | 10.76% | 53097 | -5405 | -10.18% | 1. Inverter 4 is down a string since 02/16/25 this issue will be investigate during PM event. | 1. SR097581
San Antonio - Ops Ctr (Bldg 307) | TX | 50239 | 46830 | 3409 | 7.28% | 54282 | -4043 | -7.448%
San Antonio - Ctr (Bldg 308) | TX | 48671 | 45757 | 2914 | 6.368% | 52330 | -3659 | -6.992% | 1. Inverter 4 underperformed by 6kW since 08/17 may be due to one string down and this issue is occur through out the month. | 1. SR106526
San Antonio - Ops Ctr (Bldg 104) | TX | 13988 | 14341 | -353 | -2.461% | 16267 | -2279 | -14.01% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
San Antonio - Ops Ctr (Bldg 102) | TX | 55066 | 44612 | 10454 | 23.43% | 58712 | -3646 | -6.21%
N Black Canyon Hwy, Phoenix - North | AZ | 81181 | 67123 | 14058 | 20.94% | 87653 | -6472 | -7.384%
N Black Canyon Hwy, Phoenix - South | AZ | 78052 | 73387 | 4665 | 6.357% | 96512 | -18460 | -19.13% | 1. Inverter 16 is derating at 33kW in the afternoon starting since 07/18 . 2. Inverter 11 tripped offline at 16:45 on 09/04 and reporting ""Insulation Resistance Low - IsolationErr"" and tripping on and off through out the month. | 1. SR104656, SR107171 2. SR107486
Building 2222, Rose Garden Ln, Phoenix | AZ | 101251 | 98655 | 2596 | 2.631% | 114270 | -13019 | -11.39% | 1. Site production was low on 09/26 due to cloudy weather.
Building 2202, Rose Garden Ln, Phoenix | AZ | 100873 | 92623 | 8250 | 8.907% | 83211 | 17662 | 21.23%
99TH Ave & BELL | AZ | 18191 | 17783 | 408 | 2.294% | 20866 | -2675 | -12.82% | 1.As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Rincon | AZ | 7294 | 5799 | 1495 | 25.78% | 7064 | 230 | 3.256%
Tucson Main Parking Garage | AZ | 12296 | 12143 | 153 | 1.26% | 10392 | 1904 | 18.32% | 1.Meter A and C phase are underreporting. Meter A and B power factor are less than 1 and on 08/21 phase C currents are showing more amps additional troubleshoot required Actual energy is taken from total inverters data | 1. SR104705

## Oct
Wells Fargo |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 1686631.3827 | 1733245.5568 | -46614.1741 | -2.689% | 1816089.0211 | -129457.6384 | -7.128% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Adams & Broadway | CA | 949.8 | 2452.448 | -1502.648 |  | 864 | 85.8 | 9.931% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Otay Mesa | CA | 39.297 | N/A |  |  | N/A |  |  | 1. Production data taken from consumption meter.
San Leandro | CA | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was not communicated for whole month. | 1.SR099548 | 1. Closed
Van Nuys | CA | 1552.1 | N/A |  |  | 1737.42 | -185.32 | -10.67% | 1. Inverter 1 has heavy shading from afternoon to evening.
Lodi - Lodi Vineyard | CA | 28980.5625 | 31654.06 | -2673.4975 | -8.446% | 30761 | -1780.4375 | -5.788% | 1. Inverter 1 and 7 have morning to afternoon shading.
Arden Fair Mall | CA | 13992 | 16086.09 | -2094.09 | -13.02% | 18570 | -4578 | -24.65% | 1. Inverter 2 has heavy shading in the morning.
Modesto - Modesto Main | CA | 10120.9062 | 13359 | -3238.0938 | -24.24% | 17922.64 | -7801.7337 | -43.53% | 1. Inverters 1, 4, and 5 have some afternoon shading. Inverter 5 is underperforming by 3kW; likely soiling. | 1. SR101247 | 1.Closed
Stevens Creek | CA | 4163.2125 | 3733.611 | 429.6015 | 11.51% | 4062 | 101.2125 | 2.492% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Covina Main | CA | 3249.6 | 2689.172 | 560.428 | 20.84% | 2815 | 434.6 | 15.44%
Old Ranch Town Center | CA | 1088.8587 | N/A |  |  | 1179 | -90.1413 | -7.646% | 1. The plant is performing as expected. The forecasted (theoretical) values may appear higher because they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance.
Mountain Gate Plaza | CA | 7579.9 | N/A |  |  | 8587 | -1007.1 | -11.73% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Arcadia Main | CA | 3521.9007 | N/A |  |  | 4489 | -967.0993 | -21.54% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Fairfield | CA | 2838.7173 | 2978.225 | -139.5077 | -4.684% | 3466 | -627.2827 | -18.1% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Los Gatos | CA | 1506.3343 | 1461.637 | 44.6973 | 3.058% | 0 | 1506.3343
San Marino | CA | 3181.8 | 3399.414 | -217.614 | -6.402% | 4094.273 | -912.473 | -22.29% | 1. Inverter 1 is underperforming by 13kW and inverter 2 by 10kW. Pending quote for return visit. | 1.SR104629 | 1. Closed 2. Closed
Buenaventura | CA | 4628.0156 | 3414.8 | 1213.2156 | 35.53% | 4846.482 | -218.4664 | -4.508% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
BE 199502 - Westgate | CA | 1492.9 | N/A |  |  | 1771.355 | -278.455 | -15.72% | 1. The plant is performing as expected. The forecasted (theoretical) values may appear higher because they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance.
98th & Grant | CO | 1830 | N/A |  |  | 1610 | 220 | 13.66%
Arapahoe Crossings | CO | 2227.0007 | N/A |  |  | 2969.073 | -742.0723 | -24.99% | 1. No communication to the inverters, As per technician visit on 08/08 inverter 3 is offline and inverter 1 is underperforming. | 1.SR105604 | 1.Closed
Aurora City Center | CO | 1357.6 | N/A |  |  | 1424 | -66.4 | -4.663%
Dry Creek | CO | 1477.1 | 0 | 1477.1 |  | 1742 | -264.9 | -15.21% | 1. Meter phase A and B currents dropped to 18Amps on 10/01 | 1. SR110707 | 1. New
Highlands Ranch S. | CO | 1617 | N/A |  |  | 1605 | 12 | 0.7477%
Lone Tree | CO | 2170.7 | N/A |  |  | 3663 | -1492.3 | -40.74% | 1. Inverter 2 was offline for the entire month and will be investigated in 2026 | 1. SR101743 | 1. Closed
Meridian | CO | 2554 | N/A |  |  | 2150 | 404 | 18.79%
Southglenn | CO | 2639.8 | N/A |  |  | 2239 | 400.8 | 17.9%
Standley Lake | CO | 3378.9 | N/A |  |  | 2986 | 392.9 | 13.16%
Havana Gardens | CO | 2846.8 | N/A |  |  | 1166 | 1680.8 | 144.2%
East Hartford | CT | 495.7 | 577 | -81.3 | -14.09% | 600.7968 | -105.0968 | -17.49% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Norwalk | CT | 231.7397 | 0 | 231.7397 |  | 714.3024 | -482.5627 | -67.56% | 1. Weather station reporting erroneous values from 07/04/2024. Will investigate next time onsite 2. An intermittent issue with Meter Phase C/Power Factor is slightly affecting the reported energy production. A case has been created with AlsoEnergy, and they have confirmed a site visit for further investigation | 1.SR107668 2.SR077700 | 1.Closed 2.Closed | SR077700
Hialeah Gardens | FL | 671.9964 | 4958.923 | -4286.9266 | -86.45% | 4137 | -3465.0036 | -83.76% | 1. Site underperforming by ~15 kW. Production appears capped at 1.6 kW on high irradiance days, with brief spikes. Will be investigating during next site visit. | 1.SR098782 | 1. Closed 2. Closed
W. Des Moines Campus EAST | IA | 143196 | 146853.3 | -3657.3 | -2.49% | 154900 | -11704 | -7.556% | 1.Inverter 4 is being RMA'd | 1.SR105331 | 1.Closed
W. Des Moines Campus SW | IA | 51760 | 79675.07 | -27915.07 | -35.04% | 76627.94 | -24867.94 | -32.45% | 1. Inverter 1 underperforming by 8kW (2 string) from 7/28/25. Inverter 3 down 1 string from 8/7 (8kW) 2. Inverter 2 tripped offline at 08:45CDT on 07/20 and remained offline throughout the month | 1.SR105483 2.SR105331 | 1.Closed 2.Closed | SR105331
WF - CIC | NC | 135077 | 141173.652 | -6096.652 | -4.319% | 158525.418 | -23448.418 | -14.79% | 1. Site was offline from 17:30 on 10/18 and again back online at 02:45 on 10/19 as Facility has performed PM on switchgear | 1.SR109637 | 1.Closed
Charlotte - Wells Fargo - DUC | NC | 135654 | 156156 | -20502 | -13.13% | 150295.5 | -14641.5 | -9.742% |  | 1.SR088678 | 1.Closed
East Windsor | NJ | 740 | 737.3135 | 2.6865 | 0.3644% | 765.6456 | -25.6456 | -3.35%
Burlington | NJ | 1979.3 | 1688.337 | 290.963 | 17.23% | 1938.693 | 40.607 | 2.095%
Bayonne | NJ | 2462.9 | 2356.127 | 106.773 | 4.532% | 2496.777 | -33.877 | -1.357%
Clifton | NJ | 3000.875 | 3035.552 | -34.677 | -1.142% | 3260.625 | -259.75 | -7.966%
North Elizabeth | NJ | 2351.5 | 1946.626 | 404.874 | 20.8% | 2666.961 | -315.461 | -11.83% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Haddon Westmont Plaza | NJ | 1776.4 | 1651.977 | 124.423 | 7.532% | 1860.688 | -84.288 | -4.53%
Parsippany | NJ | 2261.3 | 2185.155 | 76.145 | 3.485% | 2221.257 | 40.043 | 1.803%
Clark | NJ | 1812.9 | 1611.941 | 200.959 | 12.47% | 1809.492 | 3.408 | 0.1883%
Closter | NJ | 439.8 | 490.9498 | -51.1498 | -10.42% | 1044.885 | -605.085 | -57.91% | 1. Inverter has been replaced on 10/09. | 1.SR091644 | 1.Closed
Holmdel | NJ | 1031 | 1848.52 | -817.52 | -44.23% | 1532.415 | -501.415 | -32.72% | 1. Site stopped communicating from 10:15 from 10/20 till end of the month | 1.SR109804 | 1.Closed
Ellisburg Circle Center | NJ | 782 | 764.7535 | 17.2465 | 2.255% | 852.9793 | -70.9793 | -8.321%
Nutley | NJ | 3162.8 | 2329.205 | 833.595 | 35.79% | 3225.886 | -63.086 | -1.956%
Marlton | NJ | 2943 | 2213.65 | 729.35 | 32.95% | 3004.853 | -61.853 | -2.058%
Middletown | NJ | 2572.8 | 1594.817 | 977.983 | 61.32% | 2619.061 | -46.261 | -1.766% | 1. Weather station is frequently reporting erroneous values ( 0 w/m^2). Has been happening intermittently since 4/14 | 1. SR100592 | 1. Closed
Whiting Crestwood | NJ | 3453.8 | 3486.616 | -32.816 | -0.9412% | 3759.585 | -305.785 | -8.133% | 1. Compared to last year’s delta values, we can still see a negative variance for this site, which suggests an issue with the forecasted value.
Barnegat | NJ | 3903.6719 | 3198.427 | 705.2449 | 22.05% | 3887.128 | 16.5439 | 0.4256%
Manchester | NJ | 1920.1 | 2154.545 | -234.445 | -10.88% | 3351.467 | -1431.367 | -42.71% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
West Deptford - Woodbury | NJ | 3153.9 | 2900.748 | 253.152 | 8.727% | 3087.319 | 66.581 | 2.157%
Edison | NJ | 2658 | 2134.737 | 523.263 | 24.51% | 2702.634 | -44.634 | -1.651%
Flemington | NJ | 2276.6 | 1915.962 | 360.638 | 18.82% | 2436.862 | -160.262 | -6.577%
Route 22 | NJ | 2384.7 | 2208.465 | 176.235 | 7.98% | 2397.644 | -12.944 | -0.5399%
Laurelton | NJ | N/A | N/A |  |  | N/A |  |  | 1. The Laurelton Site has been closed down and sold as of 7/31/25 | 1. SR108795 | 1. Closed
Mahwah | NJ | 1704.8 | 176.602 | 1528.198 | 865.3% | 1906.129 | -201.329 | -10.56% | 1. Weather station is frequently reporting erroneous values ( 0 w/m^2) during mid days.We have reached out to AlsoEnergy for remote assistance and waiting for their response | 1. SR100593 | 1. Closed
Franklin Township WF | NJ | 2018.8 | 1799.627 | 219.173 | 12.18% | 2186.652 | -167.852 | -7.676%
Bordentown | NJ | 1799.6 | 1390.057 | 409.543 | 29.46% | 1804.926 | -5.326 | -0.2951%
South Plainfield | NJ | 1253.7 | 1034.241 | 219.459 | 21.22% | 1240.202 | 13.498 | 1.088%
Somerset | NJ | 1867.9 | 1916.47 | -48.57 | -2.534% | 1996.133 | -128.233 | -6.424%
Clinton Main Relo | NJ | 2171.5859 | 2261.329 | -89.7431 | -3.969% | 2200.638 | -29.0521 | -1.32%
North Brunswick | NJ | 2062 | 1803.528 | 258.472 | 14.33% | 2460.074 | -398.074 | -16.18% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Cherry Hill | NJ | 1527.1641 | 1575.692 | -48.5279 | -3.08% | 1587.492 | -60.3279 | -3.8%
Hainesport | NJ | 1696.8 | 1745.18 | -48.38 | -2.772% | 1693.048 | 3.752 | 0.2216%
San Antonio - Ops Ctr (Bldg 106) | TX | 46185.9044 | 45158.36 | 1027.5444 | 2.275% | 48748.86 | -2562.9556 | -5.257% | 1. Site was offline at 10:21 on 10/15 and back online at 13:21 on 10/15. | 1. SR109508 | 1. Closed
San Antonio - Ops Ctr GM | TX | 346847.25 | 413522.1 | -66674.85 | -16.12% | 368570 | -21722.75 | -5.894% | 1. Inverter 4 was offline at 07:00 on 09/18 and reporting Loss of Main GridV.OutLim | 1. SR108243 | 1. Closed
San Antonio - Ctr (Bldg 201) | TX | 47705.75 | 44828.56 | 2877.19 | 6.418% | 48754.78 | -1049.03 | -2.152%
San Antonio - Ops Ctr (Bldg 203) | TX | 48653.625 | 46344.69 | 2308.935 | 4.982% | 50121.03 | -1467.405 | -2.928%
San Antonio - Ops Ctr (Bldg 205) | TX | 43763.4375 | 40848.73 | 2914.7075 | 7.135% | 46312.85 | -2549.4125 | -5.505% | 1. Inverter 4 is down a string since 02/16/25 this issue will be investigate during PM event. | 1. SR097581 | 1. Closed
San Antonio - Ops Ctr (Bldg 307) | TX | 46724.9788 | 44425.37 | 2299.6087 | 5.176% | 47644.63 | -919.6512 | -1.93%
San Antonio - Ctr (Bldg 308) | TX | 46002 | 43407.57 | 2594.43 | 5.977% | 46317.78 | -315.78 | -0.6818% | 1. Inverter 4 underperformed by 6kW since 08/17 may be due to one string down and this issue is occur through out the month and issue schedule with PM. | 1. SR106526 | 1. Closed
San Antonio - Ops Ctr (Bldg 104) | TX | 12675.1094 | 13604.88 | -929.7706 | -6.834% | 14177.75 | -1502.6406 | -10.6% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
San Antonio - Ops Ctr (Bldg 102) | TX | 51037.9875 | 41188.41 | 9849.5775 | 23.91% | 51758.89 | -720.9025 | -1.393%
N Black Canyon Hwy, Phoenix - North | AZ | 74729.875 | 65802.38 | 8927.495 | 13.57% | 74636 | 93.875 | 0.1258%
N Black Canyon Hwy, Phoenix - South | AZ | 70678.625 | 71957.95 | -1279.325 | -1.778% | 82568 | -11889.375 | -14.4% | 1. Inverter 16 is derating at 33kW in the afternoon starting since 07/18 . 2. Inverter 11 tripped offline at 16:45 on 09/04 and reporting ""Insulation Resistance Low - IsolationErr"" and tripping on and off through out the month. | 1. SR104656, SR107171 2. SR107486 | 1. Closed 2. Closed | SR107171 | SR107486
Building 2222, Rose Garden Ln, Phoenix | AZ | 88407.75 | 86976.69 | 1431.06 | 1.645% | 90982 | -2574.25 | -2.829%
Building 2202, Rose Garden Ln, Phoenix | AZ | 88457 | 77264.71 | 11192.29 | 14.49% | 71027.1 | 17429.9 | 24.54%
99TH Ave & BELL | AZ | 15531.6985 | 14976.55 | 555.1485 | 3.707% | 17695 | -2163.3015 | -12.23% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Rincon | AZ | 6804.4531 | 5092.435 | 1712.0181 | 33.62% | 6194 | 610.4531 | 9.856% | 1. Weather station has morning shading.
Tucson Main Parking Garage | AZ | 11185 | 11066.62 | 118.38 | 1.07% | 10062 | 1123 | 11.16% | 1. Meter A and C phase are underreporting. Meter A and B power factor are less than 1 and on 08/21 phase C currents are showing more amps additional troubleshoot required Actual energy is taken from total inverters data | 1. SR104705 | 1. Closed

## Nov
Wells Fargo |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA
Otay Mesa | CA | [5 empty] | 0
San Leandro | CA
Van Nuys | CA
Lodi - Lodi Vineyard | CA
Arden Fair Mall | CA
Modesto - Modesto Main | CA
Stevens Creek | CA
Covina Main | CA
Old Ranch Town Center | CA
Mountain Gate Plaza | CA
Arcadia Main | CA
Fairfield | CA
Los Gatos | CA
San Marino | CA
Buenaventura | CA
BE 199502 - Westgate | CA
98th & Grant | CO
Arapahoe Crossings | CO
Aurora City Center | CO
Dry Creek | CO
Highlands Ranch S. | CO
Lone Tree | CO
Meridian | CO
Southglenn | CO
Standley Lake | CO
Havana Gardens | CO
East Hartford | CT
Norwalk | CT
Hialeah Gardens | FL
W. Des Moines Campus EAST | IA
W. Des Moines Campus SW | IA
WF - CIC | NC
Charlotte - Wells Fargo - DUC | NC
East Windsor | NJ
Burlington | NJ
Bayonne | NJ
Clifton | NJ
North Elizabeth | NJ
Haddon Westmont Plaza | NJ
Parsippany | NJ
Clark | NJ
Closter | NJ
Holmdel | NJ
Ellisburg Circle Center | NJ
Nutley | NJ
Marlton | NJ
Middletown | NJ
Whiting Crestwood | NJ
Barnegat | NJ
Manchester | NJ
West Deptford - Woodbury | NJ
Edison | NJ
Flemington | NJ
Route 22 | NJ
Laurelton | NJ
Mahwah | NJ
Franklin Township WF | NJ
Bordentown | NJ
South Plainfield | NJ
Somerset | NJ
Clinton Main Relo | NJ
North Brunswick | NJ
Cherry Hill | NJ
Hainesport | NJ
San Antonio - Ops Ctr (Bldg 106) | TX
San Antonio - Ops Ctr GM | TX
San Antonio - Ctr (Bldg 201) | TX
San Antonio - Ops Ctr (Bldg 203) | TX
San Antonio - Ops Ctr (Bldg 205) | TX
San Antonio - Ops Ctr (Bldg 307) | TX
San Antonio - Ctr (Bldg 308) | TX
San Antonio - Ops Ctr (Bldg 104) | TX
San Antonio - Ops Ctr (Bldg 102) | TX
N Black Canyon Hwy, Phoenix - North | AZ
N Black Canyon Hwy, Phoenix - South | AZ
Building 2222, Rose Garden Ln, Phoenix | AZ
Building 2202, Rose Garden Ln, Phoenix | AZ
99TH Ave & BELL | AZ
Rincon | AZ
Tucson Main Parking Garage | AZ

## Dec
Wells Fargo |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA
Otay Mesa | CA
San Leandro | CA
Van Nuys | CA
Lodi - Lodi Vineyard | CA
Arden Fair Mall | CA
Modesto - Modesto Main | CA
Stevens Creek | CA
Covina Main | CA
Old Ranch Town Center | CA
Mountain Gate Plaza | CA
Arcadia Main | CA
Fairfield | CA
Los Gatos | CA
San Marino | CA
Buenaventura | CA
BE 199502 - Westgate | CA
98th & Grant | CO
Arapahoe Crossings | CO
Aurora City Center | CO
Dry Creek | CO
Highlands Ranch S. | CO
Lone Tree | CO
Meridian | CO
Southglenn | CO
Standley Lake | CO
Havana Gardens | CO
East Hartford | CT
Norwalk | CT
Hialeah Gardens | FL
W. Des Moines Campus EAST | IA
W. Des Moines Campus SW | IA
WF - CIC | NC
Charlotte - Wells Fargo - DUC | NC
East Windsor | NJ
Burlington | NJ
Bayonne | NJ
Clifton | NJ
North Elizabeth | NJ
Haddon Westmont Plaza | NJ
Parsippany | NJ
Clark | NJ
Closter | NJ
Holmdel | NJ
Ellisburg Circle Center | NJ
Nutley | NJ
Marlton | NJ
Middletown | NJ
Whiting Crestwood | NJ
Barnegat | NJ
Manchester | NJ
West Deptford - Woodbury | NJ
Edison | NJ
Flemington | NJ
Route 22 | NJ
Laurelton | NJ
Mahwah | NJ
Franklin Township WF | NJ
Bordentown | NJ
South Plainfield | NJ
Somerset | NJ
Clinton Main Relo | NJ
North Brunswick | NJ
Cherry Hill | NJ
Hainesport | NJ
San Antonio - Ops Ctr (Bldg 106) | TX
San Antonio - Ops Ctr GM | TX
San Antonio - Ctr (Bldg 201) | TX
San Antonio - Ops Ctr (Bldg 203) | TX
San Antonio - Ops Ctr (Bldg 205) | TX
San Antonio - Ops Ctr (Bldg 307) | TX
San Antonio - Ctr (Bldg 308) | TX
San Antonio - Ops Ctr (Bldg 104) | TX
San Antonio - Ops Ctr (Bldg 102) | TX
N Black Canyon Hwy, Phoenix - North | AZ
N Black Canyon Hwy, Phoenix - South | AZ
Building 2222, Rose Garden Ln, Phoenix | AZ
Building 2202, Rose Garden Ln, Phoenix | AZ
99TH Ave & BELL | AZ
Rincon | AZ
Tucson Main Parking Garage | AZ

## Sites
Portfolio: | Wells Fargo
Site DAS Name | Site | State | Update | DAS | BE | Admin/Retail | July 2025 Facility Partner
BE 191334 - Adams & Broadway | Adams & Broadway | CA | AEF | PowerTrack | 191334 | Retail | CBRE
BE 196270 - Otay Mesa (ATM) | Otay Mesa | CA |  | PowerTrack | 196270 | Retail | CBRE
BE 144682 - San Leandro Ops Center | San Leandro | CA | AEF | PowerTrack | 144682 | Admin | JLL
BE 191705 - Van Nuys | Van Nuys | CA | AF | PowerTrack | 191705 | Retail | CBRE
BE 105499 - Lodi Vineyard | Lodi - Lodi Vineyard | CA | AEF | PowerTrack | 105499 | Admin | JLL
BE 144486 - Arden Fair Mall | Arden Fair Mall | CA | AEF | PowerTrack | 144486 | Admin | JLL
BE 199250 - Modesto Main | Modesto - Modesto Main | CA | AEF | PowerTrack | 199250 | Admin | JLL
BE 199506 - Stevens Creek | Stevens Creek | CA | AEF | PowerTrack | 199506 | Retail | CBRE
BE 101173 - Covina Main | Covina Main | CA | AEF | PowerTrack | 101173 | Retail | CBRE
BE 144507 - Old Ranch Town Center | Old Ranch Town Center | CA | AF | PowerTrack | 144507 | Retail | CBRE
BE 191411 - Mountain Gate Plaza | Mountain Gate Plaza | CA | AF | PowerTrack | 191411 | Retail | CBRE
BE 144410 - Arcadia Main | Arcadia Main | CA | AF | PowerTrack | 144410 | Retail | CBRE
BE 199190 - Fairfield | Fairfield | CA | AEF | PowerTrack | 199190 | Retail | CBRE
BE 199487 - Los Gatos | Los Gatos | CA | AEF | PowerTrack | 199487 | Retail | CBRE
BE 199892 - San Marino | San Marino | CA | AEF | PowerTrack | 199892 | Retail | CBRE
BE 199924 - Buenaventura | Buenaventura | CA | AEF | PowerTrack | 199924 | Retail | CBRE
CA: San Jose - Westgate | BE 199502 - Westgate | CA |  | PowerTrack | 199502 | Retail | CBRE
BE 103541 - 98th & Grant | 98th & Grant | CO | AF | PowerTrack | 103541 | Retail | CBRE
BE 101451 - Arapahoe Crossings | Arapahoe Crossings | CO | AF | PowerTrack | 101451 | Retail | CBRE
BE 120617 - Aurora City Center | Aurora City Center | CO | AF | PowerTrack | 120617 | Retail | CBRE
BE 101995 - Dry Creek | Dry Creek | CO | AEF | PowerTrack | 101995 | Retail | CBRE
BE 102040 - Highlands Ranch South | Highlands Ranch S. | CO | AEF | PowerTrack | 102040 | Retail | CBRE
BE 120717 - Lone Tree | Lone Tree | CO | AEF | PowerTrack | 120717 | Retail | CBRE
BE 103553 - Meridian | Meridian | CO | AF | PowerTrack | 103553 | Retail | CBRE
BE 105797 - Southglenn Relocation | Southglenn | CO |  | PowerTrack | 105797 | Retail | CBRE
BE 120768 - Standley Lake | Standley Lake | CO | AEF | PowerTrack | 120768 | Retail | CBRE
BE 106004 - Havana Gardens | Havana Gardens | CO | AF | PowerTrack | 106004 | Retail | CBRE
BE 144783 - East Hartford | East Hartford | CT | AEF | PowerTrack | 144783 | Retail | CBRE
BE 144725 - Norwalk Post Road | Norwalk | CT | AEF | PowerTrack | 144725 | Retail | CBRE
BE 107447 - Hialeah Gardens | Hialeah Gardens | FL | AEF | PowerTrack | 107447 | Retail | CBRE
BE 150496 - West Des Moines Campus - East | W. Des Moines Campus EAST | IA | AEF | PowerTrack | 150496 | Admin | CBRE
BE 150496 - West Des Moines Campus - SW | W. Des Moines Campus SW | IA | AEF | PowerTrack | 150496 | Admin | CBRE
BE 141278 - CIC | WF - CIC | NC |  | PowerTrack | 141278 | Admin | JLL
BE 141954 - DUC | Charlotte - Wells Fargo - DUC | NC |  | PowerTrack | 141954 | Admin | JLL
BE 140171 - East Windsor | East Windsor | NJ | AEF | PowerTrack | 140171 | Retail | CBRE
BE 141423 - Burlington Springside | Burlington | NJ | AEF | PowerTrack | 141423 | Retail | CBRE
BE 141327 - Bayonne Office | Bayonne | NJ | AEF | PowerTrack | 141327 | Retail | CBRE
BE 141382 - Clifton Office | Clifton | NJ | AEF | PowerTrack | 141382 | Retail | CBRE
BE 141427 - North Elizabeth Office | North Elizabeth | NJ | AEF | PowerTrack | 141427 | Retail | CBRE
BE 145739 - Westmont Plaza | Haddon Westmont Plaza | NJ | AEF | PowerTrack | 145739 | Retail | CBRE
BE 141464 - Parsippany Route 46 | Parsippany | NJ | AEF | PowerTrack | 141464 | Retail | CBRE
BE 141467 - Clark Office | Clark | NJ | AEF | PowerTrack | 141467 | Retail | CBRE
BE 141468 - Closter Office | Closter | NJ | AEF | PowerTrack | 141468 | Retail | CBRE
BE 140216 - Holmdel - Rt. 35 | Holmdel | NJ | AEF | PowerTrack | 140216 | Retail | CBRE
BE 144566 - Ellisburg Circle Center | Ellisburg Circle Center | NJ | AEF | PowerTrack | 144566 | Retail | CBRE
BE 141317 - Nutley Franklin | Nutley | NJ | AEF | PowerTrack | 141317 | Retail | CBRE
BE 140334 - Marlton | Marlton | NJ | AEF | PowerTrack | 140334 | Retail | CBRE
BE 140262 - Middletown - UC | Middletown | NJ | AEF | PowerTrack | 140262 | Retail | CBRE
BE 141443 - Whiting Crestwood | Whiting Crestwood | NJ | AEF | PowerTrack | 141443 | Retail | CBRE
BE 141441 - Barnegat Office | Barnegat | NJ | AEF | PowerTrack | 141441 | Retail | CBRE
BE 141445 - Manchester Office | Manchester | NJ | AEF | PowerTrack | 141445 | Retail | CBRE
BE 144269 - West Deptford / Woodbury | West Deptford - Woodbury | NJ | AEF | PowerTrack | 144269 | Retail | CBRE
BE 141344 - Edison Office | Edison | NJ | AEF | PowerTrack | 141344 | Retail | CBRE
BE 142050 - Flemington | Flemington | NJ | AEF | PowerTrack | 142050 | Retail | CBRE
BE 140332 - Rt. 22 Springfield | Route 22 | NJ | AEF | PowerTrack | 140332 | Retail | CBRE
BE 141466 - Laurelton Office | Laurelton | NJ |  | PowerTrack | 141466 | Retail | CBRE
BE 142088 - Mahwah | Mahwah | NJ | AEF | PowerTrack | 142088 | Retail | CBRE
BE 144110 - Franklin Township | Franklin Township WF | NJ | AEF | PowerTrack | 144110 | Retail | CBRE
BE 144103 - Bordentown | Bordentown | NJ | AEF | PowerTrack | 144103 | Retail | CBRE
BE 141918 - South Plainfield Oak Park | South Plainfield | NJ | AEF | PowerTrack | 141918 | Retail | CBRE
BE 144813 - Somerset | Somerset | NJ | AEF | PowerTrack | 144813 | Retail | CBRE
BE 145709 - Clinton | Clinton Main Relo | NJ |  | PowerTrack | 145709 | Retail | CBRE
BE 143233 - North Brunswick Financial Ctr | North Brunswick | NJ | AEF | PowerTrack | 143233 | Retail | CBRE
BE 141916 - Cherry Hill Short Hills | Cherry Hill | NJ | AEF | PowerTrack | 141916 | Retail | CBRE
BE 142875 - Hainesport Crossroads | Hainesport | NJ | AEF | PowerTrack | 142875 | Retail | CBRE
BE 144679 - 106 - San Antonio Ops | San Antonio - Ops Ctr (Bldg 106) | TX |  | PowerTrack | 144679 | Admin | CBRE
BE 144679 - GM - San Antonio Ops | San Antonio - Ops Ctr GM | TX |  | PowerTrack | 144679 | Admin | CBRE
BE 144679 - 201 - San Antonio Ops | San Antonio - Ctr (Bldg 201) | TX |  | PowerTrack | 144679 | Admin | CBRE
BE 144679 - 203 - San Antonio Ops | San Antonio - Ops Ctr (Bldg 203) | TX |  | PowerTrack | 144679 | Admin | CBRE
BE 144679 - 205 - San Antonio Ops | San Antonio - Ops Ctr (Bldg 205) | TX |  | PowerTrack | 144679 | Admin | CBRE
BE 144679 - 307 - San Antonio Ops | San Antonio - Ops Ctr (Bldg 307) | TX |  | PowerTrack | 144679 | Admin | CBRE
BE 144679 - 308 - San Antonio Ops | San Antonio - Ctr (Bldg 308) | TX |  | PowerTrack | 144679 | Admin | CBRE
BE 144679 - 104 - San Antonio Ops | San Antonio - Ops Ctr (Bldg 104) | TX |  | PowerTrack | 144679 | Admin | CBRE
BE 144679 - 102 - San Antonio Ops | San Antonio - Ops Ctr (Bldg 102) | TX |  | PowerTrack | 144679 | Admin | CBRE
BE 101497 - N Black Canyon Hwy, Phoenix - North | N Black Canyon Hwy, Phoenix - North | AZ | AEF | PowerTrack | 101497 | Admin | JLL
BE 101497 - N Black Canyon Hwy, Phoenix - South | N Black Canyon Hwy, Phoenix - South | AZ | AEF | PowerTrack | 101497 | Admin | JLL
BE 102073 - Building 2222, Rose Garden Ln, Phoenix | Building 2222, Rose Garden Ln, Phoenix | AZ | AEF | PowerTrack | 102073 | Admin | JLL
BE 102566 - Building 2202, Rose Garden Ln, Phoenix | Building 2202, Rose Garden Ln, Phoenix | AZ | AEF | PowerTrack | 102566 | Admin | JLL
BE 192010 - 99TH Ave & BELL | 99TH Ave & BELL | AZ | AEF | PowerTrack | 192010 | Retail | CBRE
BE 192156 - Rincon | Rincon | AZ | AEF | PowerTrack | 192156 | Retail | CBRE
BE 198359 - Tucson Main Parking Garage | Tucson Main Parking Garage | AZ | AEF | PowerTrack | 198359 | Retail | CBRE