## Year to Date
Luminace |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 25149053.5558 | 26782535.4312 | -1633481.8754 | -6.099% | 37380720.284 | -12231666.7282 | -32.72%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Raymond Ed Re-Development - DC-23-0001 | DC | 442042.2504 | 357732.61 | 84309.6404 | 23.57% | 364957.95 | -38807.95 | -10.63%
Berkeley - NJ-22-C893 Berkeley I | NJ | 1905939 | 1568745.2792 | 337193.7208 | 21.49% | 5671765.13 | -3765826.13 | -66.4%
Berkeley - NJ-22-C894 Berkeley II | NJ | 3204012.3791 | 3026817.8 | 177194.5791 | 5.854% | 5695869 | -2491856.6209 | -43.75%
BEMS Landfill East | NJ | 1445846.16 | 3438165.201 | -1992319.041 | -57.95% | 5180275.29 | -3734429.13 | -72.09%
Southampton - BEMS West NJ-22-C898 | NJ | 4830054.9942 | 5413787.7 | -583732.7058 | -10.78% | 5507348 | -677293.0058 | -12.3%
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 73043.2644 | 20037.303 | 53005.9614 | 264.5% | 19448 | -309.9883 | -1.594%
Lakewood Township - Public Works | NJ | 1196112.975 | 547225.362 | 648887.613 | 118.6% | 703535.051 | 492577.924 | 70.01%
Canby - Dover - OR-23-C003 | OR | 2555298.849 | 2504702.6 | 50596.249 | 2.02% | 2650230 | -94931.151 | -3.582%
Estacada - Clayfield - OR-23-C001 | OR | 1943872.902 | 2040013.6 | -96140.698 | -4.713% | 2938068 | -994195.098 | -33.84%
Willamina - Waterford - OR-23-C006 | OR | 1698158.4067 | 2032927.901 | -334769.4943 | -16.47% | 2428860.72 | -730702.3133 | -30.08%
OR-23-C005 Solops SPI - Belvedere Solar | OR | 3391568.626 | 3297116.3 | 94452.326 | 2.865% | 3457129 | -65560.374 | -1.896%
OR-23-C002 SPI - Cork Solar | OR | 1475963.752 | 1378969.075 | 96994.677 | 7.034% | 1405666.043 | 70297.709 | 5.001%
OR: Oregon City - Buckner Creek - OR-23-C008 | OR | 237462.39 | 357689.4 | -120227.01 | -33.61% | 424314 | -186851.61 | -44.04%
OR: Dundee - Gun Club - OR-23-C009 | OR | 483722.546 | 514135 | -30412.454 | -5.915% | 538888.1 | -55165.554 | -10.24%
OR: Molalla - Marquam - OR-23-C010 | OR | 265955.061 | 284470.3 | -18515.239 | -6.509% | 394366 | -128410.939 | -32.56%

## 1st Qtr
Luminace |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 1526713.3764 | 1623475.4862 | -96762.1098 | -5.96% | 5982362.51 | -4455649.1336 | -74.48%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Raymond Ed Re-Development - DC-23-0001 | DC | 115892.2504 | 0 | 115892.2504 |  | 0 | 0
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 32042.4562 | -32042.4562 | -100% | 1495580.21 | -1495580.21 | -100%
Berkeley - NJ-22-C894 Berkeley II | NJ | 109808.1055 | 271422.9 | -161614.7945 | -59.54% | 1480295 | -1370486.8945 | -92.58%
BEMS Landfill East | NJ | 0 | 13254.93 | -13254.93 | -100% | 1554068.3 | -1554068.3 | -100%
Southampton - BEMS West NJ-22-C898 | NJ | 1043156 | 1306755.2 | -263599.2 | -20.17% | 1352961 | -309805 | -22.9%
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 13246.3581 | 0 | 13246.3581 |  | 0 | 0
Lakewood Township - Public Works | NJ | 244610.6624 | 0 | 244610.6624 |  | 99458 | 145152.6624 | 145.9%
Canby - Dover - OR-23-C003 | OR | 0 | 0 | 0 |  | 0 | 0
Estacada - Clayfield - OR-23-C001 | OR | 0 | 0 | 0 |  | 0 | 0
Willamina - Waterford - OR-23-C006 | OR | 0 | 0 | 0 |  | 0 | 0
OR-23-C005 Solops SPI - Belvedere Solar | OR | 0 | 0 | 0 |  | 0 | 0
OR-23-C002 SPI - Cork Solar | OR | 0 | 0 | 0 |  | 0 | 0
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR

## 2nd Qtr
Luminace |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 8503548.1283 | 9039653.033 | -536104.9047 | -5.931% | 13787020.76 | -5283472.6317 | -38.32%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Raymond Ed Re-Development - DC-23-0001 | DC | 168345.6 | 181763.78 | -13418.18 | -7.382% | 187096.3 | -18750.7 | -10.02%
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 0 | 0 |  | 2101906.67 | -2101906.67 | -100%
Berkeley - NJ-22-C894 Berkeley II | NJ | 1267343.2736 | 788162.7 | 479180.5736 | 60.8% | 2118046 | -850702.7264 | -40.16%
BEMS Landfill East | NJ | 2909 | 1275699.521 | -1272790.521 | -99.77% | 2062841.79 | -2059932.79 | -99.86%
Southampton - BEMS West NJ-22-C898 | NJ | 1803228 | 1916638.5 | -113410.5 | -5.917% | 2092575 | -289347 | -13.83%
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 29075.4536 | 0 | 29075.4536 |  | 0 | 0
Lakewood Township - Public Works | NJ | 484004.4261 | 0 | 484004.4261 |  | 266490 | 217514.4261 | 81.62%
Canby - Dover - OR-23-C003 | OR | 1059524.378 | 1010842.3 | 48682.078 | 4.816% | 1019387 | 40137.378 | 3.937%
Estacada - Clayfield - OR-23-C001 | OR | 1217604.408 | 1107693.5 | 109910.908 | 9.923% | 1101450 | 116154.408 | 10.55%
Willamina - Waterford - OR-23-C006 | OR | 449018.424 | 862021.177 | -413002.753 | -47.91% | 938139 | -489120.576 | -52.14%
OR-23-C005 Solops SPI - Belvedere Solar | OR | 1425196.633 | 1339749.9 | 85446.733 | 6.378% | 1362976 | 62220.633 | 4.565%
OR-23-C002 SPI - Cork Solar | OR | 597298.532 | 557081.655 | 40216.877 | 7.219% | 536113 | 61185.532 | 11.41%
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR

## 3rd Qtr
Luminace |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 15118792.0511 | 16119406.912 | -1000614.8609 | -6.208% | 17611337.014 | -2492544.9629 | -14.15%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Raymond Ed Re-Development - DC-23-0001 | DC | 157804.4 | 175968.83 | -18164.43 | -10.32% | 177861.65 | -20057.25 | -11.28%
Berkeley - NJ-22-C893 Berkeley I | NJ | 1905939 | 1536702.823 | 369236.177 | 24.03% | 2074278.25 | -168339.25 | -8.116%
Berkeley - NJ-22-C894 Berkeley II | NJ | 1826861 | 1967232.2 | -140371.2 | -7.135% | 2097528 | -270667 | -12.9%
BEMS Landfill East | NJ | 1442937.16 | 2149210.75 | -706273.59 | -32.86% | 1563365.2 | -120428.04 | -7.703%
Southampton - BEMS West NJ-22-C898 | NJ | 1983670.9942 | 2190394 | -206723.0058 | -9.438% | 2061812 | -78141.0058 | -3.79%
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 30721.4527 | 20037.303 | 10684.1497 | 53.32% | 19448 | -309.9883 | -1.594%
Lakewood Township - Public Works | NJ | 467497.8865 | 547225.362 | -79727.4755 | -14.57% | 337587.051 | 129910.8355 | 38.48%
Canby - Dover - OR-23-C003 | OR | 1495774.471 | 1493860.3 | 1914.171 | 0.1281% | 1630843 | -135068.529 | -8.282%
Estacada - Clayfield - OR-23-C001 | OR | 726268.494 | 932320.1 | -206051.606 | -22.1% | 1836618 | -1110349.506 | -60.46%
Willamina - Waterford - OR-23-C006 | OR | 1249139.9827 | 1170906.724 | 78233.2587 | 6.681% | 1490721.72 | -241581.7373 | -16.21%
OR-23-C005 Solops SPI - Belvedere Solar | OR | 1966371.993 | 1957366.4 | 9005.593 | 0.4601% | 2094153 | -127781.007 | -6.102%
OR-23-C002 SPI - Cork Solar | OR | 878665.22 | 821887.42 | 56777.8 | 6.908% | 869553.043 | 9112.177 | 1.048%
OR: Oregon City - Buckner Creek - OR-23-C008 | OR | 237462.39 | 357689.4 | -120227.01 | -33.61% | 424314 | -186851.61 | -44.04%
OR: Dundee - Gun Club - OR-23-C009 | OR | 483722.546 | 514135 | -30412.454 | -5.915% | 538888.1 | -55165.554 | -10.24%
OR: Molalla - Marquam - OR-23-C010 | OR | 265955.061 | 284470.3 | -18515.239 | -6.509% | 394366 | -128410.939 | -32.56%

## 4th Qtr
Luminace |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Raymond Ed Re-Development - DC-23-0001 | DC | 0 | 0 | 0 |  | 0 | 0
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 0 | 0 |  | 0 | 0
Berkeley - NJ-22-C894 Berkeley II | NJ | 0 | 0 | 0 |  | 0 | 0
BEMS Landfill East | NJ | 0 | 0 | 0 |  | 0 | 0
Southampton - BEMS West NJ-22-C898 | NJ | 0 | 0 | 0 |  | 0 | 0
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ |  | 0 |  |  | 0 | 0
Lakewood Township - Public Works | NJ |  | 0 |  |  | 0 | 0
Canby - Dover - OR-23-C003 | OR |  | 0 |  |  | 0 | 0
Estacada - Clayfield - OR-23-C001 | OR |  | 0 |  |  | 0 | 0
Willamina - Waterford - OR-23-C006 | OR |  | 0 |  |  | 0 | 0
OR-23-C005 Solops SPI - Belvedere Solar | OR |  | 0 |  |  | 0 | 0
OR-23-C002 SPI - Cork Solar | OR |  | 0 |  |  | 0 | 0
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR

## Jan
Luminace |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 391768.8975 | 660242.88 | -268473.9825 | -40.66% | 1616542 | -1224773.1025 | -75.77% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 14808.792 | N/A |  |  | N/A |  |  | 1. CSS resolved the DAS issues on 01/03, and M0 started reporting the production on 01/03. However, M1 is reporting negative values. As per the drawings, the site capacity is 365 kW, but meter M0 is reporting 295 kW, and M1 is reporting -295 kW. We have consider M0 production as total site production. Reached out to AE #557940 | 1.SR094989, SR096863 | SR096863
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 31205.78 | -31205.78 | -100% | 412354 | -412354 | -100% | 1. Site is dealing with utility-related issue throughout the month, and the EPC team is currently addressing the issue. | 1. SR093414
Berkeley - NJ-22-C894 Berkeley II | NJ | 109808.1055 | 271422.9 | -161614.7945 | -59.54% | 406892 | -297083.8945 | -73.01% | 1. Site is dealing with utility-related issue throughout the month, and the EPC team is currently addressing the issue. | 1. SR093414
BEMS Landfill East | NJ | 0 | 0 | 0 |  | 435058 | -435058 | -100% | 1.Utility company has shut down site since 06/11/24. | 1.SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 267152 | 357614.2 | -90462.2 | -25.3% | 362238 | -95086 | -26.25% | 1.Site tripped offline at 2:30AM on 01/21 due to Phase A voltage missing Fault and back online at 10AM on 01/30. | 1.SR095756
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ
Lakewood Township - Public Works | NJ
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Since meter M1 is reporting negative values from 01/03 we have consider M0 production as total site production.

## Feb
Luminace |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 431689.124 | 397154.4762 | 34534.6478 | 8.696% | 1851765.4 | -1420076.276 | -76.69% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 27512.157 | N/A |  |  | N/A |  |  | 1.M1 meter is reporting negative values from 01/03 and through out the Month. AE says likely an onsite issue and to swap CT lead polarity. 2.Site stopped communicating from 02/26 due to some DAS equipment was RMA'd. CSS is about to do capacity test at site after DAS issues resolved. 3. Expected and forecasted data are unavailable. | 1.SR096863 2.SR094989, SR097768 | SR094989 | SR097768
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 836.6762 | -836.6762 | -100% | 461858.4 | -461858.4 | -100% | 1. Site is dealing with utility-related issue throughout the month, and the EPC team is currently addressing the issue. | 1.SR093413
Berkeley - NJ-22-C894 Berkeley II | NJ | 0 | N/A |  |  | 456469 | -456469 | -100% | 1. Site is dealing with utility-related issue throughout the month, and the EPC team is currently addressing the issue. | 1.SR093414
BEMS Landfill East | NJ | 0 | N/A |  |  | 498875 | -498875 | -100% | 1.Utility company has shut down site since 06/11/24 due to the solar causing an issue with the grid. | 1.SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 306069 | 396317.8 | -90248.8 | -22.77% | 403220 | -97151 | -24.09% | 1. Site was tripped offline at 12:15AM on 02/22 due to Phase A voltage missing fault and back online at 11:45AM on 02/28. | 1.SR097638
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 4807.5 | N/A |  |  | N/A |  |  | 1. Expected and forecasted data are unavailable.
Lakewood Township - Public Works | NJ | 93300.467 | N/A |  |  | 31343 | 61957.467 | 197.7% | 1. Forecasted data was very low and expected data are unavailable.
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Since meter M1 is reporting negative values from 01/03 we have consider M0 production as total site production.

## Mar
Luminace |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 703255.355 | 566078.13 | 137177.225 | 24.23% | 2514055.11 | -1810799.755 | -72.03% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 73571.3014 | N/A |  |  | N/A |  |  | 1.Site communications are back at 11:45AM on 03/25 after RMA installation. 2. We don't have expected and forecasted energy values for this site. | 1.SR094989,SR097768 | SR097768
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | N/A |  |  | 621367.81 | -621367.81 | -100% | 1.The site is dealing with utility-related issues due to damaged CTs and PTs in their metering bank, as has been the case throughout the month. The EPC team is currently addressing the issue. | 1.SR098409,SR093413 | SR093413
Berkeley - NJ-22-C894 Berkeley II | NJ | 0 | N/A |  |  | 616934 | -616934 | -100% | 1.The site is dealing with utility-related issues due to damaged CTs and PTs in their metering bank, as has been the case throughout the month. The EPC team is currently addressing the issue. | 1.SR098411,SR093414 | SR093414
BEMS Landfill East | NJ | 0 | 13254.93 | -13254.93 | -100% | 620135.3 | -620135.3 | -100% | 1.The site communication was back at 10:15AM and again stopped communication on 03/04 at 15:00 due to an issue with the MV breaker on the skid. The team is currently working with SMA to resolve the issue and is testing the IKI relay. Additionally, a single-phase witness test under load with the utility is pending prior to re-energization. 2.Utility company has shut down site since 06/11/24 due to the solar causing an issue with the grid. | 1.SR098408 2.SR086098 | SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 469935 | 552823.2 | -82888.2 | -14.99% | 587503 | -117568 | -20.01% | 1.Site tripped offline 18:15 on 03/05 and back online at 12:45 on 03/14. | 1.SR097638
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 8438.8581 | N/A |  |  | N/A
Lakewood Township - Public Works | NJ | 151310.1954 | N/A |  |  | 68115 | 83195.1954 | 122.1% | 1. The forecasted values have been updated by AE, but they appear to be low.
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR

## Apr
Luminace |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 854032.0153 | 717297.95 | 136734.0653 | 19.06% | 2800077.99 | -1946045.9747 | -69.5% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 54203.1 | 57596.35 | -3393.25 | -5.891% | 56794.59 | -2591.49 | -4.563%
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 0 | 0 |  | 676075 | -676075 | -100% | 1.The site is dealing with utility-related issues due to damaged CTs and PTs in their metering bank, as has been the case throughout the month. The EPC team is currently addressing the issue. | 1. SR098409
Berkeley - NJ-22-C894 Berkeley II | NJ | 0 | 0 | 0 |  | 676850 | -676850 | -100% | 1.The site is dealing with utility-related issues due to damaged CTs and PTs in their metering bank, as has been the case throughout the month. The EPC team is currently addressing the issue. | 1. SR098411
BEMS Landfill East | NJ | 0 | 12059.7 | -12059.7 | -100% | 651557.4 | -651557.4 | -100% | 1.The site communication was back at 10:15AM and again stopped communication on 03/04 at 15:00 due to an issue with the MV breaker on the skid. The team is currently working with SMA to resolve the issue and is testing the IKI relay. Additionally, a single-phase witness test under load with the utility is pending prior to re-energization. 2.Utility company has shut down site since 06/11/24 due to the solar causing an issue with the grid. | 1.SR098408 2.SR086098 | SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 635861 | 647641.9 | -11780.9 | -1.819% | 658293 | -22432 | -3.408%
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 9269.4465 | N/A |  |  | N/A
Lakewood Township - Public Works | NJ | 154698.4688 | N/A |  |  | 80508 | 74190.4688 | 92.15% | 1. The forecasted values have been updated by AE, but they appear to be low.
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR

## May
Luminace |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 3877714.643 | 3723083.84 | 154630.803 | 4.153% | 5379743.8 | -1502029.157 | -27.92% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 54648.5 | 59815.54 | -5167.04 | -8.638% | 63486.3 | -8837.8 | -13.92% | 1. Low production due to rain
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 0 | 0 |  | 710210 | -710210 | -100% | 1.The site is dealing with utility-related issues due to damaged CTs and PTs in their metering bank, as has been the case throughout the month. The EPC team is currently addressing the issue. | 1.SR098409
Berkeley - NJ-22-C894 Berkeley II | NJ | 701245.2736 | 191085.9 | 510159.3736 | 267% | 710606 | -9360.7264 | -1.317% | 1.The site was dealing with utility-related issues due to damaged CTs and PTs in their metering bank.Site was back online at 16:00EDT on 05/20. | 1.SR098411
BEMS Landfill East | NJ | 0 | 586005 | -586005 | -100% | 695675.5 | -695675.5 | -100% | 1.The site communication was back at 10:15 and again stopped communication on 03/04 at 15:00 due to an issue with the MV breaker on the skid. The team is currently working with SMA to resolve the issue and is testing the IKI relay. Additionally, a single-phase witness test under load with the utility is pending prior to re-energization. 2.Utility company has shut down site since 06/11/24 due to the solar causing an issue with the grid. | 1.SR098408 2.SR086098 | SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 628239 | 645088.6 | -16849.6 | -2.612% | 704768 | -76529 | -10.86% | 1. Low production due to rain
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 9749.9441 | N/A |  |  | N/A
Lakewood Township - Public Works | NJ | 157465.6563 | N/A |  |  | 92403 | 65062.6563 | 70.41% | 1. The forecasted values have been updated by AE, but they appear to be low.
Canby - Dover - OR-23-C003 | OR | 499021.269 | 471441.3 | 27579.969 | 5.85% | 494897 | 4124.269 | 0.8334% | 1. Multiple trackers had been stuck since 04/03 and started tracking again on 05/22. 2. Inverters 7, 8, and 16 are experiencing morning shading, with inverter 8 in particular not reaching its full production until 09:45. | 1. SR101115 2. SR101155 | SR101155
Estacada - Clayfield - OR-23-C001 | OR | 554193.004 | 515253.5 | 38939.504 | 7.557% | 532245 | 21948.004 | 4.124% | 1. Multiple trackers had been stuck since 05/07 and started tracking again on 05/22. 2. The site tripped offline at 14:00 on 05/12 and came back online at 09:00 on 05/13. | 1. SR101126 2. SR101287 | SR101287
Willamina - Waterford - OR-23-C006 | OR | 345311.5 | 387541.9 | -42230.4 | -10.9% | 464151 | -118839.5 | -25.6% | 1. All inverters are power limited to 85kW. Per As-Builts, they should be running at 122kW. 2. The site tripped offline at 10:00 on 05/23 and came back online at 11:15 on 05/29. | 1. SR101124 2. SR101894 | SR101894
OR-23-C005 Solops SPI - Belvedere Solar | OR | 641330.014 | 599695.6 | 41634.414 | 6.943% | 653170 | -11839.986 | -1.813% | 1. Site tripped offline at 16:07 on 05/15 and came back online at 08:30 on 05/20. | 1. SR101566
OR-23-C002 SPI - Cork Solar | OR | 286510.482 | 267156.5 | 19353.982 | 7.244% | 258132 | 28378.482 | 10.99%
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR

## Jun
Luminace |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 3771801.47 | 4599271.243 | -827469.773 | -17.99% | 5607198.97 | -1835397.5 | -32.73% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 59494 | 64351.89 | -4857.89 | -7.549% | 66815.41 | -7321.41 | -10.96% | 1. Site has low production on 06/08, 06/26, 06/15, 06/16, 06/17, 06/27 due to low irradiance.
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 0 | 0 |  | 715621.67 | -715621.67 | -100% | 1.Site was offline for whole month. | 1.SR098409
Berkeley - NJ-22-C894 Berkeley II | NJ | 566098 | 597076.8 | -30978.8 | -5.188% | 730590 | -164492 | -22.51% | 1.Site tripped offline since 13:00 on 06/27. | 1.SR103839
BEMS Landfill East | NJ | 2909 | 677634.821 | -674725.821 | -99.57% | 715608.89 | -712699.89 | -99.59% | 1.Site was offline for whole month. | 1.SR098408, SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 539128 | 623908 | -84780 | -13.59% | 729514 | -190386 | -26.1% | 1.Site tripped offline at 14:45 on 06/05 and was back online at 16:15 on 06/05,again tripped offline at 07:45 on 06/08 reporting reporting "Missing Phase A Voltage" and was back online at 10:00 on 06/09,again tripped offline at 23:45 on 06/10 and was back online at 08:15 on 06/12,again tripped offline at 20:00 on 06/14 and remained offline throughout the month. | 1.SR102671
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 10056.063 | N/A |  |  | N/A
Lakewood Township - Public Works | NJ | 171840.301 | N/A |  |  | 93579 | 78261.301 | 83.63% | 1.Inverter 2.3 was underperforming by 6KW since 06/01 during peak hours and remained the same throughout the month | 1.SR103097
Canby - Dover - OR-23-C003 | OR | 560503.109 | 539401 | 21102.109 | 3.912% | 524490 | 36013.109 | 6.866%
Estacada - Clayfield - OR-23-C001 | OR | 663411.404 | 592440 | 70971.404 | 11.98% | 569205 | 94206.404 | 16.55% | 1.Tracker motor 68 was struck at -58 degrees at 08:30 pdt on 06/10 and was back at 13:45 pdt on 06/24 | 1.SR103219
Willamina - Waterford - OR-23-C006 | OR | 103706.924 | 474479.277 | -370772.353 | -78.14% | 473988 | -370281.076 | -78.12% | 1.All inverters are power limited to 85kW. Per As-Builts, they should be running at 122kW. | 1.SR101124
OR-23-C005 Solops SPI - Belvedere Solar | OR | 783866.619 | 740054.3 | 43812.319 | 5.92% | 709806 | 74060.619 | 10.43%
OR-23-C002 SPI - Cork Solar | OR | 310788.05 | 289925.155 | 20862.895 | 7.196% | 277981 | 32807.05 | 11.8%
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR

## Jul
Luminace |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 5167208.148 | 5683836.835 | -516628.687 | -9.089% | 5773431.353 | -606223.205 | -10.5% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 57705 | 63485.59 | -5780.59 | -9.105% | 67817.09 | -10112.09 | -14.91% | 1. Inverter 8 tripped offline at 17:00 on 07/06 and back online on 07/07. Inverter again went offline at 9:15 on 07/07 and back online at 12:40 on the same day. and inverter 8 started late on 07/21 at 10:45. | 1. SR104065
Berkeley - NJ-22-C893 Berkeley I | NJ | 586285 | 562423.289 | 23861.711 | 4.243% | 753344.5 | -167059.5 | -22.18% | 1. The site had been offline for several months and came back online at 15:30 on 07/02. 2. Site was offline from 12:00 to 14:00 on 07/29 due to PM Event | 1. SR098409 2. PM11764
Berkeley - NJ-22-C894 Berkeley II | NJ | 697981 | 698857.1 | -876.1 | -0.1254% | 760155 | -62174 | -8.179% | 1. SIte was offline since 06/27 and back online at 13:00 on 07/03. 2. Inverter tripped offline 16:45 on 07/31 due to"Error Error" and remaied offline. | 1. SR103839 2. SR105463 | SR105463
BEMS Landfill East | NJ | 328242.16 | 743855.75 | -415613.59 | -55.87% | 283735 | 44507.16 | 15.69% | 1. The site had been offline for several months and came back online at 15:00 on 07/21. | 1.SR098408, SR086098 | SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 771229 | 807871.5 | -36642.5 | -4.536% | 764197 | 7032 | 0.9202% | 1. Site started late on 07/17 at 08:30. | 1. SR102671
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 11583.441 | N/A |  |  | N/A
Lakewood Township - Public Works | NJ | 139268.824 | 195547.462 | -56278.638 | -28.78% | 94258 | 45010.824 | 47.75% | 1. Site tripped offline at 16:15 on 07/01 and back online at 8:00 on 07/09. | 1. SR103899
Canby - Dover - OR-23-C003 | OR | 606657.224 | 607264 | -606.776 | -0.09992% | 628020 | -21362.776 | -3.402%
Estacada - Clayfield - OR-23-C001 | OR | 345245.485 | 407692.8 | -62447.315 | -15.32% | 731514 | -386268.515 | -52.8% | 1. Tracker motor 26.5 was strucked since 07/07. Tracker has not returned to service and will remain open for client visibility during ongoing EPC punch lists 2. Site tripped offline at 8:30 on 07/15. This site has not returned to service and will remain open for client visibility during ongoing EPC punch lists | 1. SR104276 2. SR104461 | SR104461
Willamina - Waterford - OR-23-C006 | OR | 446366.5 | 465402.724 | -19036.224 | -4.09% | 547504.72 | -101138.22 | -18.47% | 1. Site was offline from 08:15 on 07/26 to 09:15 on 07/28 and again site was offline from 20:30 o 07/28 to end of month. 2. Since the meter did not communicate from 06/06 to 07/10, the total meter energy was backfilled on 07/10. Therefore, we used the inverter energy from 07/01 to 07/10 and added it with the production meter energy from 07/11 to 07/31. | 1. SR105123
OR-23-C005 Solops SPI - Belvedere Solar | OR | 828134.537 | 805271.2 | 22863.337 | 2.839% | 823154 | 4980.537 | 0.6051%
OR-23-C002 SPI - Cork Solar | OR | 348509.977 | 326165.42 | 22344.557 | 6.851% | 319732.043 | 28777.934 | 9.001%
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR

## Aug
Luminace |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 4965475.9051 | 4988205.532 | -22729.6269 | -0.4557% | 5787157.721 | -821681.8159 | -14.2% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 55645.4 | 61869.44 | -6224.04 | -10.06% | 60498.02 | -4852.62 | -8.021% | 1. Inverter 4 was underproduced for whole month. | 1. SR107731
Berkeley - NJ-22-C893 Berkeley I | NJ | 693283 | 539725.412 | 153557.588 | 28.45% | 701899.15 | -8616.15 | -1.228% | 1.Site was offline at 20:15 on 08/20 and came back at 12:00 on 08/21 | 1.SR106617
Berkeley - NJ-22-C894 Berkeley II | NJ | 626497 | 679139.4 | -52642.4 | -7.751% | 712241 | -85744 | -12.04% | 1.Inverter 1 offline 16:45 on 07/31 and it came back online at 10:15 on 08/04 2.Site was offline on 08/14 and came back online at 13:15 on 08/15 3.Site was offline at 20:25 to 10:15 on 08/21 | 1.SR105463 2.SR106265 3.SR106618 | SR106265 | SR106618
BEMS Landfill East | NJ | 663197 | 776737.4 | -113540.4 | -14.62% | 687675.5 | -24478.5 | -3.56% | 1. Inverter 1 combiner 13, 14, 15 and 16 are offline since site regained its communications on 07/21. | 1.SR106977
Southampton - BEMS West NJ-22-C898 | NJ | 695453 | 774345.9 | -78892.9 | -10.19% | 697041 | -1588 | -0.2278% | 1. Site was producing as expected.
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 10886.3789 | 11437.18 | -550.8011 | -4.816% | 10813 | 73.3789 | 0.6786%
Lakewood Township - Public Works | NJ | 184757.1875 | 194634.4 | -9877.2125 | -5.075% | 174400.051 | 10357.1365 | 5.939%
Canby - Dover - OR-23-C003 | OR | 503949.346 | 491321.7 | 12627.646 | 2.57% | 580932 | -76982.654 | -13.25% | 1. Inverter 8 and 6 have heavy morning shading
Estacada - Clayfield - OR-23-C001 | OR | 141023.273 | 201984.4 | -60961.127 | -30.18% | 624249 | -483225.727 | -77.41% | 1.Tracker motor 26.5 was strucked since 07/07. Back online 10:00 on 08/22 2The site tripped offline at 08:30 on 07/15. The inverters came back online at 16:45 on 08/20, but the meter was not communicating as of 17:25. Meter communications were restored at 10:45 on 08/22. 3.All trackers are stowed from 8/23/25 reporting "Manual_Mode_2: Manual Mode ON Manual_Mode_3: Manual Mode ON". on 08/29 all trackers are tracking except row 18 (18.1 through 18.10) 4.Site tripped offline at 07:45 to 16:30 on 08/27 | 1.SR104276 2. SR104461 3. SR106841 4. SR107017 | SR104461 | SR106841 | SR107017
Willamina - Waterford - OR-23-C006 | OR | 419845.1437 | 325034.6 | 94810.5437 | 29.17% | 510859 | -91013.8563 | -17.82% | 1. All inverters are power limited to 85kW. Per As-Builts, they should be running at 122kW. 2.Site was back online at 12:15 on 08/05 and again site tripped offline at 08:00 on 08/08 and came back online at 16:15 on 08/11 | 1.SR101124 2. SR105123 | SR105123
OR-23-C005 Solops SPI - Belvedere Solar | OR | 678379.971 | 666487.9 | 11892.071 | 1.784% | 724856 | -46476.029 | -6.412%
OR-23-C002 SPI - Cork Solar | OR | 292559.205 | 265487.8 | 27071.405 | 10.2% | 301694 | -9134.795 | -3.028%
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR

## Sep
Luminace |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 4986107.998 | 5447364.545 | -461256.547 | -8.468% | 6050747.94 | -1064639.942 | -17.6%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 44454 | 50613.8 | -6159.8 | -12.17% | 49546.54 | -5092.54 | -10.28% | 1. Inverter 4 was underperforming by 6kW for whole month. 2. Inverter 8 was offline fom 07:00 to 11:15 on 09/10. | 1. SR107731 2. SR107760 | SR107760
Berkeley - NJ-22-C893 Berkeley I | NJ | 626371 | 434554.122 | 191816.878 | 44.14% | 619034.6 | 7336.4 | 1.185% | 1. Combiner 1-5 was isolated for whole month. | 1. SR106974
Berkeley - NJ-22-C894 Berkeley II | NJ | 502383 | 589235.7 | -86852.7 | -14.74% | 625132 | -122749 | -19.64% | 1. Site was offline from 16:00 on 09/04 to 12:00 on 09/08. 2. Inverter was derated to 2800kW for whole month due to bad fan. | 1. SR107483 2. SR107895 | SR107895
BEMS Landfill East | NJ | 451498 | 628617.6 | -177119.6 | -28.18% | 591954.7 | -140456.7 | -23.73% | 1. Site was offline from 12:00 on 09/01 to 10:45 on 09/02 and again the site was offline from 11:00 on 09/03 to 10:30 on 09/04 and again the site was offline from 13:00 on 09/14 to 09:00 on 09/19 and again the inverter was offline from 08:30 to 11:15 on 09/23 and from 09:00 to 10:45 on 09/24. | 1. SR107944, SR107388, SR107269 | SR107388 | SR107269
Southampton - BEMS West NJ-22-C898 | NJ | 516988.9942 | 608176.6 | -91187.6058 | -14.99% | 600574 | -83585.0058 | -13.92% | 1. Site was offline from 11:30 to 14:00 on 09/23 and again site was offline from 19:00 on 09/23 to 07:00 on 09/26 and again the site was offline from 16:30 on 09/27 to end of the month. | 1. SR108453, SR108684 | SR108684
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 8251.6328 | 8600.123 | -348.4902 | -4.052% | 8635 | -383.3672 | -4.44%
Lakewood Township - Public Works | NJ | 143471.875 | 157043.5 | -13571.625 | -8.642% | 68929 | 74542.875 | 108.1% | 1. As per weather station the plant is performing as expected. The forecasted (theoretical) values may appear lower and they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance.
Canby - Dover - OR-23-C003 | OR | 385167.901 | 395274.6 | -10106.699 | -2.557% | 421891 | -36723.099 | -8.704%
Estacada - Clayfield - OR-23-C001 | OR | 239999.736 | 322642.9 | -82643.164 | -25.61% | 480855 | -240855.264 | -50.09% | 1. The site was offline from 08:45 on 09/01 to 13:00 on 09/02, from 07:30 to 17:45 on 09/03, and from 07:30 to 16:00 on 09/08. It was also offline from 15:00 on 09/12 to 08:30 on 09/17. Additionally, the site was offline from 09:00 on 09/25 through the end of the month. 2. All trackers were not communicated from 09/10 to end of the month. | 1. SR107017 2. SR106841 | SR106841
Willamina - Waterford - OR-23-C006 | OR | 382928.339 | 380469.4 | 2458.939 | 0.6463% | 432358 | -49429.661 | -11.43% | 1. The rating of all inverters are 122.14kW but they are limited to 85kW. | 1. SR101124
OR-23-C005 Solops SPI - Belvedere Solar | OR | 459857.485 | 485607.3 | -25749.815 | -5.303% | 546143 | -86285.515 | -15.8% | 1. All trackers were not communicating from 09/05 to end of the month. 2. Site was offline from 07:45 to 15:15 on 09/02. | 1. SR107723 2. SR107292 | SR107292
OR-23-C002 SPI - Cork Solar | OR | 237596.038 | 230234.2 | 7361.838 | 3.198% | 248127 | -10530.962 | -4.244%
OR: Oregon City - Buckner Creek - OR-23-C008 | OR | 237462.39 | 357689.4 | -120227.01 | -33.61% | 424314 | -186851.61 | -44.04% | 1. Inverter 16 was offline from 09:30 on 09/28 to 02:30 on 09/29. 2. Inverter 3 being offline for most of the days in month. 3. Inverter 11 started late on 09/06 at 10:00. 4. Meter was not capturing total inverter production for whole month. 5. Motor 28 through 40 was stuck. | 1. SR108693 2. SR108253 3. SR107549 4. SR107187 5. SR107186 | SR108253 | SR107549 | SR107187 | SR107186
OR: Dundee - Gun Club - OR-23-C009 | OR | 483722.546 | 514135 | -30412.454 | -5.915% | 538888.1 | -55165.554 | -10.24% | 1. Inverter 8 and 2 had heavy morning shading.
OR: Molalla - Marquam - OR-23-C010 | OR | 265955.061 | 284470.3 | -18515.239 | -6.509% | 394366 | -128410.939 | -32.56% | 1. Inverters was 10,14,15 are underperforming by 7kW, and inverters 1,3,8,12,13 are underperforming by 5kW for whole month. 2. All trackers were stuck for whole month. | 1. SR108553 2. SR108552 | SR108552

## Oct
Luminace |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC
Berkeley - NJ-22-C893 Berkeley I | NJ
Berkeley - NJ-22-C894 Berkeley II | NJ
BEMS Landfill East | NJ
Southampton - BEMS West NJ-22-C898 | NJ
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ
Lakewood Township - Public Works | NJ
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR

## Nov
Luminace |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC
Berkeley - NJ-22-C893 Berkeley I | NJ
Berkeley - NJ-22-C894 Berkeley II | NJ
BEMS Landfill East | NJ
Southampton - BEMS West NJ-22-C898 | NJ
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ
Lakewood Township - Public Works | NJ
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR

## Dec
Luminace |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC
Berkeley - NJ-22-C893 Berkeley I | NJ
Berkeley - NJ-22-C894 Berkeley II | NJ
BEMS Landfill East | NJ
Southampton - BEMS West NJ-22-C898 | NJ
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ
Lakewood Township - Public Works | NJ
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR

## Sites
Portfolio: | Luminace
Site DAS Name | Site | State | Update | DAS
DC-23-0001 - Raymond Elementary Redev | Raymond Ed Re-Development - DC-23-0001 | DC | AEF | PowerTrack
NJ-22-C893 - CS Energy - Berkeley I | Berkeley - NJ-22-C893 Berkeley I | NJ | AEF | PowerTrack
NJ-22-C894 - CS Energy - Berkeley II | Berkeley - NJ-22-C894 Berkeley II | NJ | AEF | PowerTrack
Southampton - BEMS East NJ-22-C897 | BEMS Landfill East | NJ |  | PowerTrack
NJ-22-C898 - BEMS Landfill West | Southampton - BEMS West NJ-22-C898 | NJ | AEF | PowerTrack
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ |  | PowerTrack
Lakewood Township - Public Works | Lakewood Township - Public Works | NJ |  | PowerTrack
OR-23-C003 Dover - SPI | Canby - Dover - OR-23-C003 | OR | AEF | PowerTrack
OR-23-C001 SPI - Clayfield Solar | Estacada - Clayfield - OR-23-C001 | OR | AEF | PowerTrack
SPI - Waterford Solar | Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR-23-C005 Solops SPI - Belvedere Solar | OR | AEF
Molalla - Cork - OR-23-C002 | OR-23-C002 SPI - Cork Solar | OR
OR-23-C008 Buckner Solar | OR: Oregon City - Buckner Creek - OR-23-C008 | OR |  | PowerTrack
OR-23-C009 Green Key Gun Club Solar | OR: Dundee - Gun Club - OR-23-C009 | OR |  | PowerTrack
OR-23-C010 Marquam Creek Solar | OR: Molalla - Marquam - OR-23-C010 | OR |  | PowerTrack