## Year to Date
MD: Frederick – NMWDA – Solar |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 1165294.243 | 0 | 1165294.243 | 0% | 0 | 1165294.243 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Frederick MD - NMWDA | MD | 1165294.243 | 0 | 1165294.243 |  | 0 | 0

## 1st Qtr
MD: Frederick – NMWDA – Solar |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 281549.994 | 0 | 281549.994 | 0% | 0 | 281549.994 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Frederick MD - NMWDA | MD | 281549.994 | 0 | 281549.994 |  | 0 | 0

## 2nd Qtr
MD: Frederick – NMWDA – Solar |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 439890.999 | 0 | 439890.999 | 0% | 0 | 439890.999 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Frederick MD - NMWDA | MD | 439890.999 | 0 | 439890.999 |  | 0 | 0

## 3rd Qtr
MD: Frederick – NMWDA – Solar |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 443853.25 | 0 | 443853.25 | 0% | 0 | 443853.25 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Frederick MD - NMWDA | MD | 443853.25 | 0 | 443853.25 |  | 0 | 0

## 4th Qtr
MD: Frederick – NMWDA – Solar |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Frederick MD - NMWDA | MD | 0 | 0 | 0 |  | 0 | 0

## Jan
MD: Frederick – NMWDA – Solar |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 48743.752 | 0 | 48743.752 | 0% | 0 | 48743.752 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Frederick MD - NMWDA | MD | 48743.752 | N/A |  |  | N/A |  |  | 1.Inverters 6,7,12 was offline on 01/03 and back online on 01/04. Inverter 6 was offline from 8AM to 16:15 on 01/13. 2.Inverter 12 was offline from 8:30 to 14:45 on 01/21. 3.Inverter 9 was offline from 9:45 to 17:00 on 01/25 and from 09:45 to 16:30 on 01/27. 4.Inverters 2, 3, 4, 5, 6, 9, 12, 13, 14, 15, and 16 went offline on 01/29 due to high voltages. On 01/30, the technician confirmed that inverters trip offline when voltage exceeds the set threshold and do not recover until it drops below 507.5 VAC. To prevent this, utility approval is needed to adjust the PV transformer tap changer and raise the inverters' recovery settings above 507V/105.8%. Inverters were brought back online. 5.Inverter 8 has been derating by 13 kW compared to its peers since 01/27. | 1.SR094253 2.SR095823 3.SR095974 4.SR096110 5.SR097660

## Feb
MD: Frederick – NMWDA – Solar |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 94278.342 | 0 | 94278.342 | 0% | 0 | 94278.342 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Frederick MD - NMWDA | MD | 94278.342 | N/A |  |  | N/A |  |  | 1.Inverter 6 was offline at 14:00 on 02/03 due to isolation faults caused by water and ice in the flex conduit, damaging string 13+ and string 12- wires. On 02/11, the technician replaced the damaged leads, reattached the conduit, torqued all connections, and sealed PVC fittings to prevent future issues. Inverter 6 was back online and producing normally. 2.Inverter 14 was tripped offline from 02/23 at 9:45 and through out the month. 3.Inverter 8 has been derating by 13 kW compared to its peers since 01/27. | 1.SR096110 2.SR097656 3.SR097660 | SR097656 | SR097660

## Mar
MD: Frederick – NMWDA – Solar |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 138527.9 | 0 | 138527.9 | 0% | 0 | 138527.9 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Frederick MD - NMWDA | MD | 138527.9 | N/A |  |  | N/A |  |  | 1.Inverter 14 tripped offline on 02/23 at 9:45 AM and came back online on 03/02. However, it tripped offline again at 11:00 AM on the same day. On 03/05, the technician identified thermal damage to the wire box, and a case was created for RMA. The inverter was brought back online on 03/25 at 12:00 PM after the technician replaced the damaged section of PV wire and MC4 connectors. 2.Inverter 8 has been derating by 13 kW compared to its peers since 01/27 technician has isolated string 10 due to ground fault on 03/05 later technician has replaced the PV wire section on 03/25. 3. Inverter 7 tripped offline on 03/03 at 08:45am and self resolved at 11:00 on 03/05 4. Inverter 7 has a string down from 03/12 later technician was able to troubleshoot the MPPT zones adjusted with assistance from Solectria on 03/25. 5.Inverters 4,6,12,13 & 16 has started late for the production at 13:30 on 03/29 & 03/30 6.Inverter 8 underperforming by 11 kW on high irradiance days. | 1.SR097656 2.SR097660 3.SR097991 4.SR098473 5.SR099131 6.SR099142 | SR097660 | SR097991 | SR098473 | SR099131 | SR099142

## Apr
MD: Frederick – NMWDA – Solar |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 135719.046 | 0 | 135719.046 | 0% | 0 | 135719.046 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Frederick MD - NMWDA | MD | 135719.046 | N/A |  |  | N/A |  |  | 1. Inverter 8 underperforming by 11 kW on high irradiance days. 2. Inverter 8 tripped offline at 14:00 on 04/04, and Inverter 7 tripped offline at 09:30 on 04/10. Inverter 8 came back online at 10:30 on 04/25, but Inverter 7 remained offline for the rest of the month. 3. Site production was low on 04/28 because a technician was on site for preventive maintenance. | 1. SR099142 2. SR099142 3. PM9146 | SR099142

## May
MD: Frederick – NMWDA – Solar |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 146820.998 | 0 | 146820.998 | 0% | 0 | 146820.998 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Frederick MD - NMWDA | MD | 146820.998 | N/A |  |  | N/A |  |  | 1. Inverter 8 tripped offline at 16:30 on 05/06 and came back online at 08:45 on 05/12. Inverter 7 was offline from 09:30 on 04/10 and came back online at 09:00 on 05/12. 2. Inverter 8 tripped offline at 12:15 on 05/23 and remained offline throughout the month. 3. Inverters 7 and 12 started production late at 11:45 on 05/31. 4. Inverter 4 has been intermittently underperforming by up to 30 kW since 05/23. | 1. SR099142 2. SR101900 3. SR102216 4. SR101904 | SR101900 | SR102216 | SR101904

## Jun
MD: Frederick – NMWDA – Solar |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 157350.955 | 0 | 157350.955 | 0% | 0 | 157350.955 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Frederick MD - NMWDA | MD | 157350.955 | N/A |  |  | N/A |  |  | 1. Inverter 4 has been intermittently underperforming by up to 30 kW since 05/23 and was also offline on 06/15. 2. Inverter 8 was offline from 12:15 on 05/23 and came back online at 09:30 on 06/13. It tripped offline again at 12:30 on 06/23 and has remained offline since then. 3. Inverter 14 has been underperforming by approximately 23–24 kW since 13:45 on 06/23. | 1. SR101904 2. SR101900 3. SR103355 | SR101900 | SR103355

## Jul
MD: Frederick – NMWDA – Solar |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 162025.7 | 0 | 162025.7 | 0% | 0 | 162025.7 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Frederick MD - NMWDA | MD | 162025.7 | N/A |  |  | N/A |  |  | 1. Inverter 8 is back online at 10:30 on 07/31 2.Inverter 4 is consistently tripping early in the morning then recovering in the afternoon through out the month. 3.Inverter 15 has been reporting normally since 7/17. | 1.SR101900 2.SR101904 3.SR104536 | SR101904 | SR104536

## Aug
MD: Frederick – NMWDA – Solar |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 154206.95 | 0 | 154206.95 | 0% | 0 | 154206.95 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Frederick MD - NMWDA | MD | 154206.95 | N/A |  |  | N/A |  |  | 1. Inverter 8 is tripped offline at 12:15 on 08/28. 2.Inverter 4 was offline for most of the days in the month. | 1.SR107095 2.SR101904 | SR101904

## Sep
MD: Frederick – NMWDA – Solar |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 127620.6 | 0 | 127620.6 | 0% | 0 | 127620.6 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Frederick MD - NMWDA | MD | 127620.6 | N/A |  |  | N/A |  |  | 1.Inverter 8 was offline from 09/01 to 08:53 on 09/04 2.Inverter 8 tripped offline at 10:15AM on 09/08 and back online on 09/09. 3.Inverter 4 was offline for most of the days in the month. | 1.SR107095 2.SR107615 3.SR101904 | SR107615 | SR101904

## Oct
MD: Frederick – NMWDA – Solar |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Frederick MD - NMWDA | MD

## Nov
MD: Frederick – NMWDA – Solar |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Frederick MD - NMWDA | MD

## Dec
MD: Frederick – NMWDA – Solar |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Frederick MD - NMWDA | MD

## Sites
Portfolio: | MD: Frederick – NMWDA – Solar
Site DAS Name | Site | State | Update | DAS
Frederick MD - NMWDA | Frederick MD - NMWDA | MD |  | InAccess