## Year to Date
MS Walker |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 340938.8348 | 0 | 340938.8348 | 0% | 0 | 340938.8348 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: MS Walker | MA | 340938.8348 | 0 | 340938.8348 |  | 0 | 263082.23

## 1st Qtr
MS Walker |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 121978.828 | 0 | 121978.828 | 0% | 0 | 121978.828 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: MS Walker | MA | 121978.828 | 0 | 121978.828 |  | 0 | 121978.828

## 2nd Qtr
MS Walker |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 174443.772 | 0 | 174443.772 | 0% | 0 | 174443.772 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: MS Walker | MA | 174443.772 | 0 | 174443.772 |  | 0 | 141103.402

## 3rd Qtr
MS Walker |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 44516.2348 | 0 | 44516.2348 | 0% | 0 | 44516.2348 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: MS Walker | MA | 44516.2348 | 0 | 44516.2348 |  | 0 | 0

## 4th Qtr
MS Walker |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: MS Walker | MA | 0 | 0 | 0 |  | 0 | 0

## Jan
MS Walker |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 29177.128 | 0 | 29177.128 | 0% | 0 | 29177.128 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: MS Walker | MA | 29177.128 | 0 | 29177.128 |  | 0 | 29177.128

## Feb
MS Walker |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 27473.4 | 0 | 27473.4 | 0% | 0 | 27473.4 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: MS Walker | MA | 27473.4 | 0 | 27473.4 |  | 0 | 27473.4

## Mar
MS Walker |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 65328.3 | 0 | 65328.3 | 0% | 0 | 65328.3 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: MS Walker | MA | 65328.3 | 0 | 65328.3 |  | 0 | 65328.3 |  | 1.The site was offline from 07:45 AM to 02:03 PM on 03/14. MS Walker technicians re-energized the site by closing the recloser 2.Inverter 17 is underperforming by approximately 4 kW, possibly due to a string being down, when compared to Inverters 16 and 15 | 1.SR098583 2.SR098784

## Apr
MS Walker |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 79195 | 0 | 79195 | 0% | 0 | 79195 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: MS Walker | MA | 79195 | N/A |  |  | 0 | 79195 |  | 1.Inverter 17 is underperforming approximately 4kW,possibly string down from 03/14 at 14:30 when compared to Inv 16 &15 which are of same strings. | 1.SR098784

## May
MS Walker |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 61908.402 | 0 | 61908.402 | 0% | 0 | 61908.402 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: MS Walker | MA | 61908.402 | 0 | 61908.402 |  | 0 | 61908.402 |  | 1.Inverter 17 is underperforming approximately 4kW,possibly string down from 03/14 at 14:30 when compared to Inv 16 &15 which are of same strings. 2.Site was offline from 12:30 on 05/03 to 12:45 on 05/07 Site was offline from 15:15 on 05/16 to 06:30 on 05/19 Site was offline from 12:45 on 05/27 to 08:15 on 05/28. The site was back online after customer closed the recloser.Site was offline due to persistent communication failures with the DAS. The issue is currently under troubleshooting | 1.SR098784 2.SR100966 | SR100966

## Jun
MS Walker |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 33340.37 | 0 | 33340.37 | 0% | 0 | 33340.37 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: MS Walker | MA | 33340.37 | N/A |  |  | N/A |  |  | 1.Site was offline almost for whole month due to persistent communication failures with the DAS. The issue is currently under troubleshooting and Tavrida is being RMA'd. | 1.SR103715

## Jul
MS Walker |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 1048.7 | 0 | 1048.7 | 0% | 0 | 1048.7 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: MS Walker | MA | 1048.7 | N/A |  |  | N/A |  |  | 1. Site was offline almost for whole month and is back online at 14:15 on 07/30 | 1.SR103715

## Aug
MS Walker |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 43467.5348 | 0 | 43467.5348 | 0% | 0 | 43467.5348 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: MS Walker | MA | 43467.5348 | N/A |  |  | N/A |  |  | 1. Site was not communicated from 17:45 on 08/15 to till date | 1. SR106454

## Sep
MS Walker |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: MS Walker | MA | 0 | N/A |  |  | N/A |  |  | 1. Site was not communicated for whole month. | 1. SR106454

## Oct
MS Walker |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: MS Walker | MA

## Nov
MS Walker |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: MS Walker | MA

## Dec
MS Walker |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: MS Walker | MA

## Sites
Portfolio: | MS Walker
Site DAS Name | Site | State | Update | DAS
MS Walker | MA: MS Walker | MA |  | InAccess