## Year to Date
Northbridge Companies |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 316972.4 | 157761.724 | 159210.676 | 100.9% | 226133.862 | 90838.538 | 40.17%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 80923.4 | 0 | 80923.4 |  | 0 | 0 | 0%
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 236049 | 157761.724 | 78287.276 | 49.62% | 226133.862 | 9915.138 | 4.385%

## 1st Qtr
Northbridge Companies |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 118219.085 | 79193.593 | 39025.492 | 49.28% | 51994.465 | 66224.62 | 127.4%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 62466.96 | 0 | 62466.96 |  | 0 | 0 | 0%
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 55752.125 | 79193.593 | -23441.468 | -29.6% | 51994.465 | 3757.66 | 7.227%

## 2nd Qtr
Northbridge Companies |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 106640.815 | 34396.06 | 72244.755 | 210% | 89142.738 | 17498.077 | 19.63%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 18456.44 | 0 | 18456.44 |  | 0 | 0
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 88184.375 | 34396.06 | 53788.315 | 156.4% | 89142.738 | -958.363 | -1.075%

## 3rd Qtr
Northbridge Companies |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 92112.5 | 44172.071 | 47940.429 | 108.5% | 84996.659 | 7115.841 | 8.372%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 0 | 0 | 0 |  | 0 | 0
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 92112.5 | 44172.071 | 47940.429 | 108.5% | 84996.659 | 7115.841 | 8.372%

## 4th Qtr
Northbridge Companies |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 0 | 0 | 0 |  | 0 | 0
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 0 | 0 | 0 |  | 0 | 0

## Jan
Northbridge Companies |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 32240.375 | 23990.493 | 8249.882 | 34.39% | 13578.087 | 18662.288 | 137.4%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 17790 | N/A |  |  | N/A
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 14450.375 | 23990.493 | -9540.118 | -39.77% | 13578.087 | 872.288 | 6.424% | 1.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. | 1.SR094280

## Feb
Northbridge Companies |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 35400.51 | 31450.165 | 3950.345 | 12.56% | 16170.202 | 19230.308 | 118.9%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 19120.26 | N/A |  |  | N/A
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 16280.25 | 31450.165 | -15169.915 | -48.23% | 16170.202 | 110.048 | 0.6806% | 1. Inverter 2.3 has tripped offline at 09:00AM on 02/12 reporting Insulation Resistance Low and back online at 06:30AM on 02/14 and On 02/28 started late for production at 01:15PM. 2.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. | 1.SR096732 2.SR094280 | SR094280

## Mar
Northbridge Companies |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 50578.2 | 23752.935 | 26825.265 | 112.9% | 22246.176 | 28332.024 | 127.4%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 25556.7 | N/A |  |  | N/A
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 25021.5 | 23752.935 | 1268.565 | 5.341% | 22246.176 | 2775.324 | 12.48% | 1.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. | 1.SR094280

## Apr
Northbridge Companies |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 46001.065 | 13297.438 | 32703.627 | 245.9% | 26440.769 | 19560.296 | 73.98%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 18456.44 | N/A |  |  | N/A |  |  | 1.Site tripped offline at 12:15 on 04/23,meter voltages were abnormal,techician checked in and found that site is running and producing without communication due to faulty step down transformer. | 1.SR100216
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 27544.625 | 13297.438 | 14247.187 | 107.1% | 26440.769 | 1103.856 | 4.175% | 1.Inverter 2.3 didn't start for production reporting "Insulation resistance low" and was back online at 12:44 on 04/22. 2.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. | 1.SR098622 2.SR094280 | SR094280

## May
Northbridge Companies |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 29245.125 | 13831.293 | 15413.832 | 111.4% | 30978.309 | -1733.184 | -5.595%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site was not communicated for whole month due to a damaged transformer affecting communications. | 1.SR100216
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 29245.125 | 13831.293 | 15413.832 | 111.4% | 30978.309 | -1733.184 | -5.595% | 1.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. | 1. SR094280

## Jun
Northbridge Companies |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 31394.625 | 7267.329 | 24127.296 | 332% | 31723.66 | -329.035 | -1.037%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site was not communicated for whole month due to a damaged transformer affecting communications. | 1.SR100216
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 31394.625 | 7267.329 | 24127.296 | 332% | 31723.66 | -329.035 | -1.037% | 1.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. | 1.SR094280

## Jul
Northbridge Companies |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 32655.625 | 12807.285 | 19848.34 | 155% | 30863.213 | 1792.412 | 5.808%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site was not communicated for whole month due to a damaged transformer affecting communications. | 1.SR100216
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 32655.625 | 12807.285 | 19848.34 | 155% | 30863.213 | 1792.412 | 5.808% | 1.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. | 1.SR094280

## Aug
Northbridge Companies |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 34330.125 | 14682.458 | 19647.667 | 133.8% | 29110 | 5220.125 | 17.93%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site was not communicated for whole month due to a damaged transformer affecting communications. | 1.SR100216
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 34330.125 | 14682.458 | 19647.667 | 133.8% | 29110 | 5220.125 | 17.93% | 1.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. | 1.SR094280

## Sep
Northbridge Companies |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 25126.75 | 16682.328 | 8444.422 | 50.62% | 25023.446 | 103.304 | 0.4128%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site was not communicated for whole month due to a damaged transformer affecting communications. | 1. SR100216
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 25126.75 | 16682.328 | 8444.422 | 50.62% | 25023.446 | 103.304 | 0.4128% | 1.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. | 1. SR094280

## Oct
Northbridge Companies |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA
MA: North Dartmouth - 293 Cross St (Array 2) | MA

## Nov
Northbridge Companies |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA
MA: North Dartmouth - 293 Cross St (Array 2) | MA

## Dec
Northbridge Companies |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA |  | 0
MA: North Dartmouth - 293 Cross St (Array 2) | MA

## Sites
Portfolio: | Northbridge Companies
Site DAS Name | Site | State | Update | DAS
MA - Northbridge Array 1 | MA: North Dartmouth - 293 Cross St (Array 1) | MA |  | Inaccess
Northbridge Array 2 | MA: North Dartmouth - 293 Cross St (Array 2) | MA |  | PowerTrack