## Year to Date
RINGS END |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 208818.1121 | 0 | 208818.1121 | 0% | 226396.408 | -17578.2959 | -7.764%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Branford - Rings End | CT | 99320.2126 | 0 | 99320.2126 |  | 106187.511 | -6867.2984 | -6.467%
Milford - Rings End | CT | 62510.737 | 0 | 62510.737 |  | 56221.521 | -557.015 | -0.9908%
New Milford - Rings End | CT | 46987.1625 | 0 | 46987.1625 |  | 63987.376 | -4010.4575 | -6.268%

## 1st Qtr
RINGS END |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 48284.3275 | 0 | 48284.3275 | 0% | 53385.403 | -5101.0755 | -9.555%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Branford - Rings End | CT | 25250.7 | 0 | 25250.7 |  | 25784.303 | -533.603 | -2.069%
Milford - Rings End | CT | 13111.985 | 0 | 13111.985 |  | 13669 | -557.015 | -4.075%
New Milford - Rings End | CT | 9921.6425 | 0 | 9921.6425 |  | 13932.1 | -4010.4575 | -28.79%

## 2nd Qtr
RINGS END |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 83226.577 | 0 | 83226.577 | 0% | 89722.074 | -6495.497 | -7.24%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Branford - Rings End | CT | 39086.13 | 0 | 39086.13 |  | 41799.621 | -2713.491 | -6.492%
Milford - Rings End | CT | 26162.9695 | 0 | 26162.9695 |  | 21705.121 | 4457.8485 | 20.54%
New Milford - Rings End | CT | 17977.4775 | 0 | 17977.4775 |  | 26217.332 | -8239.8545 | -31.43%

## 3rd Qtr
RINGS END |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 77307.2076 | 0 | 77307.2076 | 0% | 83288.931 | -5981.7234 | -7.182%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Branford - Rings End | CT | 34983.3826 | 0 | 34983.3826 |  | 38603.587 | -3620.2044 | -9.378%
Milford - Rings End | CT | 23235.7825 | 0 | 23235.7825 |  | 20847.4 | 2388.3825 | 11.46%
New Milford - Rings End | CT | 19088.0426 | 0 | 19088.0426 |  | 23837.944 | -4749.9014 | -19.93%

## 4th Qtr
RINGS END |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Branford - Rings End | CT | 0 | 0 | 0 |  | 0 | 0
Milford - Rings End | CT | 0 | 0 | 0 |  | 0 | 0
New Milford - Rings End | CT | 0 | 0 | 0 |  | 0 | 0

## Jan
RINGS END |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 12740.6425 | 0 | 12740.6425 | 0% | 12946.1 | -205.4575 | -1.587%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Rings End | CT | 6650.53 | N/A |  |  | 6291.7 | 358.83 | 5.703% | 1.Low generation due to weather/snow on 01/20 , 01/21
Milford - Rings End | CT | 3552.22 | N/A |  |  | 3298 | 254.22 | 7.708% | 1. Inverter 2 tripped offline at 08:45 AM on 01/18/25. On 01/23/25, the technician performed a reset inhibition and brought it back online at 09:30. 2. Inverter 1 & 2 are offline from 01/29/25 due to an ARC fault and remained offline through the month. 3. Low generation due to weather/snow on 01/21 ,01/22 | 1. SR095695 2. SR096102 | SR096102
New Milford - Rings End | CT | 2537.8925 | N/A |  |  | 3356.4 | -818.5075 | -24.39% | 1. Inverter 2 was underperforming approximately 18kW compared to peer as Strings 2.2 and 2.3 have been disconnected from 09/03 for further troubleshooting. 2. Low generation due to weather/snow 01/06 ,01/31 | 1. SR088902

## Feb
RINGS END |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 11728.335 | 0 | 11728.335 | 0% | 16349.5 | -4621.165 | -28.26%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Rings End | CT | 6751.05 | N/A |  |  | 7839.8 | -1088.75 | -13.89% | 1. Site was offline from 13:00 on 02/03/25 and came back online at 14:15 on 02/05/25, after the technician re-energized it. 2. Low generation due to weather/snow on 02/09 to 02/13 | 1. SR096277
Milford - Rings End | CT | 2518.835 | N/A |  |  | 4205 | -1686.165 | -40.1% | 1. Inverter 1 & 2 back online at 10:15 on 02/25/25, after the technician re-energized them. 2. Low generation due to weather/snow on 02/09 to 02/13 | 1. SR096102
New Milford - Rings End | CT | 2458.45 | N/A |  |  | 4304.7 | -1846.25 | -42.89% | 1. Inverter 2 was underperforming approximately 18kW compared to peer as Strings 2.2 and 2.3 have been disconnected from 09/03 for further troubleshooting. 2. Low generation due to weather/snow on 02/09 to 02/13 | 1. SR088902

## Mar
RINGS END |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 23815.35 | 0 | 23815.35 | 0% | 24089.803 | -274.453 | -1.139%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Rings End | CT | 11849.12 | N/A |  |  | 11652.803 | 196.317 | 1.685% | 1.Low generation due to weather/snow on 03/24
Milford - Rings End | CT | 7040.93 | N/A |  |  | 6166 | 874.93 | 14.19% | 1.Inverter 1 was offline from 03/06 and remained offline for rest of the month 2.Low generation due to weather/snow on 03/24 | 1.SR098202
New Milford - Rings End | CT | 4925.3 | N/A |  |  | 6271 | -1345.7 | -21.46% | 1. Inverter 2 was underperforming by approximately 18 kW compared to its peer, as Strings 2.2 and 2.3 have been disconnected since 09/03/24 for further troubleshooting. Four optimizers required to repair Strings 2.2 and 2.3 have been RMAd from 10/30/24 2.Inverter 1 intermittently tripped on 03/25 due to high voltage on Line 3. The issue self-resolved on 03/26. 3.Low generation due to weather/snow on 03/24 | 1.SR088902 2.SR098985 | SR098985

## Apr
RINGS END |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 29485.587 | 0 | 29485.587 | 0% | 27323.733 | 2161.854 | 7.912%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Rings End | CT | 12913.49 | 0 |  |  | 12686.516 | 226.974 | 1.789%
Milford - Rings End | CT | 10560.202 | 0 | 10560.202 |  | 6762.382 | 3797.82 | 56.16% | 1.Inverter 1 was offline from 04/01 to 04/09 .Inverter 1 is back online at 10:15 after technician has reset inverter | 1.SR098202
New Milford - Rings End | CT | 6011.895 | 0 | 6011.895 |  | 7874.835 | -1862.94 | -23.66% | 1.Inverter 2 was underperforming by approximately 18 kW compared to its peers. Four optimizers required to repair Strings 2.2 and 2.3 have been RMAd from 10/30/24.Issue resolved on 04/10 after technician has troubleshoot the optimizers | 1.SR088902

## May
RINGS END |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 28177.485 | 0 | 28177.485 | 0% | 31023.923 | -2846.438 | -9.175%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Rings End | CT | 12453.97 | 0 | 12453.97 |  | 14490.436 | -2036.466 | -14.05% | 1.Low generation due to rain on 05/05,05/09,05/21,05/22.
Milford - Rings End | CT | 9999.025 | 0 | 9999.025 |  | 7403.948 | 2595.077 | 35.05% | 1.Low generation due to rain on 05/04,05/09,05/21,05/22.
New Milford - Rings End | CT | 5724.49 | 0 | 5724.49 |  | 9129.539 | -3405.049 | -37.3% | 1.Inverter 2 is underperming approximately 22kw compared to its peer inverter string 2.2 was Rma'd from 10/30/24 | 1. SR088902

## Jun
RINGS END |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 25563.505 | 0 | 25563.505 | 0% | 31374.418 | -5810.913 | -18.52%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Rings End | CT | 13718.67 | 0 | 13718.67 |  | 14622.669 | -903.999 | -6.182%
Milford - Rings End | CT | 5603.7425 | 0 | 5603.7425 |  | 7538.791 | -1935.0485 | -25.67% | 1.Inverters 1,2&3 were offline through out the month due to "High Residual Current". | 1.SR103735,SR096102 | SR096102
New Milford - Rings End | CT | 6241.0925 | 0 | 6241.0925 |  | 9212.958 | -2971.8655 | -32.26% | 1.Inverter 2 is underperming approximately 22kw compared to its peer inverter, Strings 2.2 and 2.3 have been disconnected from 09/03 for further troubleshooting and 4 P700 optimizers are needed to repair the strings. | 1.SR088902

## Jul
RINGS END |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 15569.9276 | 0 | 15569.9276 | 0% | 31253.227 | -15683.2994 | -50.18%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Rings End | CT | 14923.87 | N/A |  |  | 14237.642 | -7283.3394 | -51.16% | The pant is performing as expected. The forecasted (theoretical) values appear lower and they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance
Milford - Rings End | CT | 8615.625 | N/A |  |  | 7841 | 774.625 | 9.879% | 1.Inverter 2 had been offline since 06/28. | 1.SR107540,SR096102 | SR096102
New Milford - Rings End | CT | 6954.3026 | N/A |  |  | 9174.585 | -2220.2824 | -24.2% | 1.Inverter 2 is underperming approximately 22kw compared to its peer inverter string 2.2 was Rma'd from 10/30/24 | 1.SR088902

## Aug
RINGS END |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 30767.1275 | 0 | 30767.1275 | 0% | 28684.704 | 2082.4235 | 7.26%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Rings End | CT | 15627.18 | N/A |  |  | 13198.745 | 2428.435 | 18.4%
Milford - Rings End | CT | 8258.1975 | N/A |  |  | 7282 | 976.1975 | 13.41% | 1.Inverter 2 had been offline since 06/28. | 1.SR107540,SR096102 | SR096102
New Milford - Rings End | CT | 6881.75 | N/A |  |  | 8203.959 | -1322.209 | -16.12% | 1.Inverter 2 is underperming approximately 22kw compared to its peer inverter string 2.2 was Rma'd from 10/30/24 | 1.SR088902

## Sep
RINGS END |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 24015.85 | 0 | 24015.85 | 0% | 23351 | 664.85 | 2.847%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Rings End | CT | 12401.9 | N/A |  |  | 11167.2 | 1234.7 | 11.06%
Milford - Rings End | CT | 6361.96 | N/A |  |  | 5724.4 | 637.56 | 11.14% | 1.Inverter 2 had been offline since 06/28. | 1.SR107540,SR096102 | SR096102
New Milford - Rings End | CT | 5251.99 | N/A |  |  | 6459.4 | -1207.41 | -18.69% | 1.Inverter 2 is underperming approximately 22kw compared to its peer inverter string 2.2 was Rma'd from 10/30/24 | 1.SR088902

## Oct
RINGS END |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Rings End | CT |  | 0
Milford - Rings End | CT |  | 0
New Milford - Rings End | CT |  | 0

## Nov
RINGS END |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Rings End | CT |  | 0
Milford - Rings End | CT |  | 0
New Milford - Rings End | CT |  | 0

## Dec
RINGS END |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Rings End | CT |  | 0
Milford - Rings End | CT |  | 0
New Milford - Rings End | CT |  | 0

## Sites
Portfolio: | RINGS END
Site DAS Name | Site | State | Update | DAS
Ring's End - Branford Store | Branford - Rings End | CT | AF | PowerTrack
Ring's End - Milford | Milford - Rings End | CT | AF | PowerTrack
Ring's End - New Milford | New Milford - Rings End | CT | A | PowerTrack