## Year to Date
Valmont Industries |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 519202.377 | 475098.189 | 44104.188 | 9.283% | 279873.354 | 239329.023 | 85.51%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Valmont | IN | 519202.377 | 475098.189 | 44104.188 | 9.283% | 279873.354 | -167314.484 | -59.78%

## 1st Qtr
Valmont Industries |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 150698.188 | 112449.57 | 38248.618 | 34.01% | 0 | 150698.188 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Valmont | IN | 150698.188 | 112449.57 | 38248.618 | 34.01% | 0 | 0

## 2nd Qtr
Valmont Industries |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 229406.063 | 197246.691 | 32159.372 | 16.3% | 279873.354 | -50467.291 | -18.03%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Valmont | IN | 229406.063 | 197246.691 | 32159.372 | 16.3% | 279873.354 | -36644.916 | -13.09%

## 3rd Qtr
Valmont Industries |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 139098.126 | 165401.928 | -26303.802 | -15.9% | 0 | 139098.126 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Valmont | IN | 139098.126 | 165401.928 | -26303.802 | -15.9% |  | -130669.568

## 4th Qtr
Valmont Industries |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Valmont | IN | 0 | 0 | 0 |  |  | 0

## Jan
Valmont Industries |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 26968.676 | 22909.665 | 4059.011 | 17.72% | 0 | 26968.676 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN | 26968.676 | 22909.665 | 4059.011 | 17.72% | N/A |  |  | 1.All trackers were stuck since 12/19/24. | 1.SR092973

## Feb
Valmont Industries |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 41511.574 | 30572.197 | 10939.377 | 35.78% | 0 | 41511.574 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN | 41511.574 | 30572.197 | 10939.377 | 35.78% | N/A |  |  | 1.All trackers were stuck since 12/19/24. | 1.SR092973

## Mar
Valmont Industries |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 82217.938 | 58967.708 | 23250.23 | 39.43% | 0 | 82217.938 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN | 82217.938 | 58967.708 | 23250.23 | 39.43% | N/A |  |  | 1.Inverter 2 tripped offline at 16:00 on 03/02 due to Grid Line Voltage Out of Range and back online at 8:45AM on 03/03. Again tripped offline from 12:00PM to 12:45PM on 03/11 due to Grid Line Voltage Out of Range. 2.Site tripped offline at 17:00 on 03/30 due to storm and remained offline whole month. 3.All trackers were stuck since 12/19/24 and Volmont site team working on trackers. | 1.SR097973 2.SR099153 3.SR092973 | SR099153 | SR092973

## Apr
Valmont Industries |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 71050.125 | 53448.026 | 17602.099 | 32.93% | 84872.5 | -13822.375 | -16.29%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN | 71050.125 | 53448.026 | 17602.099 | 32.93% | 84872.5 |  | 0% | 1. The site tripped offline at 17:00 on 03/30 and came back online at 14:15 on 04/07. 2. Inverter 4 tripped offline at 17:30 on 04/29 due to a 'Grid Line Voltage Out of Range' error. A technician was on-site on 04/30 and swapped the powerheads of Inverter 3 and Inverter 4 to check if the fault reoccurs. The inverter came back online at 09:00 on 04/30. 3. All trackers are not tracking. | 1. SR099153 2. SR100671 3. SR099992 | SR100671 | SR099992

## May
Valmont Industries |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 84285.875 | 69529.908 | 14755.967 | 21.22% | 96105.854 | -11819.979 | -12.3%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN | 84285.875 | 69529.908 | 14755.967 | 21.22% | 96105.854 | -11819.979 | -12.3% | 1. Inverter 2 tripped offline at 11:30 on 05/15 due to "Grid Line Voltage Out of Range - GridV.OutLim". A technician was on-site on 05/16 and reset the inverter, which came back online at 13:00 on 05/16. The inverter tripped offline again at 16:00 on 05/19. 2. Inverter 4 tripped offline at 16:00 on 05/15 due to "Grid Line Voltage Out of Range - GridV.OutLim", came back online at 12:00 on 05/16, and is currently being RMA’d. 3. All trackers are not tracking. | 1. SR101477 2. SR101551 3. SR099992 | SR101551 | SR099992

## Jun
Valmont Industries |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 74070.063 | 74268.757 | -198.694 | -0.2675% | 98895 | -24824.937 | -25.1%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN | 74070.063 | 74268.757 | -198.694 | -0.2675% | 98895 | -24824.937 | -25.1% | 1. Inverter 2 tripped offline at 16:00 from 05/19. inverter came back online on 06/06. And again inverter 2 tripped offline again 12:30 on 06/08 . Inverter was offline from 13:00 on 06/08 to 07:00 on 06/11 and again inverter was offline from 14:00 on 06/12 to 12:00 on 06/16 multiple days trough out the month 2.The site tripped offline from 15:45 to 16:15 on 06/20 due to a technician working on Inverter 2 3. Inverter 3 tripped offline from 13:45 on 06/21 to end of the month and reporting "Grid Line Voltage Out of Range - GridV.OutLim" 4.Inverter 4 tripped offline from 16:45 on 06/25 to end of the month and reporting "Grid Line Voltage Out of Range - GridV.OutLim". 5. All trackers are not tracking. | 1.SR101477 2.SR101551 3. SR103258 4.SR103554 5. SR099992 | SR101551 | SR103258 | SR103554 | SR099992

## Jul
Valmont Industries |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 57409.25 | 73218.471 | -15809.221 | -21.59% | 100560.774 | -43151.524 | -42.91%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN | 57409.25 | 73218.471 | -15809.221 | -21.59% | 100560.774 | -43151.524 | -42.91% | 1. Inverter 3 tripped offline from 13:45 on 06/21 to end of the month and reporting "Grid Line Voltage Out of Range - GridV.OutLim" 2.Inverter 4 tripped offline from 16:45 on 06/25 to end of the month and reporting "Grid Line Voltage Out of Range - GridV.OutLim". 3.All trackers are not tracking from 04/18 | 1.SR103258 2.SR103554 3.SR099992 | SR103554 | SR099992

## Aug
Valmont Industries |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 66772.313 | 71299.581 | -4527.268 | -6.35% | 92052.42 | -25280.107 | -27.46%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN | 66772.313 | 71299.581 | -4527.268 | -6.35% | 92052.42 | -25280.107 | -27.46% | 1. Inverter 3 was back online at 15:15 on 08/05 2. Inverter 4 is back online at 15:15 on 08/05 3.Inverter 3 tripped offline at 16:00 on 08/06 and back online at 15:45 on 08/26, while tech on site the site was offline from 11:00 to 15:45 4.Site tripped offline at 16:45 on 08/27 and back online at 13:30 on 08/28. Again site tripped offline at 14:45 on 08/30. 5.All trackers are not tracking from 04/18. On 08/27 tech replaced the ethernet cable but not connected rained out. | 1.SR103258 2.SR103554 3.SR105771 4.SR107052 5.SR099992 | SR103554 | SR105771 | SR107052 | SR099992

## Sep
Valmont Industries |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 14916.563 | 20883.876 | -5967.313 | -28.57% | 77154.5 | -62237.937 | -80.67%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN | 14916.563 | 20883.876 | -5967.313 | -28.57% | 77154.5 | -62237.937 | -80.67% | 1. Site was back online at 09/02 at 12:30 2.Site tripped offline at 13:25 on 09/04 and back online at 04:30am on 09/05. 3.Site tripped offline on 09/06 at 12:15 and back online at 11:00 on 09/09 4. Site tripped offline on 09/10 at 14:45 and back online at 12:00 on 09/30 | 1.SR107052 2.SR107447 3.SR107555 4.SR107782 | SR107447 | SR107555 | SR107782

## Oct
Valmont Industries |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN |  |  |  |  | 0

## Nov
Valmont Industries |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN |  |  |  |  | 0 |  |  | 1. Inverter 4 is underperforming by 6kW from 11/02 due to stuck tracker. 2. Site tripped offline at 05:15 AM and back online at 06:00 AM on 11/25 due to utility outage. 3. Forecasted data is not available.

## Dec
Valmont Industries |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN |  |  |  |  | 0

## Sites
Portfolio: | Valmont Industries
Site DAS Name | Site | State | Update | DAS
Valmont Bristol | Valmont | IN |  | PowerTrack