## Year to Date
Generate Capital |  |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  |  | 15338370.7232 | 12898958.885 | 2439411.8382 | 18.91% | 21017476.3131 | -5679105.59 | -27.02%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | %
K026 | NY | SOL-10356 | 8328.108 | 12159.88 | -3831.772 | -31.51% | 11055.95 | -2727.842 | -24.67%
K041 | NY | SOL-10357 | 5871.5312 | 9407.467 | -3535.9358 | -37.59% | 9924 | -4052.4688 | -40.84%
K043 | NY | SOL-10358 | 7527.0625 | 10861.06 | -3333.9975 | -30.7% | 2303 | 5224.0625 | 226.8%
K058 | NY | SOL-10360 | 5490.6875 | 8437.168 | -2946.4805 | -34.92% | 9101.326 | -3610.6385 | -39.67%
K115 | NY | SOL-10361 | 3483.875 | 7300.807 | -3816.932 | -52.28% | 5565.882 | -2082.007 | -37.41%
K152 | NY | SOL-10362 | 2067.4375 | 4344.89 | -2277.4525 | -52.42% | 3567 | -1499.5625 | -42.04%
K166 | NY | SOL-10363 | 7527.75 | 16102.59 | -8574.84 | -53.25% | 12064.56 | -4536.81 | -37.6%
K206 | NY | SOL-10927 | 5243.875 | 5255.242 | -11.367 | -0.2163% | 6894 | -1650.125 | -23.94%
K251 | NY | SOL-10365 | 5285.5625 | 0 | 5285.5625 |  | 8483.094 | -3197.5315 | -37.69%
K269 | NY | SOL-10366 | 4482.4375 | 7734.486 | -3252.0485 | -42.05% | 7723.149 | -3240.7115 | -41.96%
K273 | NY | SOL-10367 | 4816.2673 | 0 | 4816.2673 |  | 9546 | -4729.7327 | -49.55%
K287 | NY | SOL-10919 | 4113.1875 | 5386.828 | -1273.6405 | -23.64% | 7303 | -3189.8125 | -43.68%
K298 | NY | SOL-10368 | 3551.375 | 6917.152 | -3365.777 | -48.66% | 6119 | -2567.625 | -41.96%
K335 | NY | SOL-10370 | 4369.8125 | 7302.417 | -2932.6045 | -40.16% | 8179 | -3809.1875 | -46.57%
K345 | NY | SOL-10920 | 5288.7188 | 5418.434 | -129.7153 | -2.394% | 6910 | -1621.2812 | -23.46%
K445 | NY | SOL-10373 | 4901 | 7406.31 | -2505.31 | -33.83% | 6782.615 | -1881.615 | -27.74%
K495 | NY | SOL-10374 | 20126.75 | 28959.78 | -8833.03 | -30.5% | 49040.59 | -28913.84 | -58.96%
M020 | NY | SOL-10380 | 5231.9688 | 7045.739 | -1813.7702 | -25.74% | 9125 | -3893.0312 | -42.66%
M092 | NY | SOL-10383 | 4773.3125 | 7344.285 | -2570.9725 | -35.01% | 8137.596 | -3364.2835 | -41.34%
M143 | NY | SOL-10384 | 4837.8125 | 7607.831 | -2770.0185 | -36.41% | 8659.26 | -3821.4475 | -44.13%
M144 | NY | SOL-10385 | 7799.625 | 13319.92 | -5520.295 | -41.44% | 23584.05 | -15784.425 | -66.93%
M167 | NY | SOL-10386 | 4931.2188 | 5726.784 | -795.5652 | -13.89% | 8065.708 | -3134.4892 | -38.86%
M188 | NY | SOL-10387 | 4259.3614 | 6602.944 | -2343.5826 | -35.49% | 12343.55 | -8084.1886 | -65.49%
EMHC | NY | SOL-10351 | 1375.3594 | 1501.042 | -125.6826 | -8.373% | 2307.806 | -932.4466 | -40.4%
Q008 | NY | SOL-10397 | 7064.75 | 10490.4 | -3425.65 | -32.66% | 10992 | -3927.25 | -35.73%
Q018 | NY | SOL-10398 | 4452.3125 | 6553.947 | -2101.6345 | -32.07% | 6648.922 | -2196.6095 | -33.04%
Q021 | NY | SOL-10399 | 3531.9375 | 8384.728 | -4852.7905 | -57.88% | 5197.547 | -1665.6095 | -32.05%
Q025 | NY | SOL-10400 | 6147.875 | 8484.735 | -2336.86 | -27.54% | 7767 | -1619.125 | -20.85%
Q074 | NY | SOL-10402 | 0 | 0 | 0 |  | 0 | 0
Q115 | NY | SOL-10872 | 4946.6875 | 7759.496 | -2812.8085 | -36.25% | 8113.763 | -3167.0755 | -39.03%
Q139 | NY | SOL-10403 | 2738.25 | 5967.658 | -3229.408 | -54.12% | 5168 | -2429.75 | -47.02%
Q157 | NY | SOL-10404 | 5387.0765 | 13435.68 | -8048.6035 | -59.9% | 9154.302 | -3767.2255 | -41.15%
Q192 | NY | SOL-10406 | 8066.875 | 13154.35 | -5087.475 | -38.68% | 13840.9 | -5774.025 | -41.72%
Q210 | NY | SOL-10407 | 7166 | 9278.773 | -2112.773 | -22.77% | 11622 | -4456 | -38.34%
Q229 | NY | SOL-10408 | 2652.625 | 6651.485 | -3998.86 | -60.12% | 3668.691 | -1016.066 | -27.7%
Q231 | NY | SOL-10870 | 11856.375 | 20736.96 | -8880.585 | -42.82% | 16899 | -5042.625 | -29.84%
Q405 | NY | SOL-10409 | 13574 | 20233.85 | -6659.85 | -32.91% | 20674.02 | -7100.02 | -34.34%
Q435 | NY | SOL-10923 | 17258.625 | 15813.72 | 1444.905 | 9.137% | 25692 | -8433.375 | -32.82%
Q485 | NY | SOL-10869 | 14504.25 | 17360.88 | -2856.63 | -16.45% | 23708.84 | -9204.59 | -38.82%
Q490 | NY | SOL-10411 | 10624.25 | 0 | 10624.25 |  | 16762.39 | -6138.14 | -36.62%
Q620 | NY | SOL-10867 | 16495 | 22544.46 | -6049.46 | -26.83% | 27145.16 | -10650.16 | -39.23%
QMOA | NY | SOL-10415 | 1603.1 | 0 | 1603.1 |  | 2917.413 | -1314.313 | -45.05%
X024 | NY | SOL-10419 | 4890.8438 | 8802.685 | -3911.8412 | -44.44% | 8671 | -3780.1562 | -43.6%
X026 | NY | SOL-10420 | 4731.6 | 10554.32 | -5822.72 | -55.17% | 11071.89 | -6340.29 | -57.26%
X090 | NY | SOL-10925 | 4833.5625 | 4545.364 | 288.1985 | 6.34% | 7353 | -2519.4375 | -34.26%
X117 | NY | SOL-10422 | 3511.7 | 8875.315 | -5363.615 | -60.43% | 6501.377 | -2989.677 | -45.99%
X125 | NY | SOL-10423 | 7310.875 | 11094.59 | -3783.715 | -34.1% | 11925.9 | -4615.025 | -38.7%
X134 | NY | SOL-10424 | 3410.9614 | 11836.37 | -8425.4086 | -71.18% | 10182 | -6771.0386 | -66.5%
X135 | NY | SOL-10425 | 5787.375 | 10788.78 | -5001.405 | -46.36% | 9790 | -4002.625 | -40.88%
X139 JHS 222 | NY | SOL-10426 | 8569.5007 | 11357.54 | -2788.0393 | -24.55% | 12346 | -3776.4993 | -30.59%
X140 | NY | SOL-10926 | 5337.1562 | 8083.305 | -2746.1488 | -33.97% | 8234 | -2896.8438 | -35.18%
X166 | NY | SOL-10427 | 5113.3 | 8835.434 | -3722.134 | -42.13% | 7246 | -2132.7 | -29.43%
Murphy | MN | SOL-10094 | 513600 | 606225.7 | -92625.7 | -15.28% | 512282.9 | 1317.1 | 0.2571%
Terning | MN | SOL-10093 | 496936.065 | 602550.7 | -105614.635 | -17.53% | 464176.1 | 32759.965 | 7.058%
Boas Road 04 | NY | SOL-10908 | 72330 | 31962 | 40368 | 126.3% | 152897 | -80567 | -52.69%
Kelly Bridge Farm | NY | SOL-10911 | 77050 | 0 | 77050 |  | 143468.69 | -66418.69 | -46.29%
Pool Brook Road | NY | SOL-10909 | 59326 | 59325 | 1 | 0.001686% | 140415.7 | -81089.7 | -57.75%
Sackett Lake | NY | SOL-10910 | 132767 | 0 | 132767 |  | 165948.84 | -33181.84 | -20%
Burritt Road | NY | SOL-10913 | 58980 | 0 | 58980 |  | 110519.08 | -51539.08 | -46.63%
Villa Roma 1 | NY | SOL-10914 | 93005 | 0 | 93005 |  | 117697.64 | -24692.64 | -20.98%
Villa Roma 2 | NY | SOL-10915 | 77763 | 0 | 77763 |  | 114722.46 | -36959.46 | -32.22%
Washington 1 | NY | SOL-10912 | 82840 | 0 | 82840 |  | 106348.65 | -23508.65 | -22.11%
Washington 3 | NY | SOL-10828 | 0 | 0 | 0 |  | 129625.05 | -129625.05 | -100%
Washington 4 | NY | SOL-10829 | 129117 | 0 | 129117 |  | 130089.75 | -972.75 | -0.7478%
Big Tree | NY | SOL-10966 | 34020 | 34070 | -50 | -0.1468% | 116825.9001 | -82805.9001 | -70.88%
Canoga | NY | SOL-10965 | 271610 | 0 | 271610 |  | 381970.76 | -110360.76 | -28.89%
County Route 84 | NY | SOL-10967 | 372470 | 370150 | 2320 | 0.6268% | 472285.7 | -99815.7 | -21.13%
Donati | NY | SOL-10968 | 89520 | 87440 | 2080 | 2.379% | 156570.4 | -67050.4 | -42.82%
Henrietta | NY | SOL-10972 | 136180 | 133860 | 2320 | 1.733% | 268925.4 | -132745.4 | -49.36%
NY 70 | NY | SOL-10970 | 176660 | 174120 | 2540 | 1.459% | 386450 | -209790 | -54.29%
Reid | NY | SOL-10991 | 137656.9248 | 284559.7 | -146902.7752 | -51.62% | 265223 | -127566.0752 | -48.1%
Sangolqui | NY | SOL-10975 | 93160 | 66700 | 26460 | 39.67% | 151974.9 | -58814.9 | -38.7%
State Highway 17B | NY | SOL-10988 | 0 | 0 | 0 |  | 384984 | -384984 | -100%
State Route 14A | NY | SOL-10997 | 0 | 0 | 0 |  | 427147.4 | -427147.4 | -100%
West Creek | NY | SOL-10995 | 265730 | 230210 | 35520 | 15.43% | 397925.5 | -132195.5 | -33.22%
Wildflower | NY | SOL-10982 | 246984 | 188692 | 58292 | 30.89% | 433603.2 | -186619.2 | -43.04%
Glen Mary 1 | NY | SOL-10993 | 164340 | 146450 | 17890 | 12.22% | 420494.8 | -256154.8 | -60.92%
Glen Mary 2 | NY | SOL-10994 | 138160 | 0 | 138160 |  | 171573.9 | -33413.9 | -19.47%
Telegraph 1 | NY | SOL-11003 | 153680 | 0 | 153680 |  | 286022.2 | -132342.2 | -46.27%
Telegraph 2 | NY | SOL-11004 | 97060 | 0 | 97060 |  | 146627.1 | -49567.1 | -33.8%
Cafferty Hill | NY | SOL-10996 | 82990 | 85880 | -2890 | -3.365% | 373143.4 | -290153.4 | -77.76%
Dunkleman | NY | SOL-11008 | 191990 | 157970 | 34020 | 21.54% | 369715.73 | -177725.73 | -48.07%
Route 19 1 | NY | SOL-11001 | 96365 | 81568.2 | 14796.8 | 18.14% | 154567.8 | -58202.8 | -37.66%
Route 19 2 | NY | SOL-11002 | 249670 | 246010 | 3660 | 1.488% | 409574.6 | -159904.6 | -39.04%
Yellow Mills 1 | NY | SOL-11006 | 107464 | 105508 | 1956 | 1.854% | 123508.6 | -16044.6 | -12.99%
Yellow Mills 2 | NY | SOL-11005 | 196674 | 0 | 196674 |  | 126216.1 | 70457.9 | 55.82%
Yellow Mills 3 | NY | SOL-11007 | 95437 | 93389 | 2048 | 2.193% | 111400.8 | -15963.8 | -14.33%
Catskill | NY | SOL-11021 | 207977 | 0 | 207977 |  | 295119.31 | -87142.31 | -29.53%
Eddy Ridge | NY | SOL-11054 | 89230 | 87456 | 1774 | 2.028% | 176115 | -86885 | -49.33%
Ridgeway #1 | NY | SOL-11018 | 244376 | 148377 | 95999 | 64.7% | 426059 | -181683 | -42.64%
Rivard 1 | NY | SOL-11011 | 148338.3301 | 270906.9 | -122568.5699 | -45.24% | 257064.8 | -108726.4699 | -42.3%
Rivard 2 | NY | SOL-11012 | 142942 | 205053 | -62111 | -30.29% | 245245.8 | -102303.8 | -41.71%
Ridgeway #2 | NY | SOL-11027 | 124718 | 121762 | 2956 | 2.428% | 219945.25 | -95227.25 | -43.3%
Spencer | NY | SOL-11017 | 366895.2 | 362740 | 4155.2 | 1.146% | 306010.64 | 60884.56 | 19.9%
Reisender | NY | SOL-10886 | 55170 | 54780 | 390 | 0.7119% | 139255.92 | -84085.92 | -60.38%
Finney | NY | SOL-10999 | 423780 | 421430 | 2350 | 0.5576% | 423916.47 | -136.47 | -0.03219%
Davis Solar | NY | SOL-10958 | 98174 | 222749.1 | -124575.1 | -55.93% | 182746 | -84572 | -46.28%
Genesee | NY | SOL-10951 | 71876 | 71030.2 | 845.8 | 1.191% | 223003.43 | -151127.43 | -67.77%
Landau I | NY | SOL-10891 | 76220 | 0 | 76220 |  | 183280 | -107060 | -58.41%
Landau II | NY | SOL-10895 | 0 | 0 | 0 |  | 345100.3 | 0 | 0%
New Beginnings | NY | SOL-10890 | 92270 | 92270 | 0 | 0% | 179886.74 | -87616.74 | -48.71%
Bullitt Farm Solar, LLC | NY | SOL-10998 | 58980 | 0 | 58980 |  | 110519.08 | -51539.08 | -46.63%
Brodhead Solar, LLC | NY | SOL-10899 | 177618 | 190253 | -12635 | -6.641% | 215650.8 | -38032.8 | -17.64%
Svenski | NY | SOL-10894 | 30220 | 0 | 30220 |  | 143761.47 | -113541.47 | -78.98%
Bantam | NY | SOL-10986 | 159790 | 190990 | -31200 | -16.34% | 384649.1825 | -224859.1825 | -58.46%
Bogart | NY | SOL-10887 | 99550 | 70660 | 28890 | 40.89% | 164078.57 | -64528.57 | -39.33%
Dubois | NY | SOL-10892 | 90300 | 90343 | -43 | -0.0476% | 0 | 0
Salt Point | NY | SOL-10888 | 124160 | 124160 | 0 | 0% | 135218.23 | -11058.23 | -8.178%
Wheatland 2A | NY | SOL-10971 | 160740 | 159600 | 1140 | 0.7143% | 282852.6 | -122112.6 | -43.17%
Wheatland 2B | NY | SOL-10961 | 164520 | 0 | 164520 |  | 279044.7 | -114524.7 | -41.04%
Brickchurch | NY | SOL-10889 | 51400 | 52570 | -1170 | -2.226% | 77601.11 | -26201.11 | -33.76%
McCarthy Solar | NY | SOL-10992 | 132470 | 0 | 132470 |  | 199506.06 | -67036.06 | -33.6%
Costanza | NY | SOL-10907 | 80480 | 80582.43 | -102.43 | -0.1271% | 161660.63 | -81180.63 | -50.22%
Lockenhurst Pond | NY | SOL-11000 | 175704 | 203514.2 | -27810.2 | -13.66% | 160367 | 15337 | 9.564%
Drinkwater | NY | SOL-10896 | 92100 | 0 | 92100 |  | 167148.09 | -75048.09 | -44.9%
Altamont | NY | SOL-11085 | 214086 | 414723.4 | -200637.4 | -48.38% | 346402.7 | -132316.7 | -38.2%
Krumkill North | NY | SOL-11086 | 178706 | 333810.6 | -155104.6 | -46.46% | 463900.5 | -285194.5 | -61.48%
Krumkill South | NY | SOL-11087 | 174363 | 315721.3 | -141358.3 | -44.77% | 363684 | -189321 | -52.06%
X092 | NY | SOL-11189 | 4003.3 | 6290.382 | -2287.082 | -36.36% | 8237 | -4233.7 | -51.4%
X093 | NY | SOL-10932 | 2882.4082 | 4009.505 | -1127.0968 | -28.11% | 4845 | -1962.5918 | -40.51%
X095 | NY | SOL-10929 | 3943.5781 | 7896.833 | -3953.2549 | -50.06% | 6901 | -2957.4219 | -42.85%
X181 | NY | SOL-10428 | 7292.9062 | 14591.35 | -7298.4438 | -50.02% | 11497 | -4204.0938 | -36.57%
X415 | NY | SOL-10429 | 4703.9531 | 7354.188 | -2650.2349 | -36.04% | 6299 | -1595.0469 | -25.32%
K198 | NY | SOL-10930 | 3744.7969 | 5314.616 | -1569.8191 | -29.54% | 5807 | -2062.2031 | -35.51%
K203 | NY | SOL-11190 | 5244.2 | 7024.09 | -1779.89 | -25.34% | 9142 | -3897.8 | -42.64%
K213 | NY | SOL-11191 | 5406.9 | 7582.657 | -2175.757 | -28.69% | 9570 | -4163.1 | -43.5%
K217 | NY | SOL-10933 | 2473.8203 | 4075.625 | -1601.8047 | -39.3% | 3879 | -1405.1797 | -36.23%
K307 | NY | SOL-10876 | 5876.7969 | 13060.53 | -7183.7331 | -55% | 7468 | -1591.2031 | -21.31%
K610 | NY | SOL-11158 | 7256.1 | 9685.564 | -2429.464 | -25.08% | 12467 | -5210.9 | -41.8%
M025 | NY | SOL-10392 | 4989.125 | 14236.48 | -9247.355 | -64.96% | 9891 | -4901.875 | -49.56%
M028 | NY | SOL-10381 | 4642.0469 | 6572.825 | -1930.7781 | -29.38% | 6540 | -1897.9531 | -29.02%
Q030 | NY | SOL-10878 | 1390.2344 | 3019.264 | -1629.0296 | -53.95% | 8785 | -7394.7656 | -84.17%
Q130 | NY | SOL-10877 | 2955.9609 | 6868.722 | -3912.7611 | -56.96% | 4243.431 | -1287.4701 | -30.34%
Q196 | NY | SOL-10879 | 3733.7969 | 7942.186 | -4208.3891 | -52.99% | 5931 | -2197.2031 | -37.05%
Q220 | NY | SOL-10873 | 4377.875 | 10716.8 | -6338.925 | -59.15% | 5740 | -1362.125 | -23.73%
Q205 | NY | SOL-10922 | 5970.6406 | 13482.7 | -7512.0594 | -55.72% | 8522 | -2551.3594 | -29.94%
Q400 | NY | SOL-10871 | 8726.2525 | 0 | 8726.2525 |  | 12985 | -4258.7475 | -32.8%
R003 | NY | SOL-10416 | 8987.25 | 11551.87 | -2564.62 | -22.2% | 13336 | -4348.75 | -32.61%
R007 | NY | SOL-10417 | 9489.9688 | 13976.96 | -4486.9912 | -32.1% | 22783.34 | -13293.3713 | -58.35%
BK16 | NY | SOL-11093 | 9596 | 12915.56 | -3319.56 | -25.7% | 13947 | -4351 | -31.2%
Trenton - Trenton East | IL | SOL-11060 | 268098 | 277362.4 | -9264.4 | -3.34% | 211713 | 56385 | 26.63%
Trenton - Trenton West | IL | SOL-11061 | 268153 | 240078.6 | 28074.4 | 11.69% | 215152 | 53001 | 24.63%
Dakota - Dakota Solar 1 | IL | SOL-11113 | 214508 | 0 | 214508 |  | 220248 | -5740 | -2.606%
X018 | NY | SOL-10418 | 4430.75 | 5815.83 | -1385.08 | -23.82% | 7520 | -3089.25 | -41.08%
Janiak Solar | NY | SOL-10898 | 105163 | 129742.5 | -24579.5 | -18.94% | 203943 | -98780 | -48.44%
County Route 11B | NY | SOL-10983 | 259418.8 | 254569.6 | 4849.2 | 1.905% | 0 | 0
Barone | NY | SOL-11034 | 162889 | 160342 | 2547 | 1.588% | 210690.0206 | -47801.0206 | -22.69%
Cedarville | IL | SOL-11069 | 156820 | 203303 | -46483 | -22.86% | 185269.1 | -28449.1 | -15.36%
O'Brien Hill #1 | NY | SOL-11098 | 0 | 0 | 0 |  | 0 | 0
O'Brien Hill #2 | NY | SOL-11099 | 230537 | 230436 | 101 | 0.04383% | 0 | 0
Trinity - Freeport | IL | SOL-11057 | 197770 | 191173.8 | 6596.2 | 3.45% | 182784 | 14986 | 8.199%
Ransom | NY | SOL-11157 | 262100 | 257255 | 4845 | 1.883% | 0 | 0
Horseheads - Wedge | NY | SOL-11160 | 153909 | 151921 | 1988 | 1.309% | 0 | 0
Otisville - Shoddy Hollow | NY | SOL-11185 | 228031 | 224988 | 3043 | 1.353% | 0 | 0
Wellsville - Chenunda Creek | NY | SOL-11187 | 112266 | 111257 | 1009 | 0.9069% | 0 | 0
DC: Washington - Essex Condominium | DC | SOL-10036 | 1208 | 1601.977 | -393.977 | -24.59% | 2142.399 | -934.399 | -43.61%
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 7951.027 | 8242.12 | -291.093 | -3.532% | 9757.33 | -1806.303 | -18.51%
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 9375 | 7407.475 | 1967.525 | 26.56% | 9752.109 | -377.109 | -3.867%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149 | 0 | 0 | 0 |  | 0 | 0
IL: Viola - Goldenrod - (PW) | IL | SOL-11132 | 574985 | 508651.7 | 66333.3 | 13.04% | 518040 | 56945 | 10.99%
IL: Marengo - Grant - (PW) | IL | SOL-11147 | 224264 | 0 | 224264 |  | 193523.2 | 30740.8 | 15.88%
NY: Cambridge - Cambridge (PW) | NY | SOL-11126 | 112395.156 | 100094.105 | 12301.051 | 12.29% | 537994 | -425598.844 | -79.11%
NY: Whitesville - Independence North | NY | SOL-11186 | 276854 | 0 | 276854 |  | 0 | 0
IL: Beecher - Cottage Grove North (PW) | IL | SOL-11114 | 213014 | 231407.5 | -18393.5 | -7.949% | 186272 | 26742 | 14.36%
IL: Beecher - Cottage Grove South (PW) | IL | SOL-11115 | 225299 | 297560.1 | -72261.1 | -24.28% | 174687 | 50612 | 28.97%
IL: Harvard - 9618 US HWY 14 (PW) | IL | SOL-11110 | 182768 | 396799.6 | -214031.6 | -53.94% | 172612 | 10156 | 5.884%
IL: Beecher - 701 E Goodenow Rd (PW) | IL | SOL-11112 | 26786 | 28958.46 | -2172.46 | -7.502% | 178720 | -151934 | -85.01%
NY: Stormville - Green Haven - (IRA) | NY | SOL-11151 | 160195.6 | 0 | 160195.6 |  | 0 | 0
IL: Hillsboro - Anacott (PW) | IL | SOL-11134 | 634429 | 0 | 634429 |  | 553720 | 80709 | 14.58%
IL: Manhattan - Gougar (PW) | IL | SOL-11148 | 121126 | 145932.1 | -24806.1 | -17% | 208326.7 | -87200.7 | -41.86%
IL: Morrison - Sawyer (PW) | IL | SOL-11176
IL: Kankakee - Jeffery (PW) | IL | SOL-11173
IL: Freeport - 2240 South 18th Ave (PW) | IL | SOL-11084

## 1st Qtr
Generate Capital |  |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  |  | 15338370.7232 | 12898958.885 | 2439411.8382 | 18.91% | 21017476.3131 | -5679105.59 | -27.02%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | %
K026 | NY | SOL-10356 | 8328.108 | 12159.88 | -3831.772 | -31.51% | 11055.95 | -2727.842 | -24.67%
K041 | NY | SOL-10357 | 5871.5312 | 9407.467 | -3535.9358 | -37.59% | 9924 | -4052.4688 | -40.84%
K043 | NY | SOL-10358 | 7527.0625 | 10861.06 | -3333.9975 | -30.7% | 2303 | 5224.0625 | 226.8%
K058 | NY | SOL-10360 | 5490.6875 | 8437.168 | -2946.4805 | -34.92% | 9101.326 | -3610.6385 | -39.67%
K115 | NY | SOL-10361 | 3483.875 | 7300.807 | -3816.932 | -52.28% | 5565.882 | -2082.007 | -37.41%
K152 | NY | SOL-10362 | 2067.4375 | 4344.89 | -2277.4525 | -52.42% | 3567 | -1499.5625 | -42.04%
K166 | NY | SOL-10363 | 7527.75 | 16102.59 | -8574.84 | -53.25% | 12064.56 | -4536.81 | -37.6%
K206 | NY | SOL-10927 | 5243.875 | 5255.242 | -11.367 | -0.2163% | 6894 | -1650.125 | -23.94%
K251 | NY | SOL-10365 | 5285.5625 | 0 | 5285.5625 |  | 8483.094 | -3197.5315 | -37.69%
K269 | NY | SOL-10366 | 4482.4375 | 7734.486 | -3252.0485 | -42.05% | 7723.149 | -3240.7115 | -41.96%
K273 | NY | SOL-10367 | 4816.2673 | 0 | 4816.2673 |  | 9546 | -4729.7327 | -49.55%
K287 | NY | SOL-10919 | 4113.1875 | 5386.828 | -1273.6405 | -23.64% | 7303 | -3189.8125 | -43.68%
K298 | NY | SOL-10368 | 3551.375 | 6917.152 | -3365.777 | -48.66% | 6119 | -2567.625 | -41.96%
K335 | NY | SOL-10370 | 4369.8125 | 7302.417 | -2932.6045 | -40.16% | 8179 | -3809.1875 | -46.57%
K345 | NY | SOL-10920 | 5288.7188 | 5418.434 | -129.7153 | -2.394% | 6910 | -1621.2812 | -23.46%
K445 | NY | SOL-10373 | 4901 | 7406.31 | -2505.31 | -33.83% | 6782.615 | -1881.615 | -27.74%
K495 | NY | SOL-10374 | 20126.75 | 28959.78 | -8833.03 | -30.5% | 49040.59 | -28913.84 | -58.96%
M020 | NY | SOL-10380 | 5231.9688 | 7045.739 | -1813.7702 | -25.74% | 9125 | -3893.0312 | -42.66%
M092 | NY | SOL-10383 | 4773.3125 | 7344.285 | -2570.9725 | -35.01% | 8137.596 | -3364.2835 | -41.34%
M143 | NY | SOL-10384 | 4837.8125 | 7607.831 | -2770.0185 | -36.41% | 8659.26 | -3821.4475 | -44.13%
M144 | NY | SOL-10385 | 7799.625 | 13319.92 | -5520.295 | -41.44% | 23584.05 | -15784.425 | -66.93%
M167 | NY | SOL-10386 | 4931.2188 | 5726.784 | -795.5652 | -13.89% | 8065.708 | -3134.4892 | -38.86%
M188 | NY | SOL-10387 | 4259.3614 | 6602.944 | -2343.5826 | -35.49% | 12343.55 | -8084.1886 | -65.49%
EMHC | NY | SOL-10351 | 1375.3594 | 1501.042 | -125.6826 | -8.373% | 2307.806 | -932.4466 | -40.4%
Q008 | NY | SOL-10397 | 7064.75 | 10490.4 | -3425.65 | -32.66% | 10992 | -3927.25 | -35.73%
Q018 | NY | SOL-10398 | 4452.3125 | 6553.947 | -2101.6345 | -32.07% | 6648.922 | -2196.6095 | -33.04%
Q021 | NY | SOL-10399 | 3531.9375 | 8384.728 | -4852.7905 | -57.88% | 5197.547 | -1665.6095 | -32.05%
Q025 | NY | SOL-10400 | 6147.875 | 8484.735 | -2336.86 | -27.54% | 7767 | -1619.125 | -20.85%
Q074 | NY | SOL-10402 | 0 | 0 | 0 |  | 0 | 0
Q115 | NY | SOL-10872 | 4946.6875 | 7759.496 | -2812.8085 | -36.25% | 8113.763 | -3167.0755 | -39.03%
Q139 | NY | SOL-10403 | 2738.25 | 5967.658 | -3229.408 | -54.12% | 5168 | -2429.75 | -47.02%
Q157 | NY | SOL-10404 | 5387.0765 | 13435.68 | -8048.6035 | -59.9% | 9154.302 | -3767.2255 | -41.15%
Q192 | NY | SOL-10406 | 8066.875 | 13154.35 | -5087.475 | -38.68% | 13840.9 | -5774.025 | -41.72%
Q210 | NY | SOL-10407 | 7166 | 9278.773 | -2112.773 | -22.77% | 11622 | -4456 | -38.34%
Q229 | NY | SOL-10408 | 2652.625 | 6651.485 | -3998.86 | -60.12% | 3668.691 | -1016.066 | -27.7%
Q231 | NY | SOL-10870 | 11856.375 | 20736.96 | -8880.585 | -42.82% | 16899 | -5042.625 | -29.84%
Q405 | NY | SOL-10409 | 13574 | 20233.85 | -6659.85 | -32.91% | 20674.02 | -7100.02 | -34.34%
Q435 | NY | SOL-10923 | 17258.625 | 15813.72 | 1444.905 | 9.137% | 25692 | -8433.375 | -32.82%
Q485 | NY | SOL-10869 | 14504.25 | 17360.88 | -2856.63 | -16.45% | 23708.84 | -9204.59 | -38.82%
Q490 | NY | SOL-10411 | 10624.25 | 0 | 10624.25 |  | 16762.39 | -6138.14 | -36.62%
Q620 | NY | SOL-10867 | 16495 | 22544.46 | -6049.46 | -26.83% | 27145.16 | -10650.16 | -39.23%
QMOA | NY | SOL-10415 | 1603.1 | 0 | 1603.1 |  | 2917.413 | -1314.313 | -45.05%
X024 | NY | SOL-10419 | 4890.8438 | 8802.685 | -3911.8412 | -44.44% | 8671 | -3780.1562 | -43.6%
X026 | NY | SOL-10420 | 4731.6 | 10554.32 | -5822.72 | -55.17% | 11071.89 | -6340.29 | -57.26%
X090 | NY | SOL-10925 | 4833.5625 | 4545.364 | 288.1985 | 6.34% | 7353 | -2519.4375 | -34.26%
X117 | NY | SOL-10422 | 3511.7 | 8875.315 | -5363.615 | -60.43% | 6501.377 | -2989.677 | -45.99%
X125 | NY | SOL-10423 | 7310.875 | 11094.59 | -3783.715 | -34.1% | 11925.9 | -4615.025 | -38.7%
X134 | NY | SOL-10424 | 3410.9614 | 11836.37 | -8425.4086 | -71.18% | 10182 | -6771.0386 | -66.5%
X135 | NY | SOL-10425 | 5787.375 | 10788.78 | -5001.405 | -46.36% | 9790 | -4002.625 | -40.88%
X139 JHS 222 | NY | SOL-10426 | 8569.5007 | 11357.54 | -2788.0393 | -24.55% | 12346 | -3776.4993 | -30.59%
X140 | NY | SOL-10926 | 5337.1562 | 8083.305 | -2746.1488 | -33.97% | 8234 | -2896.8438 | -35.18%
X166 | NY | SOL-10427 | 5113.3 | 8835.434 | -3722.134 | -42.13% | 7246 | -2132.7 | -29.43%
Murphy | MN | SOL-10094 | 513600 | 606225.7 | -92625.7 | -15.28% | 512282.9 | 1317.1 | 0.2571%
Terning | MN | SOL-10093 | 496936.065 | 602550.7 | -105614.635 | -17.53% | 464176.1 | 32759.965 | 7.058%
Boas Road 04 | NY | SOL-10908 | 72330 | 31962 | 40368 | 126.3% | 152897 | -80567 | -52.69%
Kelly Bridge Farm | NY | SOL-10911 | 77050 | 0 | 77050 |  | 143468.69 | -66418.69 | -46.29%
Pool Brook Road | NY | SOL-10909 | 59326 | 59325 | 1 | 0.001686% | 140415.7 | -81089.7 | -57.75%
Sackett Lake | NY | SOL-10910 | 132767 | 0 | 132767 |  | 165948.84 | -33181.84 | -20%
Burritt Road | NY | SOL-10913 | 58980 | 0 | 58980 |  | 110519.08 | -51539.08 | -46.63%
Villa Roma 1 | NY | SOL-10914 | 93005 | 0 | 93005 |  | 117697.64 | -24692.64 | -20.98%
Villa Roma 2 | NY | SOL-10915 | 77763 | 0 | 77763 |  | 114722.46 | -36959.46 | -32.22%
Washington 1 | NY | SOL-10912 | 82840 | 0 | 82840 |  | 106348.65 | -23508.65 | -22.11%
Washington 3 | NY | SOL-10828 | 0 | 0 | 0 |  | 129625.05 | -129625.05 | -100%
Washington 4 | NY | SOL-10829 | 129117 | 0 | 129117 |  | 130089.75 | -972.75 | -0.7478%
Big Tree | NY | SOL-10966 | 34020 | 34070 | -50 | -0.1468% | 116825.9001 | -82805.9001 | -70.88%
Canoga | NY | SOL-10965 | 271610 | 0 | 271610 |  | 381970.76 | -110360.76 | -28.89%
County Route 84 | NY | SOL-10967 | 372470 | 370150 | 2320 | 0.6268% | 472285.7 | -99815.7 | -21.13%
Donati | NY | SOL-10968 | 89520 | 87440 | 2080 | 2.379% | 156570.4 | -67050.4 | -42.82%
Henrietta | NY | SOL-10972 | 136180 | 133860 | 2320 | 1.733% | 268925.4 | -132745.4 | -49.36%
NY 70 | NY | SOL-10970 | 176660 | 174120 | 2540 | 1.459% | 386450 | -209790 | -54.29%
Reid | NY | SOL-10991 | 137656.9248 | 284559.7 | -146902.7752 | -51.62% | 265223 | -127566.0752 | -48.1%
Sangolqui | NY | SOL-10975 | 93160 | 66700 | 26460 | 39.67% | 151974.9 | -58814.9 | -38.7%
State Highway 17B | NY | SOL-10988 | 0 | 0 | 0 |  | 384984 | -384984 | -100%
State Route 14A | NY | SOL-10997 | 0 | 0 | 0 |  | 427147.4 | -427147.4 | -100%
West Creek | NY | SOL-10995 | 265730 | 230210 | 35520 | 15.43% | 397925.5 | -132195.5 | -33.22%
Wildflower | NY | SOL-10982 | 246984 | 188692 | 58292 | 30.89% | 433603.2 | -186619.2 | -43.04%
Glen Mary 1 | NY | SOL-10993 | 164340 | 146450 | 17890 | 12.22% | 420494.8 | -256154.8 | -60.92%
Glen Mary 2 | NY | SOL-10994 | 138160 | 0 | 138160 |  | 171573.9 | -33413.9 | -19.47%
Telegraph 1 | NY | SOL-11003 | 153680 | 0 | 153680 |  | 286022.2 | -132342.2 | -46.27%
Telegraph 2 | NY | SOL-11004 | 97060 | 0 | 97060 |  | 146627.1 | -49567.1 | -33.8%
Cafferty Hill | NY | SOL-10996 | 82990 | 85880 | -2890 | -3.365% | 373143.4 | -290153.4 | -77.76%
Dunkleman | NY | SOL-11008 | 191990 | 157970 | 34020 | 21.54% | 369715.73 | -177725.73 | -48.07%
Route 19 1 | NY | SOL-11001 | 96365 | 81568.2 | 14796.8 | 18.14% | 154567.8 | -58202.8 | -37.66%
Route 19 2 | NY | SOL-11002 | 249670 | 246010 | 3660 | 1.488% | 409574.6 | -159904.6 | -39.04%
Yellow Mills 1 | NY | SOL-11006 | 107464 | 105508 | 1956 | 1.854% | 123508.6 | -16044.6 | -12.99%
Yellow Mills 2 | NY | SOL-11005 | 196674 | 0 | 196674 |  | 126216.1 | 70457.9 | 55.82%
Yellow Mills 3 | NY | SOL-11007 | 95437 | 93389 | 2048 | 2.193% | 111400.8 | -15963.8 | -14.33%
Catskill | NY | SOL-11021 | 207977 | 0 | 207977 |  | 295119.31 | -87142.31 | -29.53%
Eddy Ridge | NY | SOL-11054 | 89230 | 87456 | 1774 | 2.028% | 176115 | -86885 | -49.33%
Ridgeway #1 | NY | SOL-11018 | 244376 | 148377 | 95999 | 64.7% | 426059 | -181683 | -42.64%
Rivard 1 | NY | SOL-11011 | 148338.3301 | 270906.9 | -122568.5699 | -45.24% | 257064.8 | -108726.4699 | -42.3%
Rivard 2 | NY | SOL-11012 | 142942 | 205053 | -62111 | -30.29% | 245245.8 | -102303.8 | -41.71%
Ridgeway #2 | NY | SOL-11027 | 124718 | 121762 | 2956 | 2.428% | 219945.25 | -95227.25 | -43.3%
Spencer | NY | SOL-11017 | 366895.2 | 362740 | 4155.2 | 1.146% | 306010.64 | 60884.56 | 19.9%
Reisender | NY | SOL-10886 | 55170 | 54780 | 390 | 0.7119% | 139255.92 | -84085.92 | -60.38%
Finney | NY | SOL-10999 | 423780 | 421430 | 2350 | 0.5576% | 423916.47 | -136.47 | -0.03219%
Davis Solar | NY | SOL-10958 | 98174 | 222749.1 | -124575.1 | -55.93% | 182746 | -84572 | -46.28%
Genesee | NY | SOL-10951 | 71876 | 71030.2 | 845.8 | 1.191% | 223003.43 | -151127.43 | -67.77%
Landau I | NY | SOL-10891 | 76220 | 0 | 76220 |  | 183280 | -107060 | -58.41%
Landau II | NY | SOL-10895 | 0 | 0 | 0 |  | 345100.3 | 0 | 0%
New Beginnings | NY | SOL-10890 | 92270 | 92270 | 0 | 0% | 179886.74 | -87616.74 | -48.71%
Bullitt Farm Solar, LLC | NY | SOL-10998 | 58980 | 0 | 58980 |  | 110519.08 | -51539.08 | -46.63%
Brodhead Solar, LLC | NY | SOL-10899 | 177618 | 190253 | -12635 | -6.641% | 215650.8 | -38032.8 | -17.64%
Svenski | NY | SOL-10894 | 30220 | 0 | 30220 |  | 143761.47 | -113541.47 | -78.98%
Bantam | NY | SOL-10986 | 159790 | 190990 | -31200 | -16.34% | 384649.1825 | -224859.1825 | -58.46%
Bogart | NY | SOL-10887 | 99550 | 70660 | 28890 | 40.89% | 164078.57 | -64528.57 | -39.33%
Dubois | NY | SOL-10892 | 90300 | 90343 | -43 | -0.0476% | 0 | 0
Salt Point | NY | SOL-10888 | 124160 | 124160 | 0 | 0% | 135218.23 | -11058.23 | -8.178%
Wheatland 2A | NY | SOL-10971 | 160740 | 159600 | 1140 | 0.7143% | 282852.6 | -122112.6 | -43.17%
Wheatland 2B | NY | SOL-10961 | 164520 | 0 | 164520 |  | 279044.7 | -114524.7 | -41.04%
Brickchurch | NY | SOL-10889 | 51400 | 52570 | -1170 | -2.226% | 77601.11 | -26201.11 | -33.76%
McCarthy Solar | NY | SOL-10992 | 132470 | 0 | 132470 |  | 199506.06 | -67036.06 | -33.6%
Costanza | NY | SOL-10907 | 80480 | 80582.43 | -102.43 | -0.1271% | 161660.63 | -81180.63 | -50.22%
Lockenhurst Pond | NY | SOL-11000 | 175704 | 203514.2 | -27810.2 | -13.66% | 160367 | 15337 | 9.564%
Drinkwater | NY | SOL-10896 | 92100 | 0 | 92100 |  | 167148.09 | -75048.09 | -44.9%
Altamont | NY | SOL-11085 | 214086 | 414723.4 | -200637.4 | -48.38% | 346402.7 | -132316.7 | -38.2%
Krumkill North | NY | SOL-11086 | 178706 | 333810.6 | -155104.6 | -46.46% | 463900.5 | -285194.5 | -61.48%
Krumkill South | NY | SOL-11087 | 174363 | 315721.3 | -141358.3 | -44.77% | 363684 | -189321 | -52.06%
X092 | NY | SOL-11189 | 4003.3 | 6290.382 | -2287.082 | -36.36% | 8237 | -4233.7 | -51.4%
X093 | NY | SOL-10932 | 2882.4082 | 4009.505 | -1127.0968 | -28.11% | 4845 | -1962.5918 | -40.51%
X095 | NY | SOL-10929 | 3943.5781 | 7896.833 | -3953.2549 | -50.06% | 6901 | -2957.4219 | -42.85%
X181 | NY | SOL-10428 | 7292.9062 | 14591.35 | -7298.4438 | -50.02% | 11497 | -4204.0938 | -36.57%
X415 | NY | SOL-10429 | 4703.9531 | 7354.188 | -2650.2349 | -36.04% | 6299 | -1595.0469 | -25.32%
K198 | NY | SOL-10930 | 3744.7969 | 5314.616 | -1569.8191 | -29.54% | 5807 | -2062.2031 | -35.51%
K203 | NY | SOL-11190 | 5244.2 | 7024.09 | -1779.89 | -25.34% | 9142 | -3897.8 | -42.64%
K213 | NY | SOL-11191 | 5406.9 | 7582.657 | -2175.757 | -28.69% | 9570 | -4163.1 | -43.5%
K217 | NY | SOL-10933 | 2473.8203 | 4075.625 | -1601.8047 | -39.3% | 3879 | -1405.1797 | -36.23%
K307 | NY | SOL-10876 | 5876.7969 | 13060.53 | -7183.7331 | -55% | 7468 | -1591.2031 | -21.31%
K610 | NY | SOL-11158 | 7256.1 | 9685.564 | -2429.464 | -25.08% | 12467 | -5210.9 | -41.8%
M025 | NY | SOL-10392 | 4989.125 | 14236.48 | -9247.355 | -64.96% | 9891 | -4901.875 | -49.56%
M028 | NY | SOL-10381 | 4642.0469 | 6572.825 | -1930.7781 | -29.38% | 6540 | -1897.9531 | -29.02%
Q030 | NY | SOL-10878 | 1390.2344 | 3019.264 | -1629.0296 | -53.95% | 8785 | -7394.7656 | -84.17%
Q130 | NY | SOL-10877 | 2955.9609 | 6868.722 | -3912.7611 | -56.96% | 4243.431 | -1287.4701 | -30.34%
Q196 | NY | SOL-10879 | 3733.7969 | 7942.186 | -4208.3891 | -52.99% | 5931 | -2197.2031 | -37.05%
Q220 | NY | SOL-10873 | 4377.875 | 10716.8 | -6338.925 | -59.15% | 5740 | -1362.125 | -23.73%
Q205 | NY | SOL-10922 | 5970.6406 | 13482.7 | -7512.0594 | -55.72% | 8522 | -2551.3594 | -29.94%
Q400 | NY | SOL-10871 | 8726.2525 | 0 | 8726.2525 |  | 12985 | -4258.7475 | -32.8%
R003 | NY | SOL-10416 | 8987.25 | 11551.87 | -2564.62 | -22.2% | 13336 | -4348.75 | -32.61%
R007 | NY | SOL-10417 | 9489.9688 | 13976.96 | -4486.9912 | -32.1% | 22783.34 | -13293.3713 | -58.35%
BK16 | NY | SOL-11093 | 9596 | 12915.56 | -3319.56 | -25.7% | 13947 | -4351 | -31.2%
Trenton - Trenton East | IL | SOL-11060 | 268098 | 277362.4 | -9264.4 | -3.34% | 211713 | 56385 | 26.63%
Trenton - Trenton West | IL | SOL-11061 | 268153 | 240078.6 | 28074.4 | 11.69% | 215152 | 53001 | 24.63%
Dakota - Dakota Solar 1 | IL | SOL-11113 | 214508 | 0 | 214508 |  | 220248 | -5740 | -2.606%
X018 | NY | SOL-10418 | 4430.75 | 5815.83 | -1385.08 | -23.82% | 7520 | -3089.25 | -41.08%
Janiak Solar | NY | SOL-10898 | 105163 | 129742.5 | -24579.5 | -18.94% | 203943 | -98780 | -48.44%
County Route 11B | NY | SOL-10983 | 259418.8 | 254569.6 | 4849.2 | 1.905% | 0 | 0
Barone | NY | SOL-11034 | 162889 | 160342 | 2547 | 1.588% | 210690.0206 | -47801.0206 | -22.69%
Cedarville | IL | SOL-11069 | 156820 | 203303 | -46483 | -22.86% | 185269.1 | -28449.1 | -15.36%
O'Brien Hill #1 | NY | SOL-11098 | 0 | 0 | 0 |  | 0 | 0
O'Brien Hill #2 | NY | SOL-11099 | 230537 | 230436 | 101 | 0.04383% | 0 | 0
Trinity - Freeport | IL | SOL-11057 | 197770 | 191173.8 | 6596.2 | 3.45% | 182784 | 14986 | 8.199%
Ransom | NY | SOL-11157 | 262100 | 257255 | 4845 | 1.883% | 0 | 0
Horseheads - Wedge | NY | SOL-11160 | 153909 | 151921 | 1988 | 1.309% | 0 | 0
Otisville - Shoddy Hollow | NY | SOL-11185 | 228031 | 224988 | 3043 | 1.353% | 0 | 0
Wellsville - Chenunda Creek | NY | SOL-11187 | 112266 | 111257 | 1009 | 0.9069% | 0 | 0
DC: Washington - Essex Condominium | DC | SOL-10036 | 1208 | 1601.977 | -393.977 | -24.59% | 2142.399 | -934.399 | -43.61%
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 7951.027 | 8242.12 | -291.093 | -3.532% | 9757.33 | -1806.303 | -18.51%
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 9375 | 7407.475 | 1967.525 | 26.56% | 9752.109 | -377.109 | -3.867%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149 | 0 | 0 | 0 |  | 0 | 0
IL: Viola - Goldenrod - (PW) | IL | SOL-11132 | 574985 | 508651.7 | 66333.3 | 13.04% | 518040 | 56945 | 10.99%
IL: Marengo - Grant - (PW) | IL | SOL-11147 | 224264 | 0 | 224264 |  | 193523.2 | 30740.8 | 15.88%
NY: Cambridge - Cambridge (PW) | NY | SOL-11126 | 112395.156 | 100094.105 | 12301.051 | 12.29% | 537994 | -425598.844 | -79.11%
NY: Whitesville - Independence North | NY | SOL-11186 | 276854 | 0 | 276854 |  | 0 | 0
IL: Beecher - Cottage Grove North (PW) | IL | SOL-11114 | 213014 | 231407.5 | -18393.5 | -7.949% | 186272 | 26742 | 14.36%
IL: Beecher - Cottage Grove South (PW) | IL | SOL-11115 | 225299 | 297560.1 | -72261.1 | -24.28% | 174687 | 50612 | 28.97%
IL: Harvard - 9618 US HWY 14 (PW) | IL | SOL-11110 | 182768 | 396799.6 | -214031.6 | -53.94% | 172612 | 10156 | 5.884%
IL: Beecher - 701 E Goodenow Rd (PW) | IL | SOL-11112 | 26786 | 28958.46 | -2172.46 | -7.502% | 178720 | -151934 | -85.01%
NY: Stormville - Green Haven - (IRA) | NY | SOL-11151 | 160195.6 | 0 | 160195.6 |  | 0 | 0
IL: Hillsboro - Anacott (PW) | IL | SOL-11134 | 634429 | 0 | 634429 |  | 553720 | 80709
IL: Manhattan - Gougar (PW) | IL | SOL-11148 | 121126 | 145932.1 | -24806.1 |  | 208326.7 | -87200.7
IL: Morrison - Sawyer (PW) | IL | SOL-11176
IL: Kankakee - Jeffery (PW) | IL | SOL-11173
IL: Freeport - 2240 South 18th Ave (PW) | IL | SOL-11084

## 2nd Qtr
Generate Capital |  |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | %
K026 | NY | SOL-10356 | 0 | 0 | 0 |  | 0 | 0
K041 | NY | SOL-10357 | 0 | 0 | 0 |  | 0 | 0
K043 | NY | SOL-10358 | 0 | 0 | 0 |  | 0 | 0
K058 | NY | SOL-10360 | 0 | 0 | 0 |  | 0 | 0
K115 | NY | SOL-10361 | 0 | 0 | 0 |  | 0 | 0
K152 | NY | SOL-10362 | 0 | 0 | 0 |  | 0 | 0
K166 | NY | SOL-10363 | 0 | 0 | 0 |  | 0 | 0
K206 | NY | SOL-10927 | 0 | 0 | 0 |  | 0 | 0
K251 | NY | SOL-10365 | 0 | 0 | 0 |  | 0 | 0
K269 | NY | SOL-10366 | 0 | 0 | 0 |  | 0 | 0
K273 | NY | SOL-10367 | 0 | 0 | 0 |  | 0 | 0
K287 | NY | SOL-10919 | 0 | 0 | 0 |  | 0 | 0
K298 | NY | SOL-10368 | 0 | 0 | 0 |  | 0 | 0
K335 | NY | SOL-10370 | 0 | 0 | 0 |  | 0 | 0
K345 | NY | SOL-10920 | 0 | 0 | 0 |  | 0 | 0
K445 | NY | SOL-10373 | 0 | 0 | 0 |  | 0 | 0
K495 | NY | SOL-10374 | 0 | 0 | 0 |  | 0 | 0
M020 | NY | SOL-10380 | 0 | 0 | 0 |  | 0 | 0
M092 | NY | SOL-10383 | 0 | 0 | 0 |  | 0 | 0
M143 | NY | SOL-10384 | 0 | 0 | 0 |  | 0 | 0
M144 | NY | SOL-10385 | 0 | 0 | 0 |  | 0 | 0
M167 | NY | SOL-10386 | 0 | 0 | 0 |  | 0 | 0
M188 | NY | SOL-10387 | 0 | 0 | 0 |  | 0 | 0
EMHC | NY | SOL-10351 | 0 | 0 | 0 |  | 0 | 0
Q008 | NY | SOL-10397 | 0 | 0 | 0 |  | 0 | 0
Q018 | NY | SOL-10398 | 0 | 0 | 0 |  | 0 | 0
Q021 | NY | SOL-10399 | 0 | 0 | 0 |  | 0 | 0
Q025 | NY | SOL-10400 | 0 | 0 | 0 |  | 0 | 0
Q074 | NY | SOL-10402 | 0 | 0 | 0 |  | 0 | 0
Q115 | NY | SOL-10872 | 0 | 0 | 0 |  | 0 | 0
Q139 | NY | SOL-10403 | 0 | 0 | 0 |  | 0 | 0
Q157 | NY | SOL-10404 | 0 | 0 | 0 |  | 0 | 0
Q192 | NY | SOL-10406 | 0 | 0 | 0 |  | 0 | 0
Q210 | NY | SOL-10407 | 0 | 0 | 0 |  | 0 | 0
Q229 | NY | SOL-10408 | 0 | 0 | 0 |  | 0 | 0
Q231 | NY | SOL-10870 | 0 | 0 | 0 |  | 0 | 0
Q405 | NY | SOL-10409 | 0 | 0 | 0 |  | 0 | 0
Q435 | NY | SOL-10923 | 0 | 0 | 0 |  | 0 | 0
Q485 | NY | SOL-10869 | 0 | 0 | 0 |  | 0 | 0
Q490 | NY | SOL-10411 | 0 | 0 | 0 |  | 0 | 0
Q620 | NY | SOL-10867 | 0 | 0 | 0 |  | 0 | 0
QMOA | NY | SOL-10415 | 0 | 0 | 0 |  | 0 | 0
X024 | NY | SOL-10419 | 0 | 0 | 0 |  | 0 | 0
X026 | NY | SOL-10420 | 0 | 0 | 0 |  | 0 | 0
X090 | NY | SOL-10925 | 0 | 0 | 0 |  | 0 | 0
X117 | NY | SOL-10422 | 0 | 0 | 0 |  | 0 | 0
X125 | NY | SOL-10423 | 0 | 0 | 0 |  | 0 | 0
X134 | NY | SOL-10424 | 0 | 0 | 0 |  | 0 | 0
X135 | NY | SOL-10425 | 0 | 0 | 0 |  | 0 | 0
X139 JHS 222 | NY | SOL-10426 | 0 | 0 | 0 |  | 0 | 0
X140 | NY | SOL-10926 | 0 | 0 | 0 |  | 0 | 0
X166 | NY | SOL-10427 | 0 | 0 | 0 |  | 0 | 0
Murphy | MN | SOL-10094 | 0 | 0 | 0 |  | 0 | 0
Terning | MN | SOL-10093 | 0 | 0 | 0 |  | 0 | 0
Boas Road 04 | NY | SOL-10908 | 0 | 0 | 0 |  | 0 | 0
Kelly Bridge Farm | NY | SOL-10911 | 0 | 0 | 0 |  | 0 | 0
Pool Brook Road | NY | SOL-10909 | 0 | 0 | 0 |  | 0 | 0
Sackett Lake | NY | SOL-10910 | 0 | 0 | 0 |  | 0 | 0
Burritt Road | NY | SOL-10913 | 0 | 0 | 0 |  | 0 | 0
Villa Roma 1 | NY | SOL-10914 | 0 | 0 | 0 |  | 0 | 0
Villa Roma 2 | NY | SOL-10915 | 0 | 0 | 0 |  | 0 | 0
Washington 1 | NY | SOL-10912 | 0 | 0 | 0 |  | 0 | 0
Washington 3 | NY | SOL-10828 | 0 | 0 | 0 |  | 0 | 0
Washington 4 | NY | SOL-10829 | 0 | 0 | 0 |  | 0 | 0
Big Tree | NY | SOL-10966 | 0 | 0 | 0 |  | 0 | 0
Canoga | NY | SOL-10965 | 0 | 0 | 0 |  | 0 | 0
County Route 84 | NY | SOL-10967 | 0 | 0 | 0 |  | 0 | 0
Donati | NY | SOL-10968 | 0 | 0 | 0 |  | 0 | 0
Henrietta | NY | SOL-10972 | 0 | 0 | 0 |  | 0 | 0
NY 70 | NY | SOL-10970 | 0 | 0 | 0 |  | 0 | 0
Reid | NY | SOL-10991 | 0 | 0 | 0 |  | 0 | 0
Sangolqui | NY | SOL-10975 | 0 | 0 | 0 |  | 0 | 0
State Highway 17B | NY | SOL-10988 | 0 | 0 | 0 |  | 0 | 0
State Route 14A | NY | SOL-10997 | 0 | 0 | 0 |  | 0 | 0
West Creek | NY | SOL-10995 | 0 | 0 | 0 |  | 0 | 0
Wildflower | NY | SOL-10982 | 0 | 0 | 0 |  | 0 | 0
Glen Mary 1 | NY | SOL-10993 | 0 | 0 | 0 |  | 0 | 0
Glen Mary 2 | NY | SOL-10994 | 0 | 0 | 0 |  | 0 | 0
Telegraph 1 | NY | SOL-11003 | 0 | 0 | 0 |  | 0 | 0
Telegraph 2 | NY | SOL-11004 | 0 | 0 | 0 |  | 0 | 0
Cafferty Hill | NY | SOL-10996 | 0 | 0 | 0 |  | 0 | 0
Dunkleman | NY | SOL-11008 | 0 | 0 | 0 |  | 0 | 0
Route 19 1 | NY | SOL-11001 | 0 | 0 | 0 |  | 0 | 0
Route 19 2 | NY | SOL-11002 | 0 | 0 | 0 |  | 0 | 0
Yellow Mills 1 | NY | SOL-11006 | 0 | 0 | 0 |  | 0 | 0
Yellow Mills 2 | NY | SOL-11005 | 0 | 0 | 0 |  | 0 | 0
Yellow Mills 3 | NY | SOL-11007 | 0 | 0 | 0 |  | 0 | 0
Catskill | NY | SOL-11021 | 0 | 0 | 0 |  | 0 | 0
Eddy Ridge | NY | SOL-11054 | 0 | 0 | 0 |  | 0 | 0
Ridgeway #1 | NY | SOL-11018 | 0 | 0 | 0 |  | 0 | 0
Rivard 1 | NY | SOL-11011 | 0 | 0 | 0 |  | 0 | 0
Rivard 2 | NY | SOL-11012 | 0 | 0 | 0 |  | 0 | 0
Ridgeway #2 | NY | SOL-11027 | 0 | 0 | 0 |  | 0 | 0
Spencer | NY | SOL-11017 | 0 | 0 | 0 |  | 0 | 0
Reisender | NY | SOL-10886 | 0 | 0 | 0 |  | 0 | 0
Finney | NY | SOL-10999 | 0 | 0 | 0 |  | 0 | 0
Davis Solar | NY | SOL-10958 | 0 | 0 | 0 |  | 0 | 0
Genesee | NY | SOL-10951 | 0 | 0 | 0 |  | 0 | 0
Landau I | NY | SOL-10891 | 0 | 0 | 0 |  | 0 | 0
Landau II | NY | SOL-10895 | 0 | 0 | 0 |  | 0 | 0
New Beginnings | NY | SOL-10890 | 0 | 0 | 0 |  | 0 | 0
Bullitt Farm Solar, LLC | NY | SOL-10998 | 0 | 0 | 0 |  | 0 | 0
Brodhead Solar, LLC | NY | SOL-10899 | 0 | 0 | 0 |  | 0 | 0
Svenski | NY | SOL-10894 | 0 | 0 | 0 |  | 0 | 0
Bantam | NY | SOL-10986 | 0 | 0 | 0 |  | 0 | 0
Bogart | NY | SOL-10887 | 0 | 0 | 0 |  | 0 | 0
Dubois | NY | SOL-10892 | 0 | 0 | 0 |  | 0 | 0
Salt Point | NY | SOL-10888 | 0 | 0 | 0 |  | 0 | 0
Wheatland 2A | NY | SOL-10971 | 0 | 0 | 0 |  | 0 | 0
Wheatland 2B | NY | SOL-10961 | 0 | 0 | 0 |  | 0 | 0
Brickchurch | NY | SOL-10889 | 0 | 0 | 0 |  | 0 | 0
McCarthy Solar | NY | SOL-10992 | 0 | 0 | 0 |  | 0 | 0
Costanza | NY | SOL-10907 | 0 | 0 | 0 |  | 0 | 0
Lockenhurst Pond | NY | SOL-11000 | 0 | 0 | 0 |  | 0 | 0
Drinkwater | NY | SOL-10896 | 0 | 0 | 0 |  | 0 | 0
Altamont | NY | SOL-11085 | 0 | 0 | 0 |  | 0 | 0
Krumkill North | NY | SOL-11086 | 0 | 0 | 0 |  | 0 | 0
Krumkill South | NY | SOL-11087 | 0 | 0 | 0 |  | 0 | 0
X092 | NY | SOL-11189 | 0 | 0 | 0 |  | 0 | 0
X093 | NY | SOL-10932 | 0 | 0 | 0 |  | 0 | 0
X095 | NY | SOL-10929 | 0 | 0 | 0 |  | 0 | 0
X181 | NY | SOL-10428 | 0 | 0 | 0 |  | 0 | 0
X415 | NY | SOL-10429 | 0 | 0 | 0 |  | 0 | 0
K198 | NY | SOL-10930 | 0 | 0 | 0 |  | 0 | 0
K203 | NY | SOL-11190 | 0 | 0 | 0 |  | 0 | 0
K213 | NY | SOL-11191 | 0 | 0 | 0 |  | 0 | 0
K217 | NY | SOL-10933 | 0 | 0 | 0 |  | 0 | 0
K307 | NY | SOL-10876 | 0 | 0 | 0 |  | 0 | 0
K610 | NY | SOL-11158 | 0 | 0 | 0 |  | 0 | 0
M025 | NY | SOL-10392 | 0 | 0 | 0 |  | 0 | 0
M028 | NY | SOL-10381 | 0 | 0 | 0 |  | 0 | 0
Q030 | NY | SOL-10878 | 0 | 0 | 0 |  | 0 | 0
Q130 | NY | SOL-10877 | 0 | 0 | 0 |  | 0 | 0
Q196 | NY | SOL-10879 | 0 | 0 | 0 |  | 0 | 0
Q220 | NY | SOL-10873 | 0 | 0 | 0 |  | 0 | 0
Q205 | NY | SOL-10922 | 0 | 0 | 0 |  | 0 | 0
Q400 | NY | SOL-10871 | 0 | 0 | 0 |  | 0 | 0
R003 | NY | SOL-10416 | 0 | 0 | 0 |  | 0 | 0
R007 | NY | SOL-10417 | 0 | 0 | 0 |  | 0 | 0
BK16 | NY | SOL-11093 | 0 | 0 | 0 |  | 0 | 0
Trenton - Trenton East | IL | SOL-11060 | 0 | 0 | 0 |  | 0 | 0
Trenton - Trenton West | IL | SOL-11061 | 0 | 0 | 0 |  | 0 | 0
Dakota - Dakota Solar 1 | IL | SOL-11113 | 0 | 0 | 0 |  | 0 | 0
X018 | NY | SOL-10418 | 0 | 0 | 0 |  | 0 | 0
Janiak Solar | NY | SOL-10898 | 0 | 0 | 0 |  | 0 | 0
County Route 11B | NY | SOL-10983 | 0 | 0 | 0 |  | 0 | 0
Barone | NY | SOL-11034 | 0 | 0 | 0 |  | 0 | 0
Cedarville | IL | SOL-11069 | 0 | 0 | 0 |  | 0 | 0
O'Brien Hill #1 | NY | SOL-11098 | 0 | 0 | 0 |  | 0 | 0
O'Brien Hill #2 | NY | SOL-11099 | 0 | 0 | 0 |  | 0 | 0
Trinity - Freeport | IL | SOL-11057 | 0 | 0 | 0 |  | 0 | 0
Ransom | NY | SOL-11157 | 0 | 0 | 0 |  | 0 | 0
Horseheads - Wedge | NY | SOL-11160 | 0 | 0 | 0 |  | 0 | 0
Otisville - Shoddy Hollow | NY | SOL-11185 | 0 | 0 | 0 |  | 0 | 0
Wellsville - Chenunda Creek | NY | SOL-11187 | 0 | 0 | 0 |  | 0 | 0
DC: Washington - Essex Condominium | DC | SOL-10036 | 0 | 0 | 0 |  | 0 | 0
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 0 | 0 | 0 |  | 0 | 0
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 0 | 0 | 0 |  | 0 | 0
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149 | 0 | 0 | 0 |  | 0 | 0
IL: Viola - Goldenrod - (PW) | IL | SOL-11132 | 0 | 0 | 0 |  | 0 | 0
IL: Marengo - Grant - (PW) | IL | SOL-11147 | 0 | 0 | 0 |  | 0 | 0
NY: Cambridge - Cambridge (PW) | NY | SOL-11126 | 0 | 0 | 0 |  | 0 | 0
NY: Whitesville - Independence North | NY | SOL-11186 | 0 | 0 | 0 |  | 0 | 0
IL: Beecher - Cottage Grove North (PW) | IL | SOL-11114 | 0 | 0 | 0 |  | 0 | 0
IL: Beecher - Cottage Grove South (PW) | IL | SOL-11115 | 0 | 0 | 0 |  | 0 | 0
IL: Harvard - 9618 US HWY 14 (PW) | IL | SOL-11110 | 0 | 0 | 0 |  | 0 | 0
IL: Beecher - 701 E Goodenow Rd (PW) | IL | SOL-11112 | 0 | 0 | 0 |  | 0 | 0
NY: Stormville - Green Haven - (IRA) | NY | SOL-11151 | 0 | 0 | 0 |  | 0 | 0
IL: Hillsboro - Anacott (PW) | IL | SOL-11134 | 0 | 0 | 0 |  | 0 | 0
IL: Manhattan - Gougar (PW) | IL | SOL-11148 | 0 | 0 | 0 |  | 0 | 0
IL: Morrison - Sawyer (PW) | IL | SOL-11176
IL: Kankakee - Jeffery (PW) | IL | SOL-11173
IL: Freeport - 2240 South 18th Ave (PW) | IL | SOL-11084

## 3rd Qtr
Generate Capital |  |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | %
K026 | NY | SOL-10356 | 0 | 0 | 0 |  | 0 | 0
K041 | NY | SOL-10357 | 0 | 0 | 0 |  | 0 | 0
K043 | NY | SOL-10358 | 0 | 0 | 0 |  | 0 | 0
K058 | NY | SOL-10360 | 0 | 0 | 0 |  | 0 | 0
K115 | NY | SOL-10361 | 0 | 0 | 0 |  | 0 | 0
K152 | NY | SOL-10362 | 0 | 0 | 0 |  | 0 | 0
K166 | NY | SOL-10363 | 0 | 0 | 0 |  | 0 | 0
K206 | NY | SOL-10927 | 0 | 0 | 0 |  | 0 | 0
K251 | NY | SOL-10365 | 0 | 0 | 0 |  | 0 | 0
K269 | NY | SOL-10366 | 0 | 0 | 0 |  | 0 | 0
K273 | NY | SOL-10367 | 0 | 0 | 0 |  | 0 | 0
K287 | NY | SOL-10919 | 0 | 0 | 0 |  | 0 | 0
K298 | NY | SOL-10368 | 0 | 0 | 0 |  | 0 | 0
K335 | NY | SOL-10370 | 0 | 0 | 0 |  | 0 | 0
K345 | NY | SOL-10920 | 0 | 0 | 0 |  | 0 | 0
K445 | NY | SOL-10373 | 0 | 0 | 0 |  | 0 | 0
K495 | NY | SOL-10374 | 0 | 0 | 0 |  | 0 | 0
M020 | NY | SOL-10380 | 0 | 0 | 0 |  | 0 | 0
M092 | NY | SOL-10383 | 0 | 0 | 0 |  | 0 | 0
M143 | NY | SOL-10384 | 0 | 0 | 0 |  | 0 | 0
M144 | NY | SOL-10385 | 0 | 0 | 0 |  | 0 | 0
M167 | NY | SOL-10386 | 0 | 0 | 0 |  | 0 | 0
M188 | NY | SOL-10387 | 0 | 0 | 0 |  | 0 | 0
EMHC | NY | SOL-10351 | 0 | 0 | 0 |  | 0 | 0
Q008 | NY | SOL-10397 | 0 | 0 | 0 |  | 0 | 0
Q018 | NY | SOL-10398 | 0 | 0 | 0 |  | 0 | 0
Q021 | NY | SOL-10399 | 0 | 0 | 0 |  | 0 | 0
Q025 | NY | SOL-10400 | 0 | 0 | 0 |  | 0 | 0
Q074 | NY | SOL-10402 | 0 | 0 | 0 |  | 0 | 0
Q115 | NY | SOL-10872 | 0 | 0 | 0 |  | 0 | 0
Q139 | NY | SOL-10403 | 0 | 0 | 0 |  | 0 | 0
Q157 | NY | SOL-10404 | 0 | 0 | 0 |  | 0 | 0
Q192 | NY | SOL-10406 | 0 | 0 | 0 |  | 0 | 0
Q210 | NY | SOL-10407 | 0 | 0 | 0 |  | 0 | 0
Q229 | NY | SOL-10408 | 0 | 0 | 0 |  | 0 | 0
Q231 | NY | SOL-10870 | 0 | 0 | 0 |  | 0 | 0
Q405 | NY | SOL-10409 | 0 | 0 | 0 |  | 0 | 0
Q435 | NY | SOL-10923 | 0 | 0 | 0 |  | 0 | 0
Q485 | NY | SOL-10869 | 0 | 0 | 0 |  | 0 | 0
Q490 | NY | SOL-10411 | 0 | 0 | 0 |  | 0 | 0
Q620 | NY | SOL-10867 | 0 | 0 | 0 |  | 0 | 0
QMOA | NY | SOL-10415 | 0 | 0 | 0 |  | 0 | 0
X024 | NY | SOL-10419 | 0 | 0 | 0 |  | 0 | 0
X026 | NY | SOL-10420 | 0 | 0 | 0 |  | 0 | 0
X090 | NY | SOL-10925 | 0 | 0 | 0 |  | 0 | 0
X117 | NY | SOL-10422 | 0 | 0 | 0 |  | 0 | 0
X125 | NY | SOL-10423 | 0 | 0 | 0 |  | 0 | 0
X134 | NY | SOL-10424 | 0 | 0 | 0 |  | 0 | 0
X135 | NY | SOL-10425 | 0 | 0 | 0 |  | 0 | 0
X139 JHS 222 | NY | SOL-10426 | 0 | 0 | 0 |  | 0 | 0
X140 | NY | SOL-10926 | 0 | 0 | 0 |  | 0 | 0
X166 | NY | SOL-10427 | 0 | 0 | 0 |  | 0 | 0
Murphy | MN | SOL-10094 | 0 | 0 | 0 |  | 0 | 0
Terning | MN | SOL-10093 | 0 | 0 | 0 |  | 0 | 0
Boas Road 04 | NY | SOL-10908 | 0 | 0 | 0 |  | 0 | 0
Kelly Bridge Farm | NY | SOL-10911 | 0 | 0 | 0 |  | 0 | 0
Pool Brook Road | NY | SOL-10909 | 0 | 0 | 0 |  | 0 | 0
Sackett Lake | NY | SOL-10910 | 0 | 0 | 0 |  | 0 | 0
Burritt Road | NY | SOL-10913 | 0 | 0 | 0 |  | 0 | 0
Villa Roma 1 | NY | SOL-10914 | 0 | 0 | 0 |  | 0 | 0
Villa Roma 2 | NY | SOL-10915 | 0 | 0 | 0 |  | 0 | 0
Washington 1 | NY | SOL-10912 | 0 | 0 | 0 |  | 0 | 0
Washington 3 | NY | SOL-10828 | 0 | 0 | 0 |  | 0 | 0
Washington 4 | NY | SOL-10829 | 0 | 0 | 0 |  | 0 | 0
Big Tree | NY | SOL-10966 | 0 | 0 | 0 |  | 0 | 0
Canoga | NY | SOL-10965 | 0 | 0 | 0 |  | 0 | 0
County Route 84 | NY | SOL-10967 | 0 | 0 | 0 |  | 0 | 0
Donati | NY | SOL-10968 | 0 | 0 | 0 |  | 0 | 0
Henrietta | NY | SOL-10972 | 0 | 0 | 0 |  | 0 | 0
NY 70 | NY | SOL-10970 | 0 | 0 | 0 |  | 0 | 0
Reid | NY | SOL-10991 | 0 | 0 | 0 |  | 0 | 0
Sangolqui | NY | SOL-10975 | 0 | 0 | 0 |  | 0 | 0
State Highway 17B | NY | SOL-10988 | 0 | 0 | 0 |  | 0 | 0
State Route 14A | NY | SOL-10997 | 0 | 0 | 0 |  | 0 | 0
West Creek | NY | SOL-10995 | 0 | 0 | 0 |  | 0 | 0
Wildflower | NY | SOL-10982 | 0 | 0 | 0 |  | 0 | 0
Glen Mary 1 | NY | SOL-10993 | 0 | 0 | 0 |  | 0 | 0
Glen Mary 2 | NY | SOL-10994 | 0 | 0 | 0 |  | 0 | 0
Telegraph 1 | NY | SOL-11003 | 0 | 0 | 0 |  | 0 | 0
Telegraph 2 | NY | SOL-11004 | 0 | 0 | 0 |  | 0 | 0
Cafferty Hill | NY | SOL-10996 | 0 | 0 | 0 |  | 0 | 0
Dunkleman | NY | SOL-11008 | 0 | 0 | 0 |  | 0 | 0
Route 19 1 | NY | SOL-11001 | 0 | 0 | 0 |  | 0 | 0
Route 19 2 | NY | SOL-11002 | 0 | 0 | 0 |  | 0 | 0
Yellow Mills 1 | NY | SOL-11006 | 0 | 0 | 0 |  | 0 | 0
Yellow Mills 2 | NY | SOL-11005 | 0 | 0 | 0 |  | 0 | 0
Yellow Mills 3 | NY | SOL-11007 | 0 | 0 | 0 |  | 0 | 0
Catskill | NY | SOL-11021 | 0 | 0 | 0 |  | 0 | 0
Eddy Ridge | NY | SOL-11054 | 0 | 0 | 0 |  | 0 | 0
Ridgeway #1 | NY | SOL-11018 | 0 | 0 | 0 |  | 0 | 0
Rivard 1 | NY | SOL-11011 | 0 | 0 | 0 |  | 0 | 0
Rivard 2 | NY | SOL-11012 | 0 | 0 | 0 |  | 0 | 0
Ridgeway #2 | NY | SOL-11027 | 0 | 0 | 0 |  | 0 | 0
Spencer | NY | SOL-11017 | 0 | 0 | 0 |  | 0 | 0
Reisender | NY | SOL-10886 | 0 | 0 | 0 |  | 0 | 0
Finney | NY | SOL-10999 | 0 | 0 | 0 |  | 0 | 0
Davis Solar | NY | SOL-10958 | 0 | 0 | 0 |  | 0 | 0
Genesee | NY | SOL-10951 | 0 | 0 | 0 |  | 0 | 0
Landau I | NY | SOL-10891 | 0 | 0 | 0 |  | 0 | 0
Landau II | NY | SOL-10895 | 0 | 0 | 0 |  | 0 | 0
New Beginnings | NY | SOL-10890 | 0 | 0 | 0 |  | 0 | 0
Bullitt Farm Solar, LLC | NY | SOL-10998 | 0 | 0 | 0 |  | 0 | 0
Brodhead Solar, LLC | NY | SOL-10899 | 0 | 0 | 0 |  | 0 | 0
Svenski | NY | SOL-10894 | 0 | 0 | 0 |  | 0 | 0
Bantam | NY | SOL-10986 | 0 | 0 | 0 |  | 0 | 0
Bogart | NY | SOL-10887 | 0 | 0 | 0 |  | 0 | 0
Dubois | NY | SOL-10892 | 0 | 0 | 0 |  | 0 | 0
Salt Point | NY | SOL-10888 | 0 | 0 | 0 |  | 0 | 0
Wheatland 2A | NY | SOL-10971 | 0 | 0 | 0 |  | 0 | 0
Wheatland 2B | NY | SOL-10961 | 0 | 0 | 0 |  | 0 | 0
Brickchurch | NY | SOL-10889 | 0 | 0 | 0 |  | 0 | 0
McCarthy Solar | NY | SOL-10992 | 0 | 0 | 0 |  | 0 | 0
Costanza | NY | SOL-10907 | 0 | 0 | 0 |  | 0 | 0
Lockenhurst Pond | NY | SOL-11000 | 0 | 0 | 0 |  | 0 | 0
Drinkwater | NY | SOL-10896 | 0 | 0 | 0 |  | 0 | 0
Altamont | NY | SOL-11085 | 0 | 0 | 0 |  | 0 | 0
Krumkill North | NY | SOL-11086 | 0 | 0 | 0 |  | 0 | 0
Krumkill South | NY | SOL-11087 | 0 | 0 | 0 |  | 0 | 0
X092 | NY | SOL-11189 | 0 | 0 | 0 |  | 0 | 0
X093 | NY | SOL-10932 | 0 | 0 | 0 |  | 0 | 0
X095 | NY | SOL-10929 | 0 | 0 | 0 |  | 0 | 0
X181 | NY | SOL-10428 | 0 | 0 | 0 |  | 0 | 0
X415 | NY | SOL-10429 | 0 | 0 | 0 |  | 0 | 0
K198 | NY | SOL-10930 | 0 | 0 | 0 |  | 0 | 0
K203 | NY | SOL-11190 | 0 | 0 | 0 |  | 0 | 0
K213 | NY | SOL-11191 | 0 | 0 | 0 |  | 0 | 0
K217 | NY | SOL-10933 | 0 | 0 | 0 |  | 0 | 0
K307 | NY | SOL-10876 | 0 | 0 | 0 |  | 0 | 0
K610 | NY | SOL-11158 | 0 | 0 | 0 |  | 0 | 0
M025 | NY | SOL-10392 | 0 | 0 | 0 |  | 0 | 0
M028 | NY | SOL-10381 | 0 | 0 | 0 |  | 0 | 0
Q030 | NY | SOL-10878 | 0 | 0 | 0 |  | 0 | 0
Q130 | NY | SOL-10877 | 0 | 0 | 0 |  | 0 | 0
Q196 | NY | SOL-10879 | 0 | 0 | 0 |  | 0 | 0
Q220 | NY | SOL-10873 | 0 | 0 | 0 |  | 0 | 0
Q205 | NY | SOL-10922 | 0 | 0 | 0 |  | 0 | 0
Q400 | NY | SOL-10871 | 0 | 0 | 0 |  | 0 | 0
R003 | NY | SOL-10416 | 0 | 0 | 0 |  | 0 | 0
R007 | NY | SOL-10417 | 0 | 0 | 0 |  | 0 | 0
BK16 | NY | SOL-11093 | 0 | 0 | 0 |  | 0 | 0
Trenton - Trenton East | IL | SOL-11060 | 0 | 0 | 0 |  | 0 | 0
Trenton - Trenton West | IL | SOL-11061 | 0 | 0 | 0 |  | 0 | 0
Dakota - Dakota Solar 1 | IL | SOL-11113 | 0 | 0 | 0 |  | 0 | 0
X018 | NY | SOL-10418 | 0 | 0 | 0 |  | 0 | 0
Janiak Solar | NY | SOL-10898 | 0 | 0 | 0 |  | 0 | 0
County Route 11B | NY | SOL-10983 | 0 | 0 | 0 |  | 0 | 0
Barone | NY | SOL-11034 | 0 | 0 | 0 |  | 0 | 0
Cedarville | IL | SOL-11069 | 0 | 0 | 0 |  | 0 | 0
O'Brien Hill #1 | NY | SOL-11098 | 0 | 0 | 0 |  | 0 | 0
O'Brien Hill #2 | NY | SOL-11099 | 0 | 0 | 0 |  | 0 | 0
Trinity - Freeport | IL | SOL-11057 | 0 | 0 | 0 |  | 0 | 0
Ransom | NY | SOL-11157 | 0 | 0 | 0 |  | 0 | 0
Horseheads - Wedge | NY | SOL-11160 | 0 | 0 | 0 |  | 0 | 0
Otisville - Shoddy Hollow | NY | SOL-11185 | 0 | 0 | 0 |  | 0 | 0
Wellsville - Chenunda Creek | NY | SOL-11187 | 0 | 0 | 0 |  | 0 | 0
DC: Washington - Essex Condominium | DC | SOL-10036 | 0 | 0 | 0 |  | 0 | 0
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 0 | 0 | 0 |  | 0 | 0
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 0 | 0 | 0 |  | 0 | 0
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149 | 0 | 0 | 0 |  | 0 | 0
IL: Viola - Goldenrod - (PW) | IL | SOL-11132 | 0 | 0 | 0 |  | 0 | 0
IL: Marengo - Grant - (PW) | IL | SOL-11147 | 0 | 0 | 0 |  | 0 | 0
NY: Cambridge - Cambridge (PW) | NY | SOL-11126 | 0 | 0 | 0 |  | 0 | 0
NY: Whitesville - Independence North | NY | SOL-11186 | 0 | 0 | 0 |  | 0 | 0
IL: Beecher - Cottage Grove North (PW) | IL | SOL-11114 | 0 | 0 | 0 |  | 0 | 0
IL: Beecher - Cottage Grove South (PW) | IL | SOL-11115 | 0 | 0 | 0 |  | 0 | 0
IL: Harvard - 9618 US HWY 14 (PW) | IL | SOL-11110 | 0 | 0 | 0 |  | 0 | 0
IL: Beecher - 701 E Goodenow Rd (PW) | IL | SOL-11112 | 0 | 0 | 0 |  | 0 | 0
NY: Stormville - Green Haven - (IRA) | NY | SOL-11151 | 0 | 0 | 0 |  | 0 | 0
IL: Hillsboro - Anacott (PW) | IL | SOL-11134 | 0 | 0 | 0 |  | 0 | 0
IL: Manhattan - Gougar (PW) | IL | SOL-11148 | 0 | 0 | 0 |  | 0 | 0
IL: Morrison - Sawyer (PW) | IL | SOL-11176
IL: Kankakee - Jeffery (PW) | IL | SOL-11173
IL: Freeport - 2240 South 18th Ave (PW) | IL | SOL-11084

## 4th Qtr
Generate Capital |  |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | %
K026 | NY | SOL-10356 | 0 | 0 | 0 |  | 0 | 0
K041 | NY | SOL-10357 | 0 | 0 | 0 |  | 0 | 0
K043 | NY | SOL-10358 | 0 | 0 | 0 |  | 0 | 0
K058 | NY | SOL-10360 | 0 | 0 | 0 |  | 0 | 0
K115 | NY | SOL-10361 | 0 | 0 | 0 |  | 0 | 0
K152 | NY | SOL-10362 | 0 | 0 | 0 |  | 0 | 0
K166 | NY | SOL-10363 | 0 | 0 | 0 |  | 0 | 0
K206 | NY | SOL-10927 | 0 | 0 | 0 |  | 0 | 0
K251 | NY | SOL-10365 | 0 | 0 | 0 |  | 0 | 0
K269 | NY | SOL-10366 | 0 | 0 | 0 |  | 0 | 0
K273 | NY | SOL-10367 | 0 | 0 | 0 |  | 0 | 0
K287 | NY | SOL-10919 | 0 | 0 | 0 |  | 0 | 0
K298 | NY | SOL-10368 | 0 | 0 | 0 |  | 0 | 0
K335 | NY | SOL-10370 | 0 | 0 | 0 |  | 0 | 0
K345 | NY | SOL-10920 | 0 | 0 | 0 |  | 0 | 0
K445 | NY | SOL-10373 | 0 | 0 | 0 |  | 0 | 0
K495 | NY | SOL-10374 | 0 | 0 | 0 |  | 0 | 0
M020 | NY | SOL-10380 | 0 | 0 | 0 |  | 0 | 0
M092 | NY | SOL-10383 | 0 | 0 | 0 |  | 0 | 0
M143 | NY | SOL-10384 | 0 | 0 | 0 |  | 0 | 0
M144 | NY | SOL-10385 | 0 | 0 | 0 |  | 0 | 0
M167 | NY | SOL-10386 | 0 | 0 | 0 |  | 0 | 0
M188 | NY | SOL-10387 | 0 | 0 | 0 |  | 0 | 0
EMHC | NY | SOL-10351 | 0 | 0 | 0 |  | 0 | 0
Q008 | NY | SOL-10397 | 0 | 0 | 0 |  | 0 | 0
Q018 | NY | SOL-10398 | 0 | 0 | 0 |  | 0 | 0
Q021 | NY | SOL-10399 | 0 | 0 | 0 |  | 0 | 0
Q025 | NY | SOL-10400 | 0 | 0 | 0 |  | 0 | 0
Q074 | NY | SOL-10402 | 0 | 0 | 0 |  | 0 | 0
Q115 | NY | SOL-10872 | 0 | 0 | 0 |  | 0 | 0
Q139 | NY | SOL-10403 | 0 | 0 | 0 |  | 0 | 0
Q157 | NY | SOL-10404 | 0 | 0 | 0 |  | 0 | 0
Q192 | NY | SOL-10406 | 0 | 0 | 0 |  | 0 | 0
Q210 | NY | SOL-10407 | 0 | 0 | 0 |  | 0 | 0
Q229 | NY | SOL-10408 | 0 | 0 | 0 |  | 0 | 0
Q231 | NY | SOL-10870 | 0 | 0 | 0 |  | 0 | 0
Q405 | NY | SOL-10409 | 0 | 0 | 0 |  | 0 | 0
Q435 | NY | SOL-10923 | 0 | 0 | 0 |  | 0 | 0
Q485 | NY | SOL-10869 | 0 | 0 | 0 |  | 0 | 0
Q490 | NY | SOL-10411 | 0 | 0 | 0 |  | 0 | 0
Q620 | NY | SOL-10867 | 0 | 0 | 0 |  | 0 | 0
QMOA | NY | SOL-10415 | 0 | 0 | 0 |  | 0 | 0
X024 | NY | SOL-10419 | 0 | 0 | 0 |  | 0 | 0
X026 | NY | SOL-10420 | 0 | 0 | 0 |  | 0 | 0
X090 | NY | SOL-10925 | 0 | 0 | 0 |  | 0 | 0
X117 | NY | SOL-10422 | 0 | 0 | 0 |  | 0 | 0
X125 | NY | SOL-10423 | 0 | 0 | 0 |  | 0 | 0
X134 | NY | SOL-10424 | 0 | 0 | 0 |  | 0 | 0
X135 | NY | SOL-10425 | 0 | 0 | 0 |  | 0 | 0
X139 JHS 222 | NY | SOL-10426 | 0 | 0 | 0 |  | 0 | 0
X140 | NY | SOL-10926 | 0 | 0 | 0 |  | 0 | 0
X166 | NY | SOL-10427 | 0 | 0 | 0 |  | 0 | 0
Murphy | MN | SOL-10094 | 0 | 0 | 0 |  | 0 | 0
Terning | MN | SOL-10093 | 0 | 0 | 0 |  | 0 | 0
Boas Road 04 | NY | SOL-10908 | 0 | 0 | 0 |  | 0 | 0
Kelly Bridge Farm | NY | SOL-10911 | 0 | 0 | 0 |  | 0 | 0
Pool Brook Road | NY | SOL-10909 | 0 | 0 | 0 |  | 0 | 0
Sackett Lake | NY | SOL-10910 | 0 | 0 | 0 |  | 0 | 0
Burritt Road | NY | SOL-10913 | 0 | 0 | 0 |  | 0 | 0
Villa Roma 1 | NY | SOL-10914 | 0 | 0 | 0 |  | 0 | 0
Villa Roma 2 | NY | SOL-10915 | 0 | 0 | 0 |  | 0 | 0
Washington 1 | NY | SOL-10912 | 0 | 0 | 0 |  | 0 | 0
Washington 3 | NY | SOL-10828 | 0 | 0 | 0 |  | 0 | 0
Washington 4 | NY | SOL-10829 | 0 | 0 | 0 |  | 0 | 0
Big Tree | NY | SOL-10966 | 0 | 0 | 0 |  | 0 | 0
Canoga | NY | SOL-10965 | 0 | 0 | 0 |  | 0 | 0
County Route 84 | NY | SOL-10967 | 0 | 0 | 0 |  | 0 | 0
Donati | NY | SOL-10968 | 0 | 0 | 0 |  | 0 | 0
Henrietta | NY | SOL-10972 | 0 | 0 | 0 |  | 0 | 0
NY 70 | NY | SOL-10970 | 0 | 0 | 0 |  | 0 | 0
Reid | NY | SOL-10991 | 0 | 0 | 0 |  | 0 | 0
Sangolqui | NY | SOL-10975 | 0 | 0 | 0 |  | 0 | 0
State Highway 17B | NY | SOL-10988 | 0 | 0 | 0 |  | 0 | 0
State Route 14A | NY | SOL-10997 | 0 | 0 | 0 |  | 0 | 0
West Creek | NY | SOL-10995 | 0 | 0 | 0 |  | 0 | 0
Wildflower | NY | SOL-10982 | 0 | 0 | 0 |  | 0 | 0
Glen Mary 1 | NY | SOL-10993 | 0 | 0 | 0 |  | 0 | 0
Glen Mary 2 | NY | SOL-10994 | 0 | 0 | 0 |  | 0 | 0
Telegraph 1 | NY | SOL-11003 | 0 | 0 | 0 |  | 0 | 0
Telegraph 2 | NY | SOL-11004 | 0 | 0 | 0 |  | 0 | 0
Cafferty Hill | NY | SOL-10996 | 0 | 0 | 0 |  | 0 | 0
Dunkleman | NY | SOL-11008 | 0 | 0 | 0 |  | 0 | 0
Route 19 1 | NY | SOL-11001 | 0 | 0 | 0 |  | 0 | 0
Route 19 2 | NY | SOL-11002 | 0 | 0 | 0 |  | 0 | 0
Yellow Mills 1 | NY | SOL-11006 | 0 | 0 | 0 |  | 0 | 0
Yellow Mills 2 | NY | SOL-11005 | 0 | 0 | 0 |  | 0 | 0
Yellow Mills 3 | NY | SOL-11007 | 0 | 0 | 0 |  | 0 | 0
Catskill | NY | SOL-11021 | 0 | 0 | 0 |  | 0 | 0
Eddy Ridge | NY | SOL-11054 | 0 | 0 | 0 |  | 0 | 0
Ridgeway #1 | NY | SOL-11018 | 0 | 0 | 0 |  | 0 | 0
Rivard 1 | NY | SOL-11011 | 0 | 0 | 0 |  | 0 | 0
Rivard 2 | NY | SOL-11012 | 0 | 0 | 0 |  | 0 | 0
Ridgeway #2 | NY | SOL-11027 | 0 | 0 | 0 |  | 0 | 0
Spencer | NY | SOL-11017 | 0 | 0 | 0 |  | 0 | 0
Reisender | NY | SOL-10886 | 0 | 0 | 0 |  | 0 | 0
Finney | NY | SOL-10999 | 0 | 0 | 0 |  | 0 | 0
Davis Solar | NY | SOL-10958 | 0 | 0 | 0 |  | 0 | 0
Genesee | NY | SOL-10951 | 0 | 0 | 0 |  | 0 | 0
Landau I | NY | SOL-10891 | 0 | 0 | 0 |  | 0 | 0
Landau II | NY | SOL-10895 | 0 | 0 | 0 |  | 0 | 0
New Beginnings | NY | SOL-10890 | 0 | 0 | 0 |  | 0 | 0
Bullitt Farm Solar, LLC | NY | SOL-10998 | 0 | 0 | 0 |  | 0 | 0
Brodhead Solar, LLC | NY | SOL-10899 | 0 | 0 | 0 |  | 0 | 0
Svenski | NY | SOL-10894 | 0 | 0 | 0 |  | 0 | 0
Bantam | NY | SOL-10986 | 0 | 0 | 0 |  | 0 | 0
Bogart | NY | SOL-10887 | 0 | 0 | 0 |  | 0 | 0
Dubois | NY | SOL-10892 | 0 | 0 | 0 |  | 0 | 0
Salt Point | NY | SOL-10888 | 0 | 0 | 0 |  | 0 | 0
Wheatland 2A | NY | SOL-10971 | 0 | 0 | 0 |  | 0 | 0
Wheatland 2B | NY | SOL-10961 | 0 | 0 | 0 |  | 0 | 0
Brickchurch | NY | SOL-10889 | 0 | 0 | 0 |  | 0 | 0
McCarthy Solar | NY | SOL-10992 | 0 | 0 | 0 |  | 0 | 0
Costanza | NY | SOL-10907 | 0 | 0 | 0 |  | 0 | 0
Lockenhurst Pond | NY | SOL-11000 | 0 | 0 | 0 |  | 0 | 0
Drinkwater | NY | SOL-10896 | 0 | 0 | 0 |  | 0 | 0
Altamont | NY | SOL-11085 | 0 | 0 | 0 |  | 0 | 0
Krumkill North | NY | SOL-11086 | 0 | 0 | 0 |  | 0 | 0
Krumkill South | NY | SOL-11087 | 0 | 0 | 0 |  | 0 | 0
X092 | NY | SOL-11189 | 0 | 0 | 0 |  | 0 | 0
X093 | NY | SOL-10932 | 0 | 0 | 0 |  | 0 | 0
X095 | NY | SOL-10929 | 0 | 0 | 0 |  | 0 | 0
X181 | NY | SOL-10428 | 0 | 0 | 0 |  | 0 | 0
X415 | NY | SOL-10429 | 0 | 0 | 0 |  | 0 | 0
K198 | NY | SOL-10930 | 0 | 0 | 0 |  | 0 | 0
K203 | NY | SOL-11190 | 0 | 0 | 0 |  | 0 | 0
K213 | NY | SOL-11191 | 0 | 0 | 0 |  | 0 | 0
K217 | NY | SOL-10933 | 0 | 0 | 0 |  | 0 | 0
K307 | NY | SOL-10876 | 0 | 0 | 0 |  | 0 | 0
K610 | NY | SOL-11158 | 0 | 0 | 0 |  | 0 | 0
M025 | NY | SOL-10392 | 0 | 0 | 0 |  | 0 | 0
M028 | NY | SOL-10381 | 0 | 0 | 0 |  | 0 | 0
Q030 | NY | SOL-10878 | 0 | 0 | 0 |  | 0 | 0
Q130 | NY | SOL-10877 | 0 | 0 | 0 |  | 0 | 0
Q196 | NY | SOL-10879 | 0 | 0 | 0 |  | 0 | 0
Q220 | NY | SOL-10873 | 0 | 0 | 0 |  | 0 | 0
Q205 | NY | SOL-10922 | 0 | 0 | 0 |  | 0 | 0
Q400 | NY | SOL-10871 | 0 | 0 | 0 |  | 0 | 0
R003 | NY | SOL-10416 | 0 | 0 | 0 |  | 0 | 0
R007 | NY | SOL-10417 | 0 | 0 | 0 |  | 0 | 0
BK16 | NY | SOL-11093 | 0 | 0 | 0 |  | 0 | 0
Trenton - Trenton East | IL | SOL-11060 | 0 | 0 | 0 |  | 0 | 0
Trenton - Trenton West | IL | SOL-11061 | 0 | 0 | 0 |  | 0 | 0
Dakota - Dakota Solar 1 | IL | SOL-11113 | 0 | 0 | 0 |  | 0 | 0
X018 | NY | SOL-10418 | 0 | 0 | 0 |  | 0 | 0
Janiak Solar | NY | SOL-10898 | 0 | 0 | 0 |  | 0 | 0
County Route 11B | NY | SOL-10983 | 0 | 0 | 0 |  | 0 | 0
Barone | NY | SOL-11034 | 0 | 0 | 0 |  | 0 | 0
Cedarville | IL | SOL-11069 | 0 | 0 | 0 |  | 0 | 0
O'Brien Hill #1 | NY | SOL-11098 | 0 | 0 | 0 |  | 0 | 0
O'Brien Hill #2 | NY | SOL-11099 | 0 | 0 | 0 |  | 0 | 0
Trinity - Freeport | IL | SOL-11057 | 0 | 0 | 0 |  | 0 | 0
Ransom | NY | SOL-11157 | 0 | 0 | 0 |  | 0 | 0
Horseheads - Wedge | NY | SOL-11160 | 0 | 0 | 0 |  | 0 | 0
Otisville - Shoddy Hollow | NY | SOL-11185 | 0 | 0 | 0 |  | 0 | 0
Wellsville - Chenunda Creek | NY | SOL-11187 | 0 | 0 | 0 |  | 0 | 0
DC: Washington - Essex Condominium | DC | SOL-10036 | 0 | 0 | 0 |  | 0 | 0
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 0 | 0 | 0 |  | 0 | 0
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 0 | 0 | 0 |  | 0 | 0
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149 | 0 | 0 | 0 |  | 0 | 0
IL: Viola - Goldenrod - (PW) | IL | SOL-11132 | 0 | 0 | 0 |  | 0 | 0
IL: Marengo - Grant - (PW) | IL | SOL-11147 | 0 | 0 | 0 |  | 0 | 0
NY: Cambridge - Cambridge (PW) | NY | SOL-11126 | 0 | 0 | 0 |  | 0 | 0
NY: Whitesville - Independence North | NY | SOL-11186 | 0 | 0 | 0 |  | 0 | 0
IL: Beecher - Cottage Grove North (PW) | IL | SOL-11114 | 0 | 0 | 0 |  | 0 | 0
IL: Beecher - Cottage Grove South (PW) | IL | SOL-11115 | 0 | 0 | 0 |  | 0 | 0
IL: Harvard - 9618 US HWY 14 (PW) | IL | SOL-11110 | 0 | 0 | 0 |  | 0 | 0
IL: Beecher - 701 E Goodenow Rd (PW) | IL | SOL-11112 | 0 | 0 | 0 |  | 0 | 0
NY: Stormville - Green Haven - (IRA) | NY | SOL-11151 | 0 | 0 | 0 |  | 0 | 0
IL: Hillsboro - Anacott (PW) | IL | SOL-11134 | 0 | 0 | 0 |  | 0 | 0
IL: Manhattan - Gougar (PW) | IL | SOL-11148 | 0 | 0 | 0 |  | 0 | 0
IL: Morrison - Sawyer (PW) | IL | SOL-11176
IL: Kankakee - Jeffery (PW) | IL | SOL-11173
IL: Freeport - 2240 South 18th Ave (PW) | IL | SOL-11084

## Jan
Generate Capital |  |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  |  | 6351649.2795 | 4972201.081 | 1379448.1985 | 27.74% | 10776605.2111 | -4424955.9315 | -41.06% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
K026 | NY | SOL-10356 | 8328.108 | 12159.88 | -3831.772 | -31.51% | 11055.95 | -2727.842 | -24.67% | 1. Meter B phase currents dropped to Zero whole month. Need to replace CT's.On 12/30 CT's were removed 2. Site production was low from 01/25 due to snow. | 1. SR107464, SR113666 | 1. Pending | SR113666
K041 | NY | SOL-10357 | 5871.5312 | 9407.467 | -3535.9358 | -37.59% | 9924 | -4052.4688 | -40.84% | 1. Site production was low from 01/25 due to snow. 2. Inverter 2 has afternoon shading.
K043 | NY | SOL-10358 | 7527.0625 | 10861.06 | -3333.9975 | -30.7% | 2303 | 5224.0625 | 226.8% | 1. Estimated values are low in AE we have also verified the file which was given by GC 2. Site production was low from 01/25 due to snow.
K058 | NY | SOL-10360 | 5490.6875 | 8437.168 | -2946.4805 | -34.92% | 9101.326 | -3610.6385 | -39.67% | 1. Site production was low on 01/17, 01/18 and from 01/25 due to snow.
K115 | NY | SOL-10361 | 3483.875 | 7300.807 | -3816.932 | -52.28% | 5565.882 | -2082.007 | -37.41% | 1. Site production was low from 01/25 due to snow.
K152 | NY | SOL-10362 | 2067.4375 | 4344.89 | -2277.4525 | -52.42% | 3567 | -1499.5625 | -42.04% | 1. 1 Optimizer was offline. 2. Site production was low from 01/25 due to snow. | 1.SR110236 | 1. pending
K166 | NY | SOL-10363 | 7527.75 | 16102.59 | -8574.84 | -53.25% | 12064.56 | -4536.81 | -37.6% | 1. 3 optimizers are offline: 2.0.160, 3.0.17, 3.0.33 2. Site production was low from 01/25 due to snow. | 1.SR095666 | 1. pending
K206 | NY | SOL-10927 | 5243.875 | 5255.242 | -11.367 | -0.2163% | 6894 | -1650.125 | -23.94% | 1. Site production was low on 01/25 and 01/26 due to snow.
K251 | NY | SOL-10365 | 5285.5625 | 0 | 5285.5625 |  | 8483.094 | -3197.5315 | -37.69% | 1. Weather station stopped communicating on 11/22 at 07:00. replacement POA. 2. Site production was low on 01/25 and 01/26 due to snow. | 1. SR093633, SR110369 | 1. Denied | SR110369
K269 | NY | SOL-10366 | 4482.4375 | 7734.486 | -3252.0485 | -42.05% | 7723.149 | -3240.7115 | -41.96% | 1. Inverter 1, Unit 3 (7e97f366) went offline on 01/07 due to a reported "DC isolation fault". A technician later identified and repaired squirrel damage, and the unit was back online on 01/14. 2. Site was offline from 01/25 due to snow. 3. Inverters producing as expected and expected value and forecasted energy values difference. | 1. SR114232 | 1. Closed
K273 | NY | SOL-10367 | 4816.2673 | 0 | 4816.2673 |  | 9546 | -4729.7327 | -49.55% | 1. 26 optimizers are down for roof repair. 2. Weather station stopped communicating since 06/14/24. 3. Site production was low on 01/17, 01/18 and from 01/25 due to snow. | 1.SR093924 2. SR086842 | 1. Pending 2. Closed | SR086842
K287 | NY | SOL-10919 | 4113.1875 | 5386.828 | -1273.6405 | -23.64% | 7303 | -3189.8125 | -43.68% | 1. Site production was low on 01/17, 01/18 and from 01/25 due to snow.
K298 | NY | SOL-10368 | 3551.375 | 6917.152 | -3365.777 | -48.66% | 6119 | -2567.625 | -41.96% | 1. Site production was low on 01/17, 01/18 and from 01/25 due to snow.
K335 | NY | SOL-10370 | 4369.8125 | 7302.417 | -2932.6045 | -40.16% | 8179 | -3809.1875 | -46.57% | 1. Inverter 1 has minor shading issue. 2. Site production was low on 01/17, 01/18 and from 01/25 due to snow.
K345 | NY | SOL-10920 | 5288.7188 | 5418.434 | -129.7153 | -2.394% | 6910 | -1621.2812 | -23.46% | 1. Site production was low on 01/17, 01/18 and from 01/25 due to snow.
K445 | NY | SOL-10373 | 4901 | 7406.31 | -2505.31 | -33.83% | 6782.615 | -1881.615 | -27.74% | 1. Site production was low on 01/17, 01/18, 01/25 and 01/26 due to snow.
K495 | NY | SOL-10374 | 20126.75 | 28959.78 | -8833.03 | -30.5% | 49040.59 | -28913.84 | -58.96% | 1. Inverter 4 was offline on 12/09 and reporting "critical temperature on AC terminal" and back online at 11:00 on 01/16. 2. Site production was low from 01/25 due to snow. | 1. SR112416 | 1. Closed
M020 | NY | SOL-10380 | 5231.9688 | 7045.739 | -1813.7702 | -25.74% | 9125 | -3893.0312 | -42.66% | 1. Site production was low on 01/17, 01/18 and from 01/25 due to snow.
M092 | NY | SOL-10383 | 4773.3125 | 7344.285 | -2570.9725 | -35.01% | 8137.596 | -3364.2835 | -41.34% | 1. Site production was low on 01/17, 01/18 and from 01/25 due to snow.
M143 | NY | SOL-10384 | 4837.8125 | 7607.831 | -2770.0185 | -36.41% | 8659.26 | -3821.4475 | -44.13% | 1. Site production was low on 01/17, 01/18 and from 01/25 due to snow.
M144 | NY | SOL-10385 | 7799.625 | 13319.92 | -5520.295 | -41.44% | 23584.05 | -15784.425 | -66.93% | 1. Site production was low on 01/17, 01/18 and from 01/25 due to snow. 2. Inverter 2 has afternoon shading.
M167 | NY | SOL-10386 | 4931.2188 | 5726.784 | -795.5652 | -13.89% | 8065.708 | -3134.4892 | -38.86% | 1. Site production was low on 01/10,01/14,01/17,01/18 and from 01/25 due to now.
M188 | NY | SOL-10387 | 4259.3614 | 6602.944 | -2343.5826 | -35.49% | 12343.55 | -8084.1886 | -65.49% | 1. Site production was low on 01/17, 01/18 and from 01/25 due to snow. 2. Inverter 2 has afternoon shading.
EMHC | NY | SOL-10351 | 1375.3594 | 1501.042 | -125.6826 | -8.373% | 2307.806 | -932.4466 | -40.4% | 1.Module 1.0.90 (21772020-D8) No communication. 1.0.29 - 217E44D3-B6 - offline. | 1. SR093236 | 1. Pending
Q008 | NY | SOL-10397 | 7064.75 | 10490.4 | -3425.65 | -32.66% | 10992 | -3927.25 | -35.73% | 1. Site production was low on 01/17, 01/18 and from 01/25 due to snow.
Q018 | NY | SOL-10398 | 4452.3125 | 6553.947 | -2101.6345 | -32.07% | 6648.922 | -2196.6095 | -33.04% | 1. Site production was low on 01/17, 01/18 and from 01/25 due to snow.
Q021 | NY | SOL-10399 | 3531.9375 | 8384.728 | -4852.7905 | -57.88% | 5197.547 | -1665.6095 | -32.05% | 1. Site production was low on 01/17, 01/18 and from 01/25 due to snow.
Q025 | NY | SOL-10400 | 6147.875 | 8484.735 | -2336.86 | -27.54% | 7767 | -1619.125 | -20.85% | 1. Actual vs Forcasted delta is showing 21% due to Forcasted energy recording high possibly due to data glitch (similar event observe last 2 years). 2.Site production was low on 01/10,01/14,01/17,01/18,01/25/01/26 due to nsow
Q074 | NY | SOL-10402 | 0 | 0 | 0 |  | 0 | 0 |  | 1. Home run Solar shut off the site at 08:30am on 09/22 to perform roof repairs. | 1. SR102529 | 1. Pending
Q115 | NY | SOL-10872 | 4946.6875 | 7759.496 | -2812.8085 | -36.25% | 8113.763 | -3167.0755 | -39.03% | 1. Site production was low on 01/17, 01/18 and from 01/25 due to snow.
Q139 | NY | SOL-10403 | 2738.25 | 5967.658 | -3229.408 | -54.12% | 5168 | -2429.75 | -47.02% | 1. Inverter 2 went offline at 07:00 on 01/07 and back online at 08:00 on 01/09. The inverter went offline again at 07:00 on 01/11 and was back online at 07:00 on 01/12. It tripped offline once again at 07:00 on 01/13. A technician found squirrel damage and replaced replaced, and the inverter was back online at 09:15 on 01/15. 2. Some optimizers with production issues 1264FFBB-30 - Half production 12639DA9-BB - Half production on 01/15. After technician replaced two optimizers, and an RMA replacement is pending. | 1. SR114229 2. SR088282 | 1. Closed 2. Pending | SR088282
Q157 | NY | SOL-10404 | 5387.0765 | 13435.68 | -8048.6035 | -59.9% | 9154.302 | -3767.2255 | -41.15% | 1. Site is underperforming by 11KW due to snow accumulation over panels | 1. SR114558 | 1. Pending
Q192 | NY | SOL-10406 | 8066.875 | 13154.35 | -5087.475 | -38.68% | 13840.9 | -5774.025 | -41.72% | 1. Inverter 3, Unit 3.1 tripped offline at 12:00 on 11/17. After a technician replaced a faulty optimizer and the inverter powerhead unit, the inverter and unit was back online at 13:30 on 01/08. | 1. SR112392 | 1. Closed
Q210 | NY | SOL-10407 | 7166 | 9278.773 | -2112.773 | -22.77% | 11622 | -4456 | -38.34% | 1. Site production was low on 01/17, 01/18, 01/25 and 01/26 due to snow.
Q229 | NY | SOL-10408 | 2652.625 | 6651.485 | -3998.86 | -60.12% | 3668.691 | -1016.066 | -27.7% | 1. 8 optimizers are offline. GenC confirms that Amrc will handle, to be combined with PM. | 1. SR088813 | 1. Pending
Q231 | NY | SOL-10870 | 11856.375 | 20736.96 | -8880.585 | -42.82% | 16899 | -5042.625 | -29.84% | 1. Site production was low on 01/17, 01/18 and from 01/25 due to snow. 2. Inverter 1 has shading issue.
Q405 | NY | SOL-10409 | 13574 | 20233.85 | -6659.85 | -32.91% | 20674.02 | -7100.02 | -34.34% | 1. 4 Inverter modules are offline Module 1.0.64 Module 4.0.39 3.0.20 1.0.64 | 1. SR093324, SR110370 | 1. Pending | SR110370
Q435 | NY | SOL-10923 | 17258.625 | 15813.72 | 1444.905 | 9.137% | 25692 | -8433.375 | -32.82% | 1. Weather station has morning shading due to that expected values are low.
Q485 | NY | SOL-10869 | 14504.25 | 17360.88 | -2856.63 | -16.45% | 23708.84 | -9204.59 | -38.82% | 1. Site production was low on 01/17, 01/18 and from 01/25 due to snow.
Q490 | NY | SOL-10411 | 10624.25 | N/A |  |  | 16762.39 | -6138.14 | -36.62% | 1. Optimizers Module 1.2.4 , Module 2.2.18 , Module 2.3.11 , Module 3.1.16 , Module 6.1.5 , Module 7.1.4 , Module 7.3.17 , Module 9.1.16 ,Module 10.3.3 , 8.0.27 are offline. Pending troubleshooting. | 1. SR093326, SR110229 | 1. Pending | SR110229
Q620 | NY | SOL-10867 | 16495 | 22544.46 | -6049.46 | -26.83% | 27145.16 | -10650.16 | -39.23% | 1.Inverter modules 3.0.144 and 5.0.100 are offline 4.0.66 - 30513B3F-FB - half production because split between 4 modules | 1. SR093327 | 1. Pending
QMOA | NY | SOL-10415 | 1603.1 | 0 | 1603.1 |  | 2917.413 | -1314.313 | -45.05% | 1. Site production was low on 01/17, 01/18 and from 01/25 due to snow.
X024 | NY | SOL-10419 | 4890.8438 | 8802.685 | -3911.8412 | -44.44% | 8671 | -3780.1562 | -43.6% | 1. Inverter 2 started late for the production on 01/01/26 and having heavy shading isuue in mid day hours 2. Inverter 2 unit 2 (7e9ee253) is offline from 01/07 and reporting a DC isolation fault and back online on 01/13. | 1. SR112764 2. SR114236 | 1. Closed 2. Closed | SR114236
X026 | NY | SOL-10420 | 4731.6 | 10554.32 | -5822.72 | -55.17% | 11071.89 | -6340.29 | -57.26% | 1. Optimizer 1.0.124 is offline. Will investigate combinely with other modules. | 1. SR109950 | 1. Pending
X090 | NY | SOL-10925 | 4833.5625 | 4545.364 | 288.1985 | 6.34% | 7353 | -2519.4375 | -34.26% | 1. Actual vs Forcasted delta is showing 34% due to Forcasted energy recording high possibly due to data glitch (similar event observe last 2 years).
X117 | NY | SOL-10422 | 3511.7 | 8875.315 | -5363.615 | -60.43% | 6501.377 | -2989.677 | -45.99% | 1. Inverter 1 having morning shading issue.
X125 | NY | SOL-10423 | 7310.875 | 11094.59 | -3783.715 | -34.1% | 11925.9 | -4615.025 | -38.7% | 1. Inverter 1 unit 1.2 having evening shading issue
X134 | NY | SOL-10424 | 3410.9614 | 11836.37 | -8425.4086 | -71.18% | 10182 | -6771.0386 | -66.5% | 1. 6 modules are offline: Module 1.2.1 Module 1.2.13 Module 1.2.14 Module 1.11.5 Module 2.1.12 Module 2.1.16 2. One of the inverters has been offline since 11/26/25 and remained offline for the rest of the month. | 1. SR098241 2. SR111775 | 1. Pending 2. Pending | SR111775
X135 | NY | SOL-10425 | 5787.375 | 10788.78 | -5001.405 | -46.36% | 9790 | -4002.625 | -40.88% | 1.Inverter 1 unit 1.3 having morning shading issue and inverter 2 having evening shading issues
X139 JHS 222 | NY | SOL-10426 | 8569.5007 | 11357.54 | -2788.0393 | -24.55% | 12346 | -3776.4993 | -30.59% | 1. Site production was low on 01/17, 01/18 and from 01/25 due to snow.
X140 | NY | SOL-10926 | 5337.1562 | 8083.305 | -2746.1488 | -33.97% | 8234 | -2896.8438 | -35.18% | 1. Site production was low on 01/17, 01/18 and from 01/25 due to snow.
X166 | NY | SOL-10427 | 5113.3 | 8835.434 | -3722.134 | -42.13% | 7246 | -2132.7 | -29.43% | 1. Inverter 2 has afternoon shading.
Murphy | MN | SOL-10094 | 513600 | 606225.7 | -92625.7 | -15.28% | 512282.9 | 1317.1 | 0.2571% | 1. Inverter 1 has tripped offline at 12:00 on 01/14 and later back online at 12:00 on 01/20. 2. Inverter E was derating at approximately 860 kW on 01/14. After a remote reset, the inverter has been producing as expected since 01/26. | 1. SR114086 2. SR114571 | 1. pending 2. Closed | SR114571
Terning | MN | SOL-10093 | 496936.065 | 602550.7 | -105614.635 | -17.53% | 464176.1 | 32759.965 | 7.058% | 1. Inverter 2 was derating at approximately 850 kW during peak irradiance on 01/15. After a technician adjusted the thermostart settings, the inverter is now producing as expected since 01/22. 2. Inverter 2 was derating at approximately 400 kW during high irradiance on 01/26. After a remote reset, the inverter has been producing as expected since 01/26. | 1. SR114637 2. SR115340 | 1. Closed 2. Completed | SR115340
Boas Road 04 | NY | SOL-10908 | 72330 | 31962 | 40368 | 126.3% | 152897 | -80567 | -52.69% | 1. Site production was low on 01/07, 01/15 & 01/26 to 01/28 due to snow 2. Weather station stopped communicating Since 01/15 | 2. SR115465 | 2. New
Kelly Bridge Farm | NY | SOL-10911 | 77050 | N/A |  |  | 143468.69 | -66418.69 | -46.29% | 1. Site Production was low on 01/17 to 01/19 & 01/25 due to snow Site production was low most of the days due to snow due to that forcasted (theoretical) values appear higher 2. Inverter 25 didn't started production on 01/22 3. Inverter 32 is underproducing by 5kW since 01/26 due to snow
Pool Brook Road | NY | SOL-10909 | 59326 | 59325 | 1 | 0.001686% | 140415.7 | -81089.7 | -57.75% | 1. Site production was low on 01/17, 01/18 & 01/25 to 01/28 due to snow Site production was low most of the days due to snow due to that forcasted (theoretical) values appear higher
Sackett Lake | NY | SOL-10910 | 132767 | N/A |  |  | 165948.84 | -33181.84 | -20% | 1. Inverter 1 offline from 01/01 and back online at 14:40 on 01/03. 2. Inverter 1 again offline on 01/20 and back online on 01/21 3. Site production was low on 01/17 to 01/19 & 01/25 due to snow | 1. SR114057 2. SR114807 | 1. Closed 2. Closed | SR114807
Burritt Road | NY | SOL-10913 | 58980 | N/A |  |  | 110519.08 | -51539.08 | -46.63% | 1. Site production was low on 01/04, 01/05 & 01/25 due to snow 2. Site tripped offline at 16:10 on 01/09 and back online at 13:10 on 01/10
Villa Roma 1 | NY | SOL-10914 | 93005 | N/A |  |  | 117697.64 | -24692.64 | -20.98% | 1. Site production was low on 01/17 to 01/19 & 01/25 due to snow.
Villa Roma 2 | NY | SOL-10915 | 77763 | N/A |  |  | 114722.46 | -36959.46 | -32.22% | 1. Site production was low on 01/17 to 01/19 & 01/25 due to snow
Washington 1 | NY | SOL-10912 | 82840 | N/A |  |  | 106348.65 | -23508.65 | -22.11% | 1. Inverter 2 tripped offline at 09:50 on 01/17 and back online on 01/18. | 1. SR114704 | 1. Closed
Washington 3 | NY | SOL-10828 | 0 | N/A |  |  | 129625.05 | -129625.05 | -100% | 1. Site was from 10:30 on 12/24 and remained offline throughout the month due to oil leak in transformer. | 1.SR105816 ,SR113584 & SR114827 | 1. Closed, Pending, Pending | SR113584 | SR114827
Washington 4 | NY | SOL-10829 | 129117 | N/A |  |  | 130089.75 | -972.75 | -0.7478%
Big Tree | NY | SOL-10966 | 34020 | 34070 | -50 | -0.1468% | 116825.9001 | -82805.9001 | -70.88% | 1. Site production was low on 01/03, 01/04 & 01/25 de to snow.
Canoga | NY | SOL-10965 | 271610 | 0 | 271610 |  | 381970.76 | -110360.76 | -28.89% | 1. Inverter 3 tripped offline from 11:40 to 13:00 on 01/02, again at 11:35 AM on 01/04 before coming back online on 01/05, and once more from 09:25 AM to 11:25 AM on 01/06. 2. Weather station is not communicating through out the month. | 2. SR111378 | 2. Closed
County Route 84 | NY | SOL-10967 | 372470 | 370150 | 2320 | 0.6268% | 472285.7 | -99815.7 | -21.13% | 1. Inverters 3 & 4 tripped offline from 10:10 on 12/31 and back online at 14:20 on 01/07 | 1. SR113456 | 1. Pending
Donati | NY | SOL-10968 | 89520 | 87440 | 2080 | 2.379% | 156570.4 | -67050.4 | -42.82% | 1. Trackers: Group A tracker 1, 5, 6, 7, & 10 Group F tracker 22, 27, & 33 Group G tracker 13 & 14 are stuck | 1. SR113372 | 1. Pending
Henrietta | NY | SOL-10972 | 136180 | 133860 | 2320 | 1.733% | 268925.4 | -132745.4 | -49.36% | 1. Inverter 1 offline on 01/02 and Inverter 1 & 2 back online at 14:30 on 01/03. 2. Gateway 5 missing 3 trackers 6, 14 and 15 were strucked since 08/20.Gc to hold untill 2026 3. 8 trackers are stuck, previously requested to hold until 2026: T01.A.30; B.24; D.17; E.06, 13, 14, & 18; F.13 | 1. SR114045 2. SR106622 3. SR114038 | 1. Closed 2. Closed 3. Pending | SR106622 | SR114038
NY 70 | NY | SOL-10970 | 176660 | 174120 | 2540 | 1.459% | 386450 | -209790 | -54.29% | 1. Site tripped offline at 18:00 on 01/09 and back online at 15:25 on 01/13. 2. 5 trackers stuck since 01/16: T01.A.18, T01.D.35, T02.C.10, T02.C.11, T02.E.02. 3. Inverter 2 started late on 01/27 & 01/28 | 1. SR114370 2. SR114654 | 1. Closed 2. Pending | SR114654
Reid | NY | SOL-10991 | 137656.9248 | 284559.7 | -146902.7752 | -51.62% | 265223 | -127566.0752 | -48.1% | 1. Inverter 18 derating at 50KW on 01/20, 01/21 & 01/24. 2. Weather station lost communication at 17:15 01/24 and regained communication at 12:30 on 01/27.
Sangolqui | NY | SOL-10975 | 93160 | 66700 | 26460 | 39.67% | 151974.9 | -58814.9 | -38.7% | 1. POA Pyranometer up is reporting zero from 12/30/25 and back to normal on 01/07 and again reporting zero from 01/08 2. 10 trackers are stuck: T01.C.44, 45, 46, 48, & 50 T01.D.48 & 49 T01.E.37 & 43 Remaining trackers offline: C.44 - R280 C.45 - R240 C.46 - R263 C.48 - R257 C.50 - R241 D.49 - R243 | 1. SR114201, SR114202 2. SR114181 | 1. Closed 2. Pending | SR114202 | SR114181
State Highway 17B | NY | SOL-10988 | 0 | 0 | 0 |  | 384984 | -384984 | -100% | 1.Site stopped communicating to GPM DAS From 02:00 on 12/17 and remained rest of the month but site is online and producing in Ingecon portal | 1. SR112948, SR114957 | 1. Denied, Work In Progress | SR114957
State Route 14A | NY | SOL-10997 | 0 | 0 | 0 |  | 427147.4 | -427147.4 | -100% | 1. The site was offline since 04/03. On 05/14, USNE replaced the SEL relay and CAT5 cable, bringing the site back online at 12:55. It went offline again on 05/22. On 05/23, the site was re-energized but was subsequently shut down after Transformer 2 showed signs of internal arcing. Further medium-voltage (MV) troubleshooting is required. On 07/02 technician was after pulling event files from the SEL for analysis. The site remains offline. | 1. SR101820 | 1. Pending
West Creek | NY | SOL-10995 | 265730 | 230210 | 35520 | 15.43% | 397925.5 | -132195.5 | -33.22% | 1. Site was taken offline at 14:10 to 15:05 on 01/08 due to technician was onsite for PM work at the site. | 1. PM 11837 & PM11906
Wildflower | NY | SOL-10982 | 246984 | 188692 | 58292 | 30.89% | 433603.2 | -186619.2 | -43.04% | 1. POA Pyranometer UP stopped communicating from 11/16 and reporting normally from 01/08 and POA Pyranometer DOWN stopped communicating since past years 2. Meter 1 is not capuring inverters data since 11/16 and resumed capturing data on 01/08. 3. Inverter 1,2 &3 experienced multiple trippings on 01/01 to 01/4. 4. Inverter is offline since 01/05 and back online at 12:10 on 01/08 5. Inverter 3 tripped offline from 11:50 to 12:55 on 01/28 6. Site production low on 01/25 due to snow | 1. SR112202 2. SR113983 3. SR114059 4. SR114167 5. SR115416 | 1. Pending 2. Pending 3. Closed 4. Closed | SR113983 | SR114059 | SR114167 | SR115416
Glen Mary 1 | NY | SOL-10993 | 164340 | 146450 | 17890 | 12.22% | 420494.8 | -256154.8 | -60.92% | 1. Site production low from 01/25 due to snow | 1. SR114994 | 1. Work in progress
Glen Mary 2 | NY | SOL-10994 | 138160 | 0 | 138160 |  | 171573.9 | -33413.9 | -19.47% | 1. POA Pyranometer UP irradiance reporting 0W/m2 since 08/18. Due to this expected energy values in monthly reports has been affected. 2. Site production low on 01/14 due to snow | 1.SR105649 | 1. Deined
Telegraph 1 | NY | SOL-11003 | 153680 | N/A |  |  | 286022.2 | -132342.2 | -46.27% | 1. Inverter 2 tripped offline at 08:05AM on 01/08 and back online on 01/09. 2. Site tripped offline from 12:10 to 13:00 on 01/10
Telegraph 2 | NY | SOL-11004 | 97060 | N/A |  |  | 146627.1 | -49567.1 | -33.8% | 1. Inverter 1, Module 1.2 tripped offline at 12:55 on 01/10 and back online on 01/11. | 1. SR114382 | 1. Closed
Cafferty Hill | NY | SOL-10996 | 82990 | 85880 | -2890 | -3.365% | 373143.4 | -290153.4 | -77.76% | 1. Site tripped offline at 10:15AM on 01/05 and back online at 13:50 on 01/23 | 1. SR114092, SR115258 | 1. Closed | SR115258
Dunkleman | NY | SOL-11008 | 191990 | 157970 | 34020 | 21.54% | 369715.73 | -177725.73 | -48.07% | 1. site was offline at 13:00 on 12/29 and back online at 15:05 on 01/07. 2. 15 trackers are stuck from 11/11 Tracker 01 devices 11, 38, 44, 75, 92, 106, 119 Tracker 02 devices 21, 27, 36, 43, 52, 66, 88, 124 | 1. SR113860, SR113861 2. SR111019 | 1. Closed 2. Pending | SR113861 | SR111019
Route 19 1 | NY | SOL-11001 | 96365 | 81568.2 | 14796.8 | 18.14% | 154567.8 | -58202.8 | -37.66% | 1. The site was offline at 14:00 on 01/08 and came back online at 02:05 on 01/09. It went offline again at 12:05 on 01/09 and was back at 13:00 on 01/10.
Route 19 2 | NY | SOL-11002 | 249670 | 246010 | 3660 | 1.488% | 409574.6 | -159904.6 | -39.04% | 1. Inverter 1 went offline at 07:50 on 01/07, reporting ‘STOP,’ and came back online at 13:40 on 01/08. | 1. SR114240 | 1. Closed
Yellow Mills 1 | NY | SOL-11006 | 107464 | 105508 | 1956 | 1.854% | 123508.6 | -16044.6 | -12.99% | 1. Modules startting late for the production most of the days during the month.
Yellow Mills 2 | NY | SOL-11005 | 196674 | 0 | 196674 |  | 126216.1 | 70457.9 | 55.82% | 1. Modules startting late for the production most of the days during the month 2. Meter is intermittently lossing communication since 09/04, production can be verified at inverter level. 3. Weather station stopped communicating at 13:55 on 04/03/25. | 2. SR107450, SR107667 | 2. Closed | SR107667
Yellow Mills 3 | NY | SOL-11007 | 95437 | 93389 | 2048 | 2.193% | 111400.8 | -15963.8 | -14.33% | 1. Modules startting late for the production most of the days during the month.
Catskill | NY | SOL-11021 | 207977 | 0 | 207977 |  | 295119.31 | -87142.31 | -29.53% | 1. Site tripped offline at 00:30 on 12/30, After the technician closed the relay, the site came back online at 10:25 on 01/01. 2. Weather station is not communicating for whole month. | 1. SR113809 2. SR106739 | 3. Closed 4. Denied | SR106739
Eddy Ridge | NY | SOL-11054 | 89230 | 87456 | 1774 | 2.028% | 176115 | -86885 | -49.33% | 1. Site tripped offline at 09:00 on 01/22 and back online at 13:00 on 01/22. | 1. SR114896 | 1. Closed
Ridgeway #1 | NY | SOL-11018 | 244376 | 148377 | 95999 | 64.7% | 426059 | -181683 | -42.64% | 1. Meter 2 stopped communication at at 18:45 on 01/08. | 1. SR115453 | 1. New
Rivard 1 | NY | SOL-11011 | 148338.3301 | 270906.9 | -122568.5699 | -45.24% | 257064.8 | -108726.4699 | -42.3% | 1.Site production was low most of the days due to snow due to that forcasted (theoretical) values appear higher
Rivard 2 | NY | SOL-11012 | 142942 | 205053 | -62111 | -30.29% | 245245.8 | -102303.8 | -41.71% | 1.Site production was low most of the days due to snow due to that forcasted (theoretical) values appear higher.
Ridgeway #2 | NY | SOL-11027 | 124718 | 121762 | 2956 | 2.428% | 219945.25 | -95227.25 | -43.3% | 1. Tracker 30 is strucked since 01/20. | 1. SR114769 | 1. Pending
Spencer | NY | SOL-11017 | 366895.2 | 362740 | 4155.2 | 1.146% | 306010.64 | 60884.56 | 19.9% | 1. 4 trackers are stuck: #116 ,147, 169, & 170 have been stuck since 01/06; 2 trackers back online on 01/08, while the remaining two require further troubleshooting. | 1. SR114186 | 1. Pending
Reisender | NY | SOL-10886 | 55170 | 54780 | 390 | 0.7119% | 139255.92 | -84085.92 | -60.38% | 1. Site was taken offline at 08:55 to 10:55 on 01/06 due to inspection at the site. | 1. SR113106 | 1. Closed
Finney | NY | SOL-10999 | 423780 | 421430 | 2350 | 0.5576% | 423916.47 | -136.47 | -0.03219% | 1. Site production was low on 01/04,01/08,01/09,01/12 & 01/27 due to snow.
Davis Solar | NY | SOL-10958 | 98174 | 222749.1 | -124575.1 | -55.93% | 182746 | -84572 | -46.28% | 1. Inverter 1 was offline at 16:20 on 12/31, After a remote reset, the inverter came back online at 07:15 on 01/02. 2. Inverter 1 went offline at 07:00 on 01/08 and came back online at 09:15 01/08 after a remote reset, then went offline again at 07:00 on 01/10 and was back online at 09:15 on 01/10 after remote reset. 3. Inverter 1 was offline at 07:00 on 01/13 due to "battery fault", After a remote reset, the inverter came back online at 09:15 on 01/13. | 1. SR113924 2. SR114283 3. SR114502 | 1. Closed 2. Closed 3. Closed | SR114283 | SR114502
Genesee | NY | SOL-10951 | 71876 | 71030.2 | 845.8 | 1.191% | 223003.43 | -151127.43 | -67.77% | 1. Site tripped offline at 10:30 on 12/18, After the technician closed the relay, the site came back online at 11:05 on 01/17. 2. NCU 1 trackers 21 & 53 are strucked since 12/03. | 1. SR113201 2. SR112035, SR113433 | 1. Closed 2. Pending | SR112035 | SR113433
Landau I | NY | SOL-10891 | 76220 | N/A |  |  | 183280 | -107060 | -58.41% | 1. CB 1.11 strings 14, 15, 5, and 6 were isolated due to ground faults; later, the technician installed jumpers and all strings were back online on 01/09. | 1.SR112199, SR105387 | 1. Closed | SR105387
Landau II | NY | SOL-10895 |  | N/A |  |  | 345100.3 |  |  | 1. Site production was low on 01/17,01/18,01/25 & 01/26 due to snow.
New Beginnings | NY | SOL-10890 | 92270 | 92270 | 0 | 0% | 179886.74 | -87616.74 | -48.71% | 1. Site production was low on 01/17,01/18,01/25 & 01/26 due to snow.
Bullitt Farm Solar, LLC | NY | SOL-10998 | 58980 |  |  |  | 110519.08 | -51539.08 | -46.63% | 1. Site production was low on 01/03 to 01/05, 01/07,01/12,01/14,01/15 & 01/22 due to snow
Brodhead Solar, LLC | NY | SOL-10899 | 177618 | 190253 | -12635 | -6.641% | 215650.8 | -38032.8 | -17.64% | 1. All trackers are currently stucked since 01/27, appears to be snow-related. | 1. SR114834 | 1. Pending
Svenski | NY | SOL-10894 | 30220 | N/A |  |  | 143761.47 | -113541.47 | -78.98% | 1. The site stopped communicating through the DAS at 16:25 on 01/10 and issue remained for the rest of the month. | 1. SR114380 | 1. Pending
Bantam | NY | SOL-10986 | 159790 | 190990 | -31200 | -16.34% | 384649.1825 | -224859.1825 | -58.46% | 1. Site tripped offline at 07:30 on 12/29 and back online at 12:30 on 01/01. 2. The meter is missing phase A throughout the month, resulting in incomplete production data for both inverters. GC will review in 2026 3. NCU 1 is missing communications and tracker angles cannot be confirmed, NCU 4 SPC 1015 is stuck. Pending replacement slew drive needed. | 1. SR113716 2. SR108248 3. SR108120 | 1. Closed 2. Closed 3. Pending | SR108248 | SR108120
Bogart | NY | SOL-10887 | 99550 | 70660 | 28890 | 40.89% | 164078.57 | -64528.57 | -39.33% | 1. The weather station dropped to 0 W/m² at 12:30 on 01/21. | 1. SR115466 | 1. New
Dubois | NY | SOL-10892 | 90300 | 90343 | -43 | -0.0476% |  |  |  | 1. Site production was low on 01/17,01/18 & 01/25 due to snow.
Salt Point | NY | SOL-10888 | 124160 | 124160 | 0 | 0% | 135218.23 | -11058.23 | -8.178% | 1. NCU 02 trackers SPC 151 and SPC 349 were stuck from 01/06 to 01/12 until a bent pin was fixed, after which all trackers came back online; later SPC 123 was stuck from 01/15 to 01/22, and SPC 151 has been stuck again since 01/22. | 1. SR114176, SR114605 | 1. Pending | SR114605
Wheatland 2A | NY | SOL-10971 | 160740 | 159600 | 1140 | 0.7143% | 282852.6 | -122112.6 | -43.17% | 1.25 trackers are currently stuck: NCU 1 SPC 101, 106, 111, 112, 116, 118, 201, 204, 301, 302, 305, 307, 309, 310 NCU 2 SPC 125, 126, 136, 141, 223, 234, 242, 324, 327, 338, 341 | 1. SR110135, SR113865 | 1. Pending | SR113865
Wheatland 2B | NY | SOL-10961 | 164520 | 0 | 164520 |  | 279044.7 | -114524.7 | -41.04% | 1. 15 trackers are stuck: NCU 1 SPC 101, 206, 218, & 314 NCU 2 SPC 118, 128, 230, 234, 321, 323, 333, 334, 336, 337, & 343 2. POA pyranometer stopped communicating from 14:05 on 11/07. Additionally, POA pyranometer is not communicating since past years | 1. SR098860, SR099264, SR113864 2. SR112216 | 1. Pending 2. Pending | SR099264 | SR113864 | SR112216
Brickchurch | NY | SOL-10889 | 51400 | 52570 | -1170 | -2.226% | 77601.11 | -26201.11 | -33.76% | 1. The site went offline at 12:55 on 12/29, After the technician closed the relay, the site came back online at 10:45 on 01/02. 2. Site west offline at 18:45 on 01/09, After the technician closed the relay, the site came back online at 16:10 on 01/12. 7 trackers 119,216,220,329, 338, 143, and 240 have seized slew drives | 1. SR113815 2. SR114375 3. SR109998 | 1. Closed 2. Closed 3. Pending | SR114375 | SR109998
McCarthy Solar | NY | SOL-10992 | 132470 | 0 | 132470 |  | 199506.06 | -67036.06 | -33.6% | 1. Weather station is not communicating through out the month. | 1. SR109079, SR110746 | 1. Deined | SR110746
Costanza | NY | SOL-10907 | 80480 | 80582.43 | -102.43 | -0.1271% | 161660.63 | -81180.63 | -50.22% | 1. Site tripped offline at 06:50 on 12/30, After the technician closed the relay, the site came back online at 10:49 on 01/02. 2. Site tripped offline at 07:40 on 01/14, After the technician closed the relay, the site came back online at 15:35 on 01/15. | 1. SR113817 2. SR114585 | 1. Closed 2. Closed | SR114585
Lockenhurst Pond | NY | SOL-11000 | 175704 | 203514.2 | -27810.2 | -13.66% | 160367 | 15337 | 9.564% | 1.Site production was low on 01/10,01/14,01/17,01/18 & 01/25 due to snow
Drinkwater | NY | SOL-10896 | 92100 | 0 | 92100 |  | 167148.09 | -75048.09 | -44.9% | 1. Inverters and weather station stopped communicating at 03:00 on 12/29. | 1. SR113818, SR115462 | 1. New | SR115462
Altamont | NY | SOL-11085 | 214086 | 414723.4 | -200637.4 | -48.38% | 346402.7 | -132316.7 | -38.2%
Krumkill North | NY | SOL-11086 | 178706 | 333810.6 | -155104.6 | -46.46% | 463900.5 | -285194.5 | -61.48% | 1.Site production was low on 01/16,01/17,01/25 -01/28 due to snow
Krumkill South | NY | SOL-11087 | 174363 | 315721.3 | -141358.3 | -44.77% | 363684 | -189321 | -52.06% | 1.Inverter S1 was back online at 09:00 on 01/02 1.Site production was low on 01/01, 01/17,01/25 -01/28 due to snow
X092 | NY | SOL-11189 | 4003.3 | 6290.382 | -2287.082 | -36.36% | 8237 | -4233.7 | -51.4% | 1.Site production was low on 01/01,01/16,01/17,01/25 -01/28 due to snow 2.Inverters 1,2 are having morning shading issue
X093 | NY | SOL-10932 | 2882.4082 | 4009.505 | -1127.0968 | -28.11% | 4845 | -1962.5918 | -40.51% | 1.Site production was low on 01/01,01/16,01/17,01/25 -01/28 due to snow
X095 | NY | SOL-10929 | 3943.5781 | 7896.833 | -3953.2549 | -50.06% | 6901 | -2957.4219 | -42.85% | 1.Site production was low on 01/17-01/21,01/25 -01/28 due to snow
X181 | NY | SOL-10428 | 7292.9062 | 14591.35 | -7298.4438 | -50.02% | 11497 | -4204.0938 | -36.57% | 1.Site production was low on 01/17-01/21,01/25 -01/28 due to snow
X415 | NY | SOL-10429 | 4703.9531 | 7354.188 | -2650.2349 | -36.04% | 6299 | -1595.0469 | -25.32% | 1.Site production was low on 01/17-01/21,01/25 -01/28 due to snow
K198 | NY | SOL-10930 | 3744.7969 | 5314.616 | -1569.8191 | -29.54% | 5807 | -2062.2031 | -35.51% | 1.Site production was low on 01/17-01/21,01/25 -01/28 due to snow
K203 | NY | SOL-11190 | 5244.2 | 7024.09 | -1779.89 | -25.34% | 9142 | -3897.8 | -42.64% | 1.Site production was low on 01/10,01/17 - 01/21,01/25 - 01/27 due to snow
K213 | NY | SOL-11191 | 5406.9 | 7582.657 | -2175.757 | -28.69% | 9570 | -4163.1 | -43.5% | 1.Site production was low on 01/10,01/17 - 01/21,01/25 - 01/28 due to snow 2. Inverters 3 and 4 had heavy shading in morning.
K217 | NY | SOL-10933 | 2473.8203 | 4075.625 | -1601.8047 | -39.3% | 3879 | -1405.1797 | -36.23% | 1.Site production was low on 01/01,01/17,01/25 -01/28 due to snow
K307 | NY | SOL-10876 | 5876.7969 | 13060.53 | -7183.7331 | -55% | 7468 | -1591.2031 | -21.31% | 1.Site production was low on 01/17-01/21,01/25 -01/28 due to snow 2. Inverter 2 experiencing minor shading issue
K610 | NY | SOL-11158 | 7256.1 | 9685.564 | -2429.464 | -25.08% | 12467 | -5210.9 | -41.8% | 1.Site production was low on 01/17-01/21,01/25 -01/28 due to snow
M025 | NY | SOL-10392 | 4989.125 | 14236.48 | -9247.355 | -64.96% | 9891 | -4901.875 | -49.56% | 1. Inverter 3 unit 3.1 was offline on 12/08 | 1.SR114464 | 1.pending
M028 | NY | SOL-10381 | 4642.0469 | 6572.825 | -1930.7781 | -29.38% | 6540 | -1897.9531 | -29.02% | 1.Site production was low on 01/17-01/21,01/25 -01/28 due to snow
Q030 | NY | SOL-10878 | 1390.2344 | 3019.264 | -1629.0296 | -53.95% | 8785 | -7394.7656 | -84.17% | 1.Site was offline at 07:30 on 12/19 and later back online at 08:15 on 01/17 | 1.SR113237 | 1.Completed
Q130 | NY | SOL-10877 | 2955.9609 | 6868.722 | -3912.7611 | -56.96% | 4243.431 | -1287.4701 | -30.34% | 1. Inverter 1 unit 1.2 has heavy shading in the afternoon. 2.Site production was low on 01/01,01/17,01/25 -01/28 due to snow
Q196 | NY | SOL-10879 | 3733.7969 | 7942.186 | -4208.3891 | -52.99% | 5931 | -2197.2031 | -37.05% | 1. Inverter 3 has heavy shading in morning and evening. 2.Site production was low on 01/17-01/21,01/25 -01/28 due to snow
Q220 | NY | SOL-10873 | 4377.875 | 10716.8 | -6338.925 | -59.15% | 5740 | -1362.125 | -23.73% | 1. Inverter 1 unit 1.2 was offline on 09/29 at 14:30 and back online at 01/05 | 1.SR112357 | 1.Closed
Q205 | NY | SOL-10922 | 5970.6406 | 13482.7 | -7512.0594 | -55.72% | 8522 | -2551.3594 | -29.94% | 1.Site production was low on 01/17-01/21,01/25 -01/28 due to snow
Q400 | NY | SOL-10871 | 8726.2525 | N/A |  |  | 12985 | -4258.7475 | -32.8%
R003 | NY | SOL-10416 | 8987.25 | 11551.87 | -2564.62 | -22.2% | 13336 | -4348.75 | -32.61% | 1.Site production was low on 01/17-01/21,01/25 -01/28 due to snow
R007 | NY | SOL-10417 | 9489.9688 | 13976.96 | -4486.9912 | -32.1% | 22783.34 | -13293.3713 | -58.35% | 1.Site production was low on 01/17-01/21,01/25 -01/28 due to snow
BK16 | NY | SOL-11093 | 9596 | 12915.56 | -3319.56 | -25.7% | 13947 | -4351 | -31.2% | 1.Site production was low on 01/17-01/21,01/25 -01/28 due to snow
Trenton - Trenton East | IL | SOL-11060 | 268098 | 277362.4 | -9264.4 | -3.34% | 211713 | 56385 | 26.63% | 1.Site tripped offline at 04:00 on 12/31 and is back online at 14:15 on 01/02 2.Site was offline from 07:30 to 17:30 on 01/07 | 1.SR113901 2.SR114216 | 1.Closed 2.Closed | SR114216
Trenton - Trenton West | IL | SOL-11061 | 268153 | 240078.6 | 28074.4 | 11.69% | 215152 | 53001 | 24.63% | 1.Site was offline from 07:15 to 17:15 on 01/07 2.Multiple trackers are stuck | 1.SR114216 2.SR109332 | 1.Closed 2.Pending | SR109332
Dakota - Dakota Solar 1 | IL | SOL-11113 | 214508 | N/A |  |  | 220248 | -5740 | -2.606% | 1. Weather station stopped communicating from 06:15AM on 12/28/2025 2. Inverter 11 started late for production on 01/24 & 01/25. | 1. SR113926 2. SR115301 | 1. Pending 2. Closed | SR115301
X018 | NY | SOL-10418 | 4430.75 | 5815.83 | -1385.08 | -23.82% | 7520 | -3089.25 | -41.08% | 1.Inverter 3 having heavy shading issue in morning hours 2. Site production was low on 01/18 & 01/25 to 01/28.
Janiak Solar | NY | SOL-10898 | 105163 | 129742.5 | -24579.5 | -18.94% | 203943 | -98780 | -48.44% | 1. Site tripped offline from 07:30AM to 09:30AM on 01/03. 2. Site tripped offline from 03:30AM to 04:15AM on 01/13 3. Site again tripped offline at 22:30 on 01/15 and remained offline throughout the month. | 1. SR114051 2. SR114488 3. SR114640 | 1. Closed 2. Closed 3. Pending | SR114488 | SR114640
County Route 11B | NY | SOL-10983 | 259418.8 | 254569.6 | 4849.2 | 1.905% | N/A |  |  | 1. One broken Module for inverter 1 need to be replaced. | 1. SR113247 | 1. Pending
Barone | NY | SOL-11034 | 162889 | 160342 | 2547 | 1.588% | 210690.0206 | -47801.0206 | -22.69% | 1. Site tripped offline at 02:00PM on 01/23 and it came back online at 14:20 on 01/24 2. Inverter experienced multiple offline events between 01/02 and 01/21, with recovery after each trip. 3. Site tripped offline at 13:05 on 01/26 and has remained offline throughout the month. 4. Trackers 75 & 108 are stuck on 01/01 and back to normal from 01/16. | 1. SR115287 2. SR113692, SR114790 3. SR115363 4. SR114177 | 1. Closed 2. Pending 3. New 4. Closed | SR113692 | SR114790 | SR115363 | SR114177
Cedarville | IL | SOL-11069 | 156820 | 203303 | -46483 | -22.86% | 185269.1 | -28449.1 | -15.36% | 1.Site production was low on 01/21 to 01/29 due to snow
O'Brien Hill #1 | NY | SOL-11098 | 0 | 0 | 0 |  | N/A |  |  | 1. The site has been offline since 03/07. The site will likely remain de-energized until late this year. | 1. SR098278, SR098670 | 1. Pending | SR098670
O'Brien Hill #2 | NY | SOL-11099 | 230537 | 230436 | 101 | 0.04383% | N/A |  |  | 1. Site is offline from 01/26 and remained offlline throught the month. 2. All trackers were stuck on 01/15, with residual snowfall of about a quarter inch reported nearby. On 01/16, all trackers except T02.D.21 resumed normal operation after earlier communication and angle issues. | 1. SR115348 2. SR112774 | 1. Pending 2. Pending | SR112774
Trinity - Freeport | IL | SOL-11057 | 197770 | 191173.8 | 6596.2 | 3.45% | 182784 | 14986 | 8.199%
Ransom | NY | SOL-11157 | 262100 | 257255 | 4845 | 1.883% | N/A |  |  | 1. Site tripped offline at 10:45AM on 01/16 and back online at 12:25PM on same day. 2. 8 Trackers are stuck on 01/06: #005, 012, 014, 035, 040, 041, & 050 and all trackers are back to normal on 01/08 expect tracker 40 and again all trackers are stuck on 01/21 and back to operating normal on 01/23 | 1. NO SR 2. SR114817 & SR114179 | 1. 2. Pending | SR114179
Horseheads - Wedge | NY | SOL-11160 | 153909 | 151921 | 1988 | 1.309% | N/A
Otisville - Shoddy Hollow | NY | SOL-11185 | 228031 | 224988 | 3043 | 1.353% | N/A |  |  | 1.The meter is missing comms but the inverters are communicating from 11/30 2. Inverter 2 is offline on 12/31 and came back online on 01/01 after self-resolving. Both inverters went offline again on 01/02 and were brought back online at 10:45 the same day after the technician power-cycled them. 3. Site offline on 01/03 was re-energized by the technician, coming back online at 11:40 AM on 01/04 4. Site offline on 01/05 and back online at 11:30AM on 01/06, It tripped offline again at 12:35 PM the same day and self-resolved, came back online at 08:10 AM on 01/07. 5. Inverters experienced multiple offline events between 01/17 and 01/25, caused by a single-phase voltage unbalance exceeding 3% of nominal voltage. | 1.SR111863 2.SR113917 3. SR114056 4. SR114169 5. SR114193 | 1.Closed 2.closed 3.Closed 4. Closed 5. Pending | SR113917 | SR114056 | SR114169 | SR114193
Wellsville - Chenunda Creek | NY | SOL-11187 | 112266 | 111257 | 1009 | 0.9069% | N/A |  |  | 1. Site tripped offline at 15:40 on 01/04. After the EV technician replaced the faulty equipment, it was energized and brought back online at 12:10 on 01/17. 2. 20 trackers are stuck since 01/22: #7-9, 10, 12, 18-19, 21-23, 27-29, 33-34, 39, 41-42, 48-49 - . These trackers showed a low battery auto-stow warning, and several were charging, which may have been related to the recent snowfall. The issue self-resolved on 01/23, but one tracker became stuck again on 01/26 | 1. SR114084 2. SR114889 | 1. Completed 2. Pending | SR114889
DC: Washington - Essex Condominium | DC | SOL-10036 | 1208 | 1601.977 | -393.977 | -24.59% | 2142.399 | -934.399 | -43.61% | 1. Site production was low from 01/25 due to snow. 2. The site is performing as expected, but the expected and forecasted values are high. A similar event was observed over the past two years.
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 7951.027 | 8242.12 | -291.093 | -3.532% | 9757.33 | -1806.303 | -18.51% | 1. Inverter 2 was offline since 07:00 on 10/11. denied by customer 2. The meter has been communicating intermittently throughout the month. | 1. SR109524 & SR114651 2. SR100771 & SR114651 | 1. Closed 2. Pending | SR114651 | SR100771 | SR114651
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 9375 | 7407.475 | 1967.525 | 26.56% | 9752.109 | -377.109 | -3.867%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149 | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was offline for whole month due to major fault onsite. | 1. SR114034, SR110863 & SR114857 | 1. Pending | SR110863 | SR114857
IL: Viola - Goldenrod - (PW) | IL | SOL-11132 | 574985 | 508651.7 | 66333.3 | 13.04% | 518040 | 56945 | 10.99% | 1. All trackers on site were not tracking properly for whole month. 2. Inverters 2.04 & 2.15 were derating at 47kw on 01/23 & 01/26 | 1. SR113569 2. SR112384 | 1. Pending 2. Closed | SR112384
IL: Marengo - Grant - (PW) | IL | SOL-11147 | 224264 | 0 | 224264 |  | 193523.2 | 30740.8 | 15.88% | 1. Weather station was not communicated for whole month. | 1. SR108392 | Pending
NY: Cambridge - Cambridge (PW) | NY | SOL-11126 | 112395.156 | 100094.105 | 12301.051 | 12.29% | 537994 | -425598.844 | -79.11% | 1. Inverter 2 was underproducing by 500kW from 12/01/2025 and back to normal production from 01/06/2026 2. Inverter 2 was offline from 01/12 to 11:00 on 01/13, again tripped offline at 12:00 on 01/16. After the technician replaced the hardware and updated the firmware, it was brought back online on 01/21. 3. POA and BPO have stopped communicating from 12/23 but later communicating intermittently and resolved on 01/29. 4. site was taken offline from 12:00 to 16:00 on 01/20 for troubleshooting on Inverter 2. | 1. SR113003, 2. SR111163, SR114420 3. SR113452 4. SR114420 | Pending Pending Pending Pending | SR111163 | SR114420 | SR113452 | SR114420
NY: Whitesville - Independence North | NY | SOL-11186 | 276854 | N/A |  |  | N/A
IL: Beecher - Cottage Grove North (PW) | IL | SOL-11114 | 213014 | 231407.5 | -18393.5 | -7.949% | 186272 | 26742 | 14.36% | 1. Inverter 2 was offline from 10:00 on 12/22 due to faulty breaker and remained offline to date. | 1. SR113455, SR113185 | Pending | SR113185
IL: Beecher - Cottage Grove South (PW) | IL | SOL-11115 | 225299 | 297560.1 | -72261.1 | -24.28% | 174687 | 50612 | 28.97% | 1. Site production was low on 01/07 to 01/11 due to snow.
IL: Harvard - 9618 US HWY 14 (PW) | IL | SOL-11110 | 182768 | 396799.6 | -214031.6 | -53.94% | 172612 | 10156 | 5.884% | 1. Site production was low on 01/17,01/18 & 01/25 to 01/31 due to snow.
IL: Beecher - 701 E Goodenow Rd (PW) | IL | SOL-11112 | 26786 | 28958.46 | -2172.46 | -7.502% | 178720 | -151934 | -85.01% | 1. Site was offline from 07:00 on 12/29 due to a faulty surge arrester and back online at 17:30 on 01/28 | 1. SR114035, SR113743 | Pending | SR113743
NY: Stormville - Green Haven - (IRA) | NY | SOL-11151 | 160195.6 | N/A |  |  | N/A |  |  | 1. Inverter 23 was offline since 07:00 on 12/05 and back online at 13:17 on 01/02 after chint remote reset. | 1 SR112320 | Closed
IL: Hillsboro - Anacott (PW) | IL | SOL-11134 | 634429 | N/A |  |  | 553720 | 80709 | 14.58% | 1. Site tripped offline at 19:00 on 01/08 and came back online at 20:15 on 01/10 after a brief utility outage. 2. Inverters 1.06 is constantly derating at 76kw on 01/26 due to External fan fault and self resolved on 01/27. | 1. SR114325 2. SR115342 | Closed Closed | SR115342
IL: Manhattan - Gougar (PW) | IL | SOL-11148 | 121126 | 145932.1 | -24806.1 | -17% | 208326.7 | -87200.7 | -41.86% | 1. Site tripped offline at 03:00 AM on 01/07. After the technician closed the Breaker, the site came back online at 10:00 on 01/09. 2. Site tripped offline at 10:00 AM on 01/21 due to a blown fuse in the transformer. It requires further troubleshooting and has remained offline throughout the month. | 1. SR114209, SR112908 2. SR114820, SR114849 | Closed Pending | SR112908 | SR114820 | SR114849
IL: Morrison - Sawyer (PW) | IL | SOL-11176 | 482576 | 453421.502 | 29154.498 | 6.43% | 528786.47 | -46210.47 | -8.739%
IL: Kankakee - Jeffery (PW) | IL | SOL-11173 | 518695 | 651180.899 | -132485.899 | -20.35% | 556108.27 | -37413.27 | -6.728% | 1.Site tripped offline at 02:45 on 01/07 and back online at 11:15 on 01/08 2.Site was offline from 05:15 to 11:00 on 01/08 3.Inverters 1 and 2 have tripped offline at 08:30 to 15:00 on 01/16 4.Site tripped offline at 07:30 on 01/20 and back online at 10:45 on 01/21 | 3.SR114686 4.SR114541 | 1.Closed 2.Closed | SR114541
IL: Freeport - 2240 South 18th Ave (PW) | IL | SOL-11084 | 197,342 | N/A |  |  | N/A

## Feb
Generate Capital |  |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
K026 | NY | SOL-10356
K041 | NY | SOL-10357
K043 | NY | SOL-10358
K058 | NY | SOL-10360
K115 | NY | SOL-10361
K152 | NY | SOL-10362
K166 | NY | SOL-10363
K206 | NY | SOL-10927
K251 | NY | SOL-10365
K269 | NY | SOL-10366
K273 | NY | SOL-10367
K287 | NY | SOL-10919
K298 | NY | SOL-10368
K335 | NY | SOL-10370
K345 | NY | SOL-10920
K445 | NY | SOL-10373
K495 | NY | SOL-10374
M020 | NY | SOL-10380
M092 | NY | SOL-10383
M143 | NY | SOL-10384
M144 | NY | SOL-10385
M167 | NY | SOL-10386
M188 | NY | SOL-10387
EMHC | NY | SOL-10351
Q008 | NY | SOL-10397
Q018 | NY | SOL-10398
Q021 | NY | SOL-10399
Q025 | NY | SOL-10400
Q074 | NY | SOL-10402
Q115 | NY | SOL-10872
Q139 | NY | SOL-10403
Q157 | NY | SOL-10404
Q192 | NY | SOL-10406
Q210 | NY | SOL-10407
Q229 | NY | SOL-10408
Q231 | NY | SOL-10870
Q405 | NY | SOL-10409
Q435 | NY | SOL-10923
Q485 | NY | SOL-10869
Q490 | NY | SOL-10411
Q620 | NY | SOL-10867
QMOA | NY | SOL-10415
X024 | NY | SOL-10419
X026 | NY | SOL-10420
X090 | NY | SOL-10925
X117 | NY | SOL-10422
X125 | NY | SOL-10423
X134 | NY | SOL-10424
X135 | NY | SOL-10425
X139 JHS 222 | NY | SOL-10426
X140 | NY | SOL-10926
X166 | NY | SOL-10427
Murphy | MN | SOL-10094
Terning | MN | SOL-10093
Boas Road 04 | NY | SOL-10908
Kelly Bridge Farm | NY | SOL-10911
Pool Brook Road | NY | SOL-10909
Sackett Lake | NY | SOL-10910
Burritt Road | NY | SOL-10913
Villa Roma 1 | NY | SOL-10914
Villa Roma 2 | NY | SOL-10915
Washington 1 | NY | SOL-10912
Washington 3 | NY | SOL-10828
Washington 4 | NY | SOL-10829
Big Tree | NY | SOL-10966
Canoga | NY | SOL-10965
County Route 84 | NY | SOL-10967
Donati | NY | SOL-10968
Henrietta | NY | SOL-10972
NY 70 | NY | SOL-10970
Reid | NY | SOL-10991
Sangolqui | NY | SOL-10975
State Highway 17B | NY | SOL-10988
State Route 14A | NY | SOL-10997
West Creek | NY | SOL-10995
Wildflower | NY | SOL-10982
Glen Mary 1 | NY | SOL-10993
Glen Mary 2 | NY | SOL-10994
Telegraph 1 | NY | SOL-11003
Telegraph 2 | NY | SOL-11004
Cafferty Hill | NY | SOL-10996
Dunkleman | NY | SOL-11008
Route 19 1 | NY | SOL-11001
Route 19 2 | NY | SOL-11002
Yellow Mills 1 | NY | SOL-11006
Yellow Mills 2 | NY | SOL-11005
Yellow Mills 3 | NY | SOL-11007
Catskill | NY | SOL-11021
Eddy Ridge | NY | SOL-11054
Ridgeway #1 | NY | SOL-11018
Rivard 1 | NY | SOL-11011
Rivard 2 | NY | SOL-11012
Ridgeway #2 | NY | SOL-11027
Spencer | NY | SOL-11017
Reisender | NY | SOL-10886
Finney | NY | SOL-10999
Davis Solar | NY | SOL-10958
Genesee | NY | SOL-10951
Landau I | NY | SOL-10891
Landau II | NY | SOL-10895
New Beginnings | NY | SOL-10890
Bullitt Farm Solar, LLC | NY | SOL-10998
Brodhead Solar, LLC | NY | SOL-10899
Svenski | NY | SOL-10894
Bantam | NY | SOL-10986
Bogart | NY | SOL-10887
Dubois | NY | SOL-10892
Salt Point | NY | SOL-10888
Wheatland 2A | NY | SOL-10971
Wheatland 2B | NY | SOL-10961
Brickchurch | NY | SOL-10889
McCarthy Solar | NY | SOL-10992
Costanza | NY | SOL-10907
Lockenhurst Pond | NY | SOL-11000
Drinkwater | NY | SOL-10896
Altamont | NY | SOL-11085
Krumkill North | NY | SOL-11086
Krumkill South | NY | SOL-11087
X092 | NY | SOL-11189
X093 | NY | SOL-10932
X095 | NY | SOL-10929
X181 | NY | SOL-10428
X415 | NY | SOL-10429
K198 | NY | SOL-10930
K203 | NY | SOL-11190
K213 | NY | SOL-11191
K217 | NY | SOL-10933
K307 | NY | SOL-10876
K610 | NY | SOL-11158
M025 | NY | SOL-10392
M028 | NY | SOL-10381
Q030 | NY | SOL-10878
Q130 | NY | SOL-10877
Q196 | NY | SOL-10879
Q220 | NY | SOL-10873
Q205 | NY | SOL-10922
Q400 | NY | SOL-10871
R003 | NY | SOL-10416
R007 | NY | SOL-10417
BK16 | NY | SOL-11093
Trenton - Trenton East | IL | SOL-11060
Trenton - Trenton West | IL | SOL-11061
Dakota - Dakota Solar 1 | IL | SOL-11113
X018 | NY | SOL-10418
Janiak Solar | NY | SOL-10898
County Route 11B | NY | SOL-10983
Barone | NY | SOL-11034
Cedarville | IL | SOL-11069
O'Brien Hill #1 | NY | SOL-11098
O'Brien Hill #2 | NY | SOL-11099
Trinity - Freeport | IL | SOL-11057
Ransom | NY | SOL-11157
Horseheads - Wedge | NY | SOL-11160
Otisville - Shoddy Hollow | NY | SOL-11185
Wellsville - Chenunda Creek | NY | SOL-11187
DC: Washington - Essex Condominium | DC | SOL-10036
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149
IL: Viola - Goldenrod - (PW) | IL | SOL-11132
IL: Marengo - Grant - (PW) | IL | SOL-11147
NY: Cambridge - Cambridge (PW) | NY | SOL-11126
NY: Whitesville - Independence North | NY | SOL-11186
IL: Beecher - Cottage Grove North (PW) | IL | SOL-11114
IL: Beecher - Cottage Grove South (PW) | IL | SOL-11115
IL: Harvard - 9618 US HWY 14 (PW) | IL | SOL-11110
IL: Beecher - 701 E Goodenow Rd (PW) | IL | SOL-11112
NY: Stormville - Green Haven - (IRA) | NY | SOL-11151
IL: Hillsboro - Anacott (PW) | IL | SOL-11134
IL: Manhattan - Gougar (PW) | IL | SOL-11148
IL: Morrison - Sawyer (PW) | IL
IL: Kankakee - Jeffery (PW) | IL
IL: Freeport - 2240 South 18th Ave (PW) | IL

## Mar
Generate Capital |  |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
K026 | NY | SOL-10356
K041 | NY | SOL-10357
K043 | NY | SOL-10358
K058 | NY | SOL-10360
K115 | NY | SOL-10361
K152 | NY | SOL-10362
K166 | NY | SOL-10363
K206 | NY | SOL-10927
K251 | NY | SOL-10365
K269 | NY | SOL-10366
K273 | NY | SOL-10367
K287 | NY | SOL-10919
K298 | NY | SOL-10368
K335 | NY | SOL-10370
K345 | NY | SOL-10920
K445 | NY | SOL-10373
K495 | NY | SOL-10374
M020 | NY | SOL-10380
M092 | NY | SOL-10383
M143 | NY | SOL-10384
M144 | NY | SOL-10385
M167 | NY | SOL-10386
M188 | NY | SOL-10387
EMHC | NY | SOL-10351
Q008 | NY | SOL-10397
Q018 | NY | SOL-10398
Q021 | NY | SOL-10399
Q025 | NY | SOL-10400
Q074 | NY | SOL-10402
Q115 | NY | SOL-10872
Q139 | NY | SOL-10403
Q157 | NY | SOL-10404
Q192 | NY | SOL-10406
Q210 | NY | SOL-10407
Q229 | NY | SOL-10408
Q231 | NY | SOL-10870
Q405 | NY | SOL-10409
Q435 | NY | SOL-10923
Q485 | NY | SOL-10869
Q490 | NY | SOL-10411
Q620 | NY | SOL-10867
QMOA | NY | SOL-10415
X024 | NY | SOL-10419
X026 | NY | SOL-10420
X090 | NY | SOL-10925
X117 | NY | SOL-10422
X125 | NY | SOL-10423
X134 | NY | SOL-10424
X135 | NY | SOL-10425
X139 JHS 222 | NY | SOL-10426
X140 | NY | SOL-10926
X166 | NY | SOL-10427
Murphy | MN | SOL-10094
Terning | MN | SOL-10093
Boas Road 04 | NY | SOL-10908
Kelly Bridge Farm | NY | SOL-10911
Pool Brook Road | NY | SOL-10909
Sackett Lake | NY | SOL-10910
Burritt Road | NY | SOL-10913
Villa Roma 1 | NY | SOL-10914
Villa Roma 2 | NY | SOL-10915
Washington 1 | NY | SOL-10912
Washington 3 | NY | SOL-10828
Washington 4 | NY | SOL-10829
Big Tree | NY | SOL-10966
Canoga | NY | SOL-10965
County Route 84 | NY | SOL-10967
Donati | NY | SOL-10968
Henrietta | NY | SOL-10972
NY 70 | NY | SOL-10970
Reid | NY | SOL-10991
Sangolqui | NY | SOL-10975
State Highway 17B | NY | SOL-10988
State Route 14A | NY | SOL-10997
West Creek | NY | SOL-10995
Wildflower | NY | SOL-10982
Glen Mary 1 | NY | SOL-10993
Glen Mary 2 | NY | SOL-10994
Telegraph 1 | NY | SOL-11003
Telegraph 2 | NY | SOL-11004
Cafferty Hill | NY | SOL-10996
Dunkleman | NY | SOL-11008
Route 19 1 | NY | SOL-11001
Route 19 2 | NY | SOL-11002
Yellow Mills 1 | NY | SOL-11006
Yellow Mills 2 | NY | SOL-11005
Yellow Mills 3 | NY | SOL-11007
Catskill | NY | SOL-11021
Eddy Ridge | NY | SOL-11054
Ridgeway #1 | NY | SOL-11018
Rivard 1 | NY | SOL-11011
Rivard 2 | NY | SOL-11012
Ridgeway #2 | NY | SOL-11027
Spencer | NY | SOL-11017
Reisender | NY | SOL-10886
Finney | NY | SOL-10999
Davis Solar | NY | SOL-10958
Genesee | NY | SOL-10951
Landau I | NY | SOL-10891
Landau II | NY | SOL-10895
New Beginnings | NY | SOL-10890
Bullitt Farm Solar, LLC | NY | SOL-10998
Brodhead Solar, LLC | NY | SOL-10899
Svenski | NY | SOL-10894
Bantam | NY | SOL-10986
Bogart | NY | SOL-10887
Dubois | NY | SOL-10892
Salt Point | NY | SOL-10888
Wheatland 2A | NY | SOL-10971
Wheatland 2B | NY | SOL-10961
Brickchurch | NY | SOL-10889
McCarthy Solar | NY | SOL-10992
Costanza | NY | SOL-10907
Lockenhurst Pond | NY | SOL-11000
Drinkwater | NY | SOL-10896
Altamont | NY | SOL-11085
Krumkill North | NY | SOL-11086
Krumkill South | NY | SOL-11087
X092 | NY | SOL-11189
X093 | NY | SOL-10932
X095 | NY | SOL-10929
X181 | NY | SOL-10428
X415 | NY | SOL-10429
K198 | NY | SOL-10930
K203 | NY | SOL-11190
K213 | NY | SOL-11191
K217 | NY | SOL-10933
K307 | NY | SOL-10876
K610 | NY | SOL-11158
M025 | NY | SOL-10392
M028 | NY | SOL-10381
Q030 | NY | SOL-10878
Q130 | NY | SOL-10877
Q196 | NY | SOL-10879
Q220 | NY | SOL-10873
Q205 | NY | SOL-10922
Q400 | NY | SOL-10871
R003 | NY | SOL-10416
R007 | NY | SOL-10417
BK16 | NY | SOL-11093
Trenton - Trenton East | IL | SOL-11060
Trenton - Trenton West | IL | SOL-11061
Dakota - Dakota Solar 1 | IL | SOL-11113
X018 | NY | SOL-10418
Janiak Solar | NY | SOL-10898
County Route 11B | NY | SOL-10983
Barone | NY | SOL-11034
Cedarville | IL | SOL-11069
O'Brien Hill #1 | NY | SOL-11098
O'Brien Hill #2 | NY | SOL-11099
Trinity - Freeport | IL | SOL-11057
Ransom | NY | SOL-11157
Horseheads - Wedge | NY | SOL-11160
Otisville - Shoddy Hollow | NY | SOL-11185
Wellsville - Chenunda Creek | NY | SOL-11187
DC: Washington - Essex Condominium | DC | SOL-10036
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149
IL: Viola - Goldenrod - (PW) | IL | SOL-11132
IL: Marengo - Grant - (PW) | IL | SOL-11147
NY: Cambridge - Cambridge (PW) | NY
NY: Whitesville - Independence North | NY
IL: Beecher - Cottage Grove North (PW) | IL
IL: Beecher - Cottage Grove South (PW) | IL
IL: Harvard - 9618 US HWY 14 (PW) | IL
IL: Beecher - 701 E Goodenow Rd (PW) | IL
NY: Stormville - Green Haven - (IRA) | NY
IL: Hillsboro - Anacott (PW) | IL
IL: Manhattan - Gougar (PW) | IL
IL: Morrison - Sawyer (PW) | IL
IL: Kankakee - Jeffery (PW) | IL
IL: Freeport - 2240 South 18th Ave (PW) | IL

## Apr
Generate Capital |  |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
K026 | NY | SOL-10356
K041 | NY | SOL-10357
K043 | NY | SOL-10358
K058 | NY | SOL-10360
K115 | NY | SOL-10361
K152 | NY | SOL-10362
K166 | NY | SOL-10363
K206 | NY | SOL-10927
K251 | NY | SOL-10365
K269 | NY | SOL-10366
K273 | NY | SOL-10367
K287 | NY | SOL-10919
K298 | NY | SOL-10368
K335 | NY | SOL-10370
K345 | NY | SOL-10920
K445 | NY | SOL-10373
K495 | NY | SOL-10374
M020 | NY | SOL-10380
M092 | NY | SOL-10383
M143 | NY | SOL-10384
M144 | NY | SOL-10385
M167 | NY | SOL-10386
M188 | NY | SOL-10387
EMHC | NY | SOL-10351
Q008 | NY | SOL-10397
Q018 | NY | SOL-10398
Q021 | NY | SOL-10399
Q025 | NY | SOL-10400
Q074 | NY | SOL-10402
Q115 | NY | SOL-10872
Q139 | NY | SOL-10403
Q157 | NY | SOL-10404
Q192 | NY | SOL-10406
Q210 | NY | SOL-10407
Q229 | NY | SOL-10408
Q231 | NY | SOL-10870
Q405 | NY | SOL-10409
Q435 | NY | SOL-10923
Q485 | NY | SOL-10869
Q490 | NY | SOL-10411
Q620 | NY | SOL-10867
QMOA | NY | SOL-10415
X024 | NY | SOL-10419
X026 | NY | SOL-10420
X090 | NY | SOL-10925
X117 | NY | SOL-10422
X125 | NY | SOL-10423
X134 | NY | SOL-10424
X135 | NY | SOL-10425
X139 JHS 222 | NY | SOL-10426
X140 | NY | SOL-10926
X166 | NY | SOL-10427
Murphy | MN | SOL-10094
Terning | MN | SOL-10093
Boas Road 04 | NY | SOL-10908
Kelly Bridge Farm | NY | SOL-10911
Pool Brook Road | NY | SOL-10909
Sackett Lake | NY | SOL-10910
Burritt Road | NY | SOL-10913
Villa Roma 1 | NY | SOL-10914
Villa Roma 2 | NY | SOL-10915
Washington 1 | NY | SOL-10912
Washington 3 | NY | SOL-10828
Washington 4 | NY | SOL-10829
Big Tree | NY | SOL-10966
Canoga | NY | SOL-10965
County Route 84 | NY | SOL-10967
Donati | NY | SOL-10968
Henrietta | NY | SOL-10972
NY 70 | NY | SOL-10970
Reid | NY | SOL-10991
Sangolqui | NY | SOL-10975
State Highway 17B | NY | SOL-10988
State Route 14A | NY | SOL-10997
West Creek | NY | SOL-10995
Wildflower | NY | SOL-10982
Glen Mary 1 | NY | SOL-10993
Glen Mary 2 | NY | SOL-10994
Telegraph 1 | NY | SOL-11003
Telegraph 2 | NY | SOL-11004
Cafferty Hill | NY | SOL-10996
Dunkleman | NY | SOL-11008
Route 19 1 | NY | SOL-11001
Route 19 2 | NY | SOL-11002
Yellow Mills 1 | NY | SOL-11006
Yellow Mills 2 | NY | SOL-11005
Yellow Mills 3 | NY | SOL-11007
Catskill | NY | SOL-11021
Eddy Ridge | NY | SOL-11054
Ridgeway #1 | NY | SOL-11018
Rivard 1 | NY | SOL-11011
Rivard 2 | NY | SOL-11012
Ridgeway #2 | NY | SOL-11027
Spencer | NY | SOL-11017
Reisender | NY | SOL-10886
Finney | NY | SOL-10999
Davis Solar | NY | SOL-10958
Genesee | NY | SOL-10951
Landau I | NY | SOL-10891
Landau II | NY | SOL-10895
New Beginnings | NY | SOL-10890
Bullitt Farm Solar, LLC | NY | SOL-10998
Brodhead Solar, LLC | NY | SOL-10899
Svenski | NY | SOL-10894
Bantam | NY | SOL-10986
Bogart | NY | SOL-10887
Dubois | NY | SOL-10892
Salt Point | NY | SOL-10888
Wheatland 2A | NY | SOL-10971
Wheatland 2B | NY | SOL-10961
Brickchurch | NY | SOL-10889
McCarthy Solar | NY | SOL-10992
Costanza | NY | SOL-10907
Lockenhurst Pond | NY | SOL-11000
Drinkwater | NY | SOL-10896
Altamont | NY | SOL-11085
Krumkill North | NY | SOL-11086
Krumkill South | NY | SOL-11087
X092 | NY | SOL-11189
X093 | NY | SOL-10932
X095 | NY | SOL-10929
X181 | NY | SOL-10428
X415 | NY | SOL-10429
K198 | NY | SOL-10930
K203 | NY | SOL-11190
K213 | NY | SOL-11191
K217 | NY | SOL-10933
K307 | NY | SOL-10876
K610 | NY | SOL-11158
M025 | NY | SOL-10392
M028 | NY | SOL-10381
Q030 | NY | SOL-10878
Q130 | NY | SOL-10877
Q196 | NY | SOL-10879
Q220 | NY | SOL-10873
Q205 | NY | SOL-10922
Q400 | NY | SOL-10871
R003 | NY | SOL-10416
R007 | NY | SOL-10417
BK16 | NY | SOL-11093
Trenton - Trenton East | IL | SOL-11060
Trenton - Trenton West | IL | SOL-11061
Dakota - Dakota Solar 1 | IL | SOL-11113
X018 | NY | SOL-10418
Janiak Solar | NY | SOL-10898
County Route 11B | NY | SOL-10983
Barone | NY | SOL-11034
Cedarville | IL | SOL-11069
O'Brien Hill #1 | NY | SOL-11098
O'Brien Hill #2 | NY | SOL-11099
Trinity - Freeport | IL | SOL-11057
Ransom | NY | SOL-11157
Horseheads - Wedge | NY | SOL-11160
Otisville - Shoddy Hollow | NY | SOL-11185
Wellsville - Chenunda Creek | NY | SOL-11187
DC: Washington - Essex Condominium | DC | SOL-10036
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149
IL: Viola - Goldenrod - (PW) | IL | SOL-11132
IL: Marengo - Grant - (PW) | IL | SOL-11147
NY: Cambridge - Cambridge (PW) | NY
NY: Whitesville - Independence North | NY
IL: Beecher - Cottage Grove North (PW) | IL
IL: Beecher - Cottage Grove South (PW) | IL
IL: Harvard - 9618 US HWY 14 (PW) | IL
IL: Beecher - 701 E Goodenow Rd (PW) | IL
NY: Stormville - Green Haven - (IRA) | NY
IL: Hillsboro - Anacott (PW) | IL
IL: Manhattan - Gougar (PW) | IL
IL: Morrison - Sawyer (PW) | IL
IL: Kankakee - Jeffery (PW) | IL
IL: Freeport - 2240 South 18th Ave (PW) | IL

## May
Generate Capital |  |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
K026 | NY | SOL-10356
K041 | NY | SOL-10357
K043 | NY | SOL-10358
K058 | NY | SOL-10360
K115 | NY | SOL-10361
K152 | NY | SOL-10362
K166 | NY | SOL-10363
K206 | NY | SOL-10927
K251 | NY | SOL-10365
K269 | NY | SOL-10366
K273 | NY | SOL-10367
K287 | NY | SOL-10919
K298 | NY | SOL-10368
K335 | NY | SOL-10370
K345 | NY | SOL-10920
K445 | NY | SOL-10373
K495 | NY | SOL-10374
M020 | NY | SOL-10380
M092 | NY | SOL-10383
M143 | NY | SOL-10384
M144 | NY | SOL-10385
M167 | NY | SOL-10386
M188 | NY | SOL-10387
EMHC | NY | SOL-10351
Q008 | NY | SOL-10397
Q018 | NY | SOL-10398
Q021 | NY | SOL-10399
Q025 | NY | SOL-10400
Q074 | NY | SOL-10402
Q115 | NY | SOL-10872
Q139 | NY | SOL-10403
Q157 | NY | SOL-10404
Q192 | NY | SOL-10406
Q210 | NY | SOL-10407
Q229 | NY | SOL-10408
Q231 | NY | SOL-10870
Q405 | NY | SOL-10409
Q435 | NY | SOL-10923
Q485 | NY | SOL-10869
Q490 | NY | SOL-10411
Q620 | NY | SOL-10867
QMOA | NY | SOL-10415
X024 | NY | SOL-10419
X026 | NY | SOL-10420
X090 | NY | SOL-10925
X117 | NY | SOL-10422
X125 | NY | SOL-10423
X134 | NY | SOL-10424
X135 | NY | SOL-10425
X139 JHS 222 | NY | SOL-10426
X140 | NY | SOL-10926
X166 | NY | SOL-10427
Murphy | MN | SOL-10094
Terning | MN | SOL-10093
Boas Road 04 | NY | SOL-10908
Kelly Bridge Farm | NY | SOL-10911
Pool Brook Road | NY | SOL-10909
Sackett Lake | NY | SOL-10910
Burritt Road | NY | SOL-10913
Villa Roma 1 | NY | SOL-10914
Villa Roma 2 | NY | SOL-10915
Washington 1 | NY | SOL-10912
Washington 3 | NY | SOL-10828
Washington 4 | NY | SOL-10829
Big Tree | NY | SOL-10966
Canoga | NY | SOL-10965
County Route 84 | NY | SOL-10967
Donati | NY | SOL-10968
Henrietta | NY | SOL-10972
NY 70 | NY | SOL-10970
Reid | NY | SOL-10991
Sangolqui | NY | SOL-10975
State Highway 17B | NY | SOL-10988
State Route 14A | NY | SOL-10997
West Creek | NY | SOL-10995
Wildflower | NY | SOL-10982
Glen Mary 1 | NY | SOL-10993
Glen Mary 2 | NY | SOL-10994
Telegraph 1 | NY | SOL-11003
Telegraph 2 | NY | SOL-11004
Cafferty Hill | NY | SOL-10996
Dunkleman | NY | SOL-11008
Route 19 1 | NY | SOL-11001
Route 19 2 | NY | SOL-11002
Yellow Mills 1 | NY | SOL-11006
Yellow Mills 2 | NY | SOL-11005
Yellow Mills 3 | NY | SOL-11007
Catskill | NY | SOL-11021
Eddy Ridge | NY | SOL-11054
Ridgeway #1 | NY | SOL-11018
Rivard 1 | NY | SOL-11011
Rivard 2 | NY | SOL-11012
Ridgeway #2 | NY | SOL-11027
Spencer | NY | SOL-11017
Reisender | NY | SOL-10886
Finney | NY | SOL-10999
Davis Solar | NY | SOL-10958
Genesee | NY | SOL-10951
Landau I | NY | SOL-10891
Landau II | NY | SOL-10895
New Beginnings | NY | SOL-10890
Bullitt Farm Solar, LLC | NY | SOL-10998
Brodhead Solar, LLC | NY | SOL-10899
Svenski | NY | SOL-10894
Bantam | NY | SOL-10986
Bogart | NY | SOL-10887
Dubois | NY | SOL-10892
Salt Point | NY | SOL-10888
Wheatland 2A | NY | SOL-10971
Wheatland 2B | NY | SOL-10961
Brickchurch | NY | SOL-10889
McCarthy Solar | NY | SOL-10992
Costanza | NY | SOL-10907
Lockenhurst Pond | NY | SOL-11000
Drinkwater | NY | SOL-10896
Altamont | NY | SOL-11085
Krumkill North | NY | SOL-11086
Krumkill South | NY | SOL-11087
X092 | NY | SOL-11189
X093 | NY | SOL-10932
X095 | NY | SOL-10929
X181 | NY | SOL-10428
X415 | NY | SOL-10429 |  |  |  | 0%
K198 | NY | SOL-10930
K203 | NY | SOL-11190
K213 | NY | SOL-11191
K217 | NY | SOL-10933
K307 | NY | SOL-10876
K610 | NY | SOL-11158
M025 | NY | SOL-10392
M028 | NY | SOL-10381
Q030 | NY | SOL-10878
Q130 | NY | SOL-10877
Q196 | NY | SOL-10879
Q220 | NY | SOL-10873
Q205 | NY | SOL-10922
Q400 | NY | SOL-10871
R003 | NY | SOL-10416
R007 | NY | SOL-10417
BK16 | NY | SOL-11093
Trenton - Trenton East | IL | SOL-11060
Trenton - Trenton West | IL | SOL-11061
Dakota - Dakota Solar 1 | IL | SOL-11113
X018 | NY | SOL-10418
Janiak Solar | NY | SOL-10898
County Route 11B | NY | SOL-10983
Barone | NY | SOL-11034
Cedarville | IL | SOL-11069
O'Brien Hill #1 | NY | SOL-11098
O'Brien Hill #2 | NY | SOL-11099
Trinity - Freeport | IL | SOL-11057
Ransom | NY | SOL-11157
Horseheads - Wedge | NY | SOL-11160
Otisville - Shoddy Hollow | NY | SOL-11185
Wellsville - Chenunda Creek | NY | SOL-11187
DC: Washington - Essex Condominium | DC | SOL-10036
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149
IL: Viola - Goldenrod - (PW) | IL | SOL-11132
IL: Marengo - Grant - (PW) | IL | SOL-11147
NY: Cambridge - Cambridge (PW) | NY
NY: Whitesville - Independence North | NY
IL: Beecher - Cottage Grove North (PW) | IL
IL: Beecher - Cottage Grove South (PW) | IL
IL: Harvard - 9618 US HWY 14 (PW) | IL
IL: Beecher - 701 E Goodenow Rd (PW) | IL
NY: Stormville - Green Haven - (IRA) | NY
IL: Hillsboro - Anacott (PW) | IL
IL: Manhattan - Gougar (PW) | IL
IL: Morrison - Sawyer (PW) | IL
IL: Kankakee - Jeffery (PW) | IL
IL: Freeport - 2240 South 18th Ave (PW) | IL

## Jun
Generate Capital |  |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
K026 | NY | SOL-10356
K041 | NY | SOL-10357
K043 | NY | SOL-10358
K058 | NY | SOL-10360
K115 | NY | SOL-10361
K152 | NY | SOL-10362
K166 | NY | SOL-10363
K206 | NY | SOL-10927
K251 | NY | SOL-10365
K269 | NY | SOL-10366
K273 | NY | SOL-10367
K287 | NY | SOL-10919
K298 | NY | SOL-10368
K335 | NY | SOL-10370
K345 | NY | SOL-10920
K445 | NY | SOL-10373
K495 | NY | SOL-10374
M020 | NY | SOL-10380
M092 | NY | SOL-10383
M143 | NY | SOL-10384
M144 | NY | SOL-10385
M167 | NY | SOL-10386
M188 | NY | SOL-10387
EMHC | NY | SOL-10351
Q008 | NY | SOL-10397
Q018 | NY | SOL-10398
Q021 | NY | SOL-10399
Q025 | NY | SOL-10400
Q074 | NY | SOL-10402
Q115 | NY | SOL-10872
Q139 | NY | SOL-10403
Q157 | NY | SOL-10404
Q192 | NY | SOL-10406
Q210 | NY | SOL-10407
Q229 | NY | SOL-10408
Q231 | NY | SOL-10870
Q405 | NY | SOL-10409
Q435 | NY | SOL-10923
Q485 | NY | SOL-10869
Q490 | NY | SOL-10411
Q620 | NY | SOL-10867
QMOA | NY | SOL-10415
X024 | NY | SOL-10419
X026 | NY | SOL-10420
X090 | NY | SOL-10925
X117 | NY | SOL-10422
X125 | NY | SOL-10423
X134 | NY | SOL-10424
X135 | NY | SOL-10425
X139 JHS 222 | NY | SOL-10426
X140 | NY | SOL-10926
X166 | NY | SOL-10427
Murphy | MN | SOL-10094
Terning | MN | SOL-10093
Boas Road 04 | NY | SOL-10908
Kelly Bridge Farm | NY | SOL-10911
Pool Brook Road | NY | SOL-10909
Sackett Lake | NY | SOL-10910
Burritt Road | NY | SOL-10913
Villa Roma 1 | NY | SOL-10914
Villa Roma 2 | NY | SOL-10915
Washington 1 | NY | SOL-10912
Washington 3 | NY | SOL-10828
Washington 4 | NY | SOL-10829
Big Tree | NY | SOL-10966
Canoga | NY | SOL-10965
County Route 84 | NY | SOL-10967
Donati | NY | SOL-10968
Henrietta | NY | SOL-10972
NY 70 | NY | SOL-10970
Reid | NY | SOL-10991
Sangolqui | NY | SOL-10975
State Highway 17B | NY | SOL-10988
State Route 14A | NY | SOL-10997
West Creek | NY | SOL-10995
Wildflower | NY | SOL-10982
Glen Mary 1 | NY | SOL-10993
Glen Mary 2 | NY | SOL-10994
Telegraph 1 | NY | SOL-11003
Telegraph 2 | NY | SOL-11004
Cafferty Hill | NY | SOL-10996
Dunkleman | NY | SOL-11008
Route 19 1 | NY | SOL-11001
Route 19 2 | NY | SOL-11002
Yellow Mills 1 | NY | SOL-11006
Yellow Mills 2 | NY | SOL-11005
Yellow Mills 3 | NY | SOL-11007
Catskill | NY | SOL-11021
Eddy Ridge | NY | SOL-11054
Ridgeway #1 | NY | SOL-11018
Rivard 1 | NY | SOL-11011
Rivard 2 | NY | SOL-11012
Ridgeway #2 | NY | SOL-11027
Spencer | NY | SOL-11017
Reisender | NY | SOL-10886
Finney | NY | SOL-10999
Davis Solar | NY | SOL-10958
Genesee | NY | SOL-10951
Landau I | NY | SOL-10891
Landau II | NY | SOL-10895
New Beginnings | NY | SOL-10890
Bullitt Farm Solar, LLC | NY | SOL-10998
Brodhead Solar, LLC | NY | SOL-10899
Svenski | NY | SOL-10894
Bantam | NY | SOL-10986
Bogart | NY | SOL-10887
Dubois | NY | SOL-10892
Salt Point | NY | SOL-10888
Wheatland 2A | NY | SOL-10971
Wheatland 2B | NY | SOL-10961
Brickchurch | NY | SOL-10889
McCarthy Solar | NY | SOL-10992
Costanza | NY | SOL-10907
Lockenhurst Pond | NY | SOL-11000
Drinkwater | NY | SOL-10896
Altamont | NY | SOL-11085
Krumkill North | NY | SOL-11086
Krumkill South | NY | SOL-11087
X092 | NY | SOL-11189
X093 | NY | SOL-10932
X095 | NY | SOL-10929
X181 | NY | SOL-10428
X415 | NY | SOL-10429
K198 | NY | SOL-10930
K203 | NY | SOL-11190
K213 | NY | SOL-11191
K217 | NY | SOL-10933
K307 | NY | SOL-10876
K610 | NY | SOL-11158
M025 | NY | SOL-10392
M028 | NY | SOL-10381
Q030 | NY | SOL-10878
Q130 | NY | SOL-10877
Q196 | NY | SOL-10879
Q220 | NY | SOL-10873
Q205 | NY | SOL-10922
Q400 | NY | SOL-10871
R003 | NY | SOL-10416
R007 | NY | SOL-10417
BK16 | NY | SOL-11093
Trenton - Trenton East | IL | SOL-11060
Trenton - Trenton West | IL | SOL-11061
Dakota - Dakota Solar 1 | IL | SOL-11113
X018 | NY | SOL-10418
Janiak Solar | NY | SOL-10898
County Route 11B | NY | SOL-10983
Barone | NY | SOL-11034
Cedarville | IL | SOL-11069
O'Brien Hill #1 | NY | SOL-11098
O'Brien Hill #2 | NY | SOL-11099
Trinity - Freeport | IL | SOL-11057
Ransom | NY | SOL-11157
Horseheads - Wedge | NY | SOL-11160
Otisville - Shoddy Hollow | NY | SOL-11185
Wellsville - Chenunda Creek | NY | SOL-11187
DC: Washington - Essex Condominium | DC | SOL-10036
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149
IL: Viola - Goldenrod - (PW) | IL | SOL-11132
IL: Marengo - Grant - (PW) | IL | SOL-11147
NY: Cambridge - Cambridge (PW) | NY
NY: Whitesville - Independence North | NY
IL: Beecher - Cottage Grove North (PW) | IL
IL: Beecher - Cottage Grove South (PW) | IL
IL: Harvard - 9618 US HWY 14 (PW) | IL
IL: Beecher - 701 E Goodenow Rd (PW) | IL
NY: Stormville - Green Haven - (IRA) | NY
IL: Hillsboro - Anacott (PW) | IL
IL: Manhattan - Gougar (PW) | IL
IL: Morrison - Sawyer (PW) | IL
IL: Kankakee - Jeffery (PW) | IL
IL: Freeport - 2240 South 18th Ave (PW) | IL

## Jul
Generate Capital |  |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
K026 | NY | SOL-10356
K041 | NY | SOL-10357
K043 | NY | SOL-10358
K058 | NY | SOL-10360
K115 | NY | SOL-10361
K152 | NY | SOL-10362
K166 | NY | SOL-10363
K206 | NY | SOL-10927
K251 | NY | SOL-10365
K269 | NY | SOL-10366
K273 | NY | SOL-10367
K287 | NY | SOL-10919
K298 | NY | SOL-10368
K335 | NY | SOL-10370
K345 | NY | SOL-10920
K445 | NY | SOL-10373
K495 | NY | SOL-10374
M020 | NY | SOL-10380
M092 | NY | SOL-10383
M143 | NY | SOL-10384
M144 | NY | SOL-10385
M167 | NY | SOL-10386
M188 | NY | SOL-10387
EMHC | NY | SOL-10351
Q008 | NY | SOL-10397
Q018 | NY | SOL-10398
Q021 | NY | SOL-10399
Q025 | NY | SOL-10400
Q074 | NY | SOL-10402
Q115 | NY | SOL-10872
Q139 | NY | SOL-10403
Q157 | NY | SOL-10404
Q192 | NY | SOL-10406
Q210 | NY | SOL-10407
Q229 | NY | SOL-10408
Q231 | NY | SOL-10870
Q405 | NY | SOL-10409
Q435 | NY | SOL-10923
Q485 | NY | SOL-10869
Q490 | NY | SOL-10411
Q620 | NY | SOL-10867
QMOA | NY | SOL-10415
X024 | NY | SOL-10419
X026 | NY | SOL-10420
X090 | NY | SOL-10925
X117 | NY | SOL-10422
X125 | NY | SOL-10423
X134 | NY | SOL-10424
X135 | NY | SOL-10425
X139 JHS 222 | NY | SOL-10426
X140 | NY | SOL-10926
X166 | NY | SOL-10427
Murphy | MN | SOL-10094
Terning | MN | SOL-10093
Boas Road 04 | NY | SOL-10908
Kelly Bridge Farm | NY | SOL-10911
Pool Brook Road | NY | SOL-10909
Sackett Lake | NY | SOL-10910
Burritt Road | NY | SOL-10913
Villa Roma 1 | NY | SOL-10914
Villa Roma 2 | NY | SOL-10915
Washington 1 | NY | SOL-10912
Washington 3 | NY | SOL-10828
Washington 4 | NY | SOL-10829
Big Tree | NY | SOL-10966
Canoga | NY | SOL-10965
County Route 84 | NY | SOL-10967
Donati | NY | SOL-10968
Henrietta | NY | SOL-10972
NY 70 | NY | SOL-10970
Reid | NY | SOL-10991
Sangolqui | NY | SOL-10975
State Highway 17B | NY | SOL-10988
State Route 14A | NY | SOL-10997
West Creek | NY | SOL-10995
Wildflower | NY | SOL-10982
Glen Mary 1 | NY | SOL-10993
Glen Mary 2 | NY | SOL-10994
Telegraph 1 | NY | SOL-11003
Telegraph 2 | NY | SOL-11004
Cafferty Hill | NY | SOL-10996
Dunkleman | NY | SOL-11008
Route 19 1 | NY | SOL-11001
Route 19 2 | NY | SOL-11002
Yellow Mills 1 | NY | SOL-11006
Yellow Mills 2 | NY | SOL-11005
Yellow Mills 3 | NY | SOL-11007
Catskill | NY | SOL-11021
Eddy Ridge | NY | SOL-11054
Ridgeway #1 | NY | SOL-11018
Rivard 1 | NY | SOL-11011
Rivard 2 | NY | SOL-11012
Ridgeway #2 | NY | SOL-11027
Spencer | NY | SOL-11017
Reisender | NY | SOL-10886
Finney | NY | SOL-10999
Davis Solar | NY | SOL-10958
Genesee | NY | SOL-10951
Landau I | NY | SOL-10891
Landau II | NY | SOL-10895
New Beginnings | NY | SOL-10890
Bullitt Farm Solar, LLC | NY | SOL-10998
Brodhead Solar, LLC | NY | SOL-10899
Svenski | NY | SOL-10894
Bantam | NY | SOL-10986
Bogart | NY | SOL-10887
Dubois | NY | SOL-10892
Salt Point | NY | SOL-10888
Wheatland 2A | NY | SOL-10971
Wheatland 2B | NY | SOL-10961
Brickchurch | NY | SOL-10889
McCarthy Solar | NY | SOL-10992
Costanza | NY | SOL-10907
Lockenhurst Pond | NY | SOL-11000
Drinkwater | NY | SOL-10896
Altamont | NY | SOL-11085
Krumkill North | NY | SOL-11086
Krumkill South | NY | SOL-11087
X092 | NY | SOL-11189
X093 | NY | SOL-10932
X095 | NY | SOL-10929
X181 | NY | SOL-10428
X415 | NY | SOL-10429
K198 | NY | SOL-10930
K203 | NY | SOL-11190
K213 | NY | SOL-11191
K217 | NY | SOL-10933
K307 | NY | SOL-10876
K610 | NY | SOL-11158
M025 | NY | SOL-10392
M028 | NY | SOL-10381
Q030 | NY | SOL-10878
Q130 | NY | SOL-10877
Q196 | NY | SOL-10879
Q220 | NY | SOL-10873
Q205 | NY | SOL-10922
Q400 | NY | SOL-10871
R003 | NY | SOL-10416
R007 | NY | SOL-10417
BK16 | NY | SOL-11093
Trenton - Trenton East | IL | SOL-11060
Trenton - Trenton West | IL | SOL-11061
Dakota - Dakota Solar 1 | IL | SOL-11113
X018 | NY | SOL-10418
Janiak Solar | NY | SOL-10898
County Route 11B | NY | SOL-10983
Barone | NY | SOL-11034
Cedarville | IL | SOL-11069
O'Brien Hill #1 | NY | SOL-11098
O'Brien Hill #2 | NY | SOL-11099
Trinity - Freeport | IL | SOL-11057
Ransom | NY | SOL-11157
Horseheads - Wedge | NY | SOL-11160
Otisville - Shoddy Hollow | NY | SOL-11185
Wellsville - Chenunda Creek | NY | SOL-11187
DC: Washington - Essex Condominium | DC | SOL-10036
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149
IL: Viola - Goldenrod - (PW) | IL | SOL-11132
IL: Marengo - Grant - (PW) | IL | SOL-11147
NY: Cambridge - Cambridge (PW) | NY
NY: Whitesville - Independence North | NY
IL: Beecher - Cottage Grove North (PW) | IL
IL: Beecher - Cottage Grove South (PW) | IL
IL: Harvard - 9618 US HWY 14 (PW) | IL
IL: Beecher - 701 E Goodenow Rd (PW) | IL
NY: Stormville - Green Haven - (IRA) | NY
IL: Hillsboro - Anacott (PW) | IL
IL: Manhattan - Gougar (PW) | IL
IL: Morrison - Sawyer (PW) | IL
IL: Kankakee - Jeffery (PW) | IL
IL: Freeport - 2240 South 18th Ave (PW) | IL

## Aug
Generate Capital |  |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
K026 | NY | SOL-10356
K041 | NY | SOL-10357
K043 | NY | SOL-10358
K058 | NY | SOL-10360
K115 | NY | SOL-10361
K152 | NY | SOL-10362
K166 | NY | SOL-10363
K206 | NY | SOL-10927
K251 | NY | SOL-10365
K269 | NY | SOL-10366
K273 | NY | SOL-10367
K287 | NY | SOL-10919
K298 | NY | SOL-10368
K335 | NY | SOL-10370
K345 | NY | SOL-10920
K445 | NY | SOL-10373
K495 | NY | SOL-10374
M020 | NY | SOL-10380
M092 | NY | SOL-10383
M143 | NY | SOL-10384
M144 | NY | SOL-10385
M167 | NY | SOL-10386
M188 | NY | SOL-10387
EMHC | NY | SOL-10351
Q008 | NY | SOL-10397
Q018 | NY | SOL-10398
Q021 | NY | SOL-10399
Q025 | NY | SOL-10400
Q074 | NY | SOL-10402
Q115 | NY | SOL-10872
Q139 | NY | SOL-10403
Q157 | NY | SOL-10404
Q192 | NY | SOL-10406
Q210 | NY | SOL-10407
Q229 | NY | SOL-10408
Q231 | NY | SOL-10870
Q405 | NY | SOL-10409
Q435 | NY | SOL-10923
Q485 | NY | SOL-10869
Q490 | NY | SOL-10411
Q620 | NY | SOL-10867
QMOA | NY | SOL-10415
X024 | NY | SOL-10419
X026 | NY | SOL-10420
X090 | NY | SOL-10925
X117 | NY | SOL-10422
X125 | NY | SOL-10423
X134 | NY | SOL-10424
X135 | NY | SOL-10425
X139 JHS 222 | NY | SOL-10426
X140 | NY | SOL-10926
X166 | NY | SOL-10427
Murphy | MN | SOL-10094
Terning | MN | SOL-10093
Boas Road 04 | NY | SOL-10908
Kelly Bridge Farm | NY | SOL-10911
Pool Brook Road | NY | SOL-10909
Sackett Lake | NY | SOL-10910
Burritt Road | NY | SOL-10913
Villa Roma 1 | NY | SOL-10914
Villa Roma 2 | NY | SOL-10915
Washington 1 | NY | SOL-10912
Washington 3 | NY | SOL-10828
Washington 4 | NY | SOL-10829
Big Tree | NY | SOL-10966
Canoga | NY | SOL-10965
County Route 84 | NY | SOL-10967
Donati | NY | SOL-10968
Henrietta | NY | SOL-10972
NY 70 | NY | SOL-10970
Reid | NY | SOL-10991
Sangolqui | NY | SOL-10975
State Highway 17B | NY | SOL-10988
State Route 14A | NY | SOL-10997
West Creek | NY | SOL-10995
Wildflower | NY | SOL-10982
Glen Mary 1 | NY | SOL-10993
Glen Mary 2 | NY | SOL-10994
Telegraph 1 | NY | SOL-11003
Telegraph 2 | NY | SOL-11004
Cafferty Hill | NY | SOL-10996
Dunkleman | NY | SOL-11008
Route 19 1 | NY | SOL-11001
Route 19 2 | NY | SOL-11002
Yellow Mills 1 | NY | SOL-11006
Yellow Mills 2 | NY | SOL-11005
Yellow Mills 3 | NY | SOL-11007
Catskill | NY | SOL-11021
Eddy Ridge | NY | SOL-11054
Ridgeway #1 | NY | SOL-11018
Rivard 1 | NY | SOL-11011
Rivard 2 | NY | SOL-11012
Ridgeway #2 | NY | SOL-11027
Spencer | NY | SOL-11017
Reisender | NY | SOL-10886
Finney | NY | SOL-10999
Davis Solar | NY | SOL-10958
Genesee | NY | SOL-10951
Landau I | NY | SOL-10891
Landau II | NY | SOL-10895
New Beginnings | NY | SOL-10890
Bullitt Farm Solar, LLC | NY | SOL-10998
Brodhead Solar, LLC | NY | SOL-10899
Svenski | NY | SOL-10894
Bantam | NY | SOL-10986
Bogart | NY | SOL-10887
Dubois | NY | SOL-10892
Salt Point | NY | SOL-10888
Wheatland 2A | NY | SOL-10971
Wheatland 2B | NY | SOL-10961
Brickchurch | NY | SOL-10889
McCarthy Solar | NY | SOL-10992
Costanza | NY | SOL-10907
Lockenhurst Pond | NY | SOL-11000
Drinkwater | NY | SOL-10896
Altamont | NY | SOL-11085
Krumkill North | NY | SOL-11086
Krumkill South | NY | SOL-11087
X092 | NY | SOL-11189
X093 | NY | SOL-10932
X095 | NY | SOL-10929
X181 | NY | SOL-10428
X415 | NY | SOL-10429
K198 | NY | SOL-10930
K203 | NY | SOL-11190
K213 | NY | SOL-11191
K217 | NY | SOL-10933
K307 | NY | SOL-10876
K610 | NY | SOL-11158
M025 | NY | SOL-10392
M028 | NY | SOL-10381
Q030 | NY | SOL-10878
Q130 | NY | SOL-10877
Q196 | NY | SOL-10879
Q220 | NY | SOL-10873
Q205 | NY | SOL-10922
Q400 | NY | SOL-10871
R003 | NY | SOL-10416
R007 | NY | SOL-10417
BK16 | NY | SOL-11093
Trenton - Trenton East | IL | SOL-11060
Trenton - Trenton West | IL | SOL-11061
Dakota - Dakota Solar 1 | IL | SOL-11113
X018 | NY | SOL-10418
Janiak Solar | NY | SOL-10898
County Route 11B | NY | SOL-10983
Barone | NY | SOL-11034
Cedarville | IL | SOL-11069
O'Brien Hill #1 | NY | SOL-11098
O'Brien Hill #2 | NY | SOL-11099
Trinity - Freeport | IL | SOL-11057
Ransom | NY | SOL-11157
Horseheads - Wedge | NY | SOL-11160
Otisville - Shoddy Hollow | NY | SOL-11185
Wellsville - Chenunda Creek | NY | SOL-11187
DC: Washington - Essex Condominium | DC | SOL-10036
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149
IL: Viola - Goldenrod - (PW) | IL | SOL-11132
IL: Marengo - Grant - (PW) | IL | SOL-11147
NY: Cambridge - Cambridge (PW) | NY
NY: Whitesville - Independence North | NY
IL: Beecher - Cottage Grove North (PW) | IL
IL: Beecher - Cottage Grove South (PW) | IL
IL: Harvard - 9618 US HWY 14 (PW) | IL
IL: Beecher - 701 E Goodenow Rd (PW) | IL
NY: Stormville - Green Haven - (IRA) | NY
IL: Hillsboro - Anacott (PW) | IL
IL: Manhattan - Gougar (PW) | IL
IL: Morrison - Sawyer (PW) | IL
IL: Kankakee - Jeffery (PW) | IL
IL: Freeport - 2240 South 18th Ave (PW) | IL

## Sep
Generate Capital |  |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
K026 | NY | SOL-10356
K041 | NY | SOL-10357
K043 | NY | SOL-10358
K058 | NY | SOL-10360
K115 | NY | SOL-10361
K152 | NY | SOL-10362
K166 | NY | SOL-10363
K206 | NY | SOL-10927
K251 | NY | SOL-10365
K269 | NY | SOL-10366
K273 | NY | SOL-10367
K287 | NY | SOL-10919
K298 | NY | SOL-10368
K335 | NY | SOL-10370
K345 | NY | SOL-10920
K445 | NY | SOL-10373
K495 | NY | SOL-10374
M020 | NY | SOL-10380
M092 | NY | SOL-10383
M143 | NY | SOL-10384
M144 | NY | SOL-10385
M167 | NY | SOL-10386
M188 | NY | SOL-10387
EMHC | NY | SOL-10351
Q008 | NY | SOL-10397
Q018 | NY | SOL-10398
Q021 | NY | SOL-10399
Q025 | NY | SOL-10400
Q074 | NY | SOL-10402
Q115 | NY | SOL-10872
Q139 | NY | SOL-10403
Q157 | NY | SOL-10404
Q192 | NY | SOL-10406
Q210 | NY | SOL-10407
Q229 | NY | SOL-10408
Q231 | NY | SOL-10870
Q405 | NY | SOL-10409
Q435 | NY | SOL-10923
Q485 | NY | SOL-10869
Q490 | NY | SOL-10411
Q620 | NY | SOL-10867
QMOA | NY | SOL-10415
X024 | NY | SOL-10419
X026 | NY | SOL-10420
X090 | NY | SOL-10925
X117 | NY | SOL-10422
X125 | NY | SOL-10423
X134 | NY | SOL-10424
X135 | NY | SOL-10425
X139 JHS 222 | NY | SOL-10426
X140 | NY | SOL-10926
X166 | NY | SOL-10427
Murphy | MN | SOL-10094
Terning | MN | SOL-10093
Boas Road 04 | NY | SOL-10908
Kelly Bridge Farm | NY | SOL-10911
Pool Brook Road | NY | SOL-10909
Sackett Lake | NY | SOL-10910
Burritt Road | NY | SOL-10913
Villa Roma 1 | NY | SOL-10914
Villa Roma 2 | NY | SOL-10915
Washington 1 | NY | SOL-10912
Washington 3 | NY | SOL-10828
Washington 4 | NY | SOL-10829
Big Tree | NY | SOL-10966
Canoga | NY | SOL-10965
County Route 84 | NY | SOL-10967
Donati | NY | SOL-10968
Henrietta | NY | SOL-10972
NY 70 | NY | SOL-10970
Reid | NY | SOL-10991
Sangolqui | NY | SOL-10975
State Highway 17B | NY | SOL-10988
State Route 14A | NY | SOL-10997
West Creek | NY | SOL-10995
Wildflower | NY | SOL-10982
Glen Mary 1 | NY | SOL-10993
Glen Mary 2 | NY | SOL-10994
Telegraph 1 | NY | SOL-11003
Telegraph 2 | NY | SOL-11004
Cafferty Hill | NY | SOL-10996
Dunkleman | NY | SOL-11008
Route 19 1 | NY | SOL-11001
Route 19 2 | NY | SOL-11002
Yellow Mills 1 | NY | SOL-11006
Yellow Mills 2 | NY | SOL-11005
Yellow Mills 3 | NY | SOL-11007
Catskill | NY | SOL-11021
Eddy Ridge | NY | SOL-11054
Ridgeway #1 | NY | SOL-11018
Rivard 1 | NY | SOL-11011
Rivard 2 | NY | SOL-11012
Ridgeway #2 | NY | SOL-11027
Spencer | NY | SOL-11017
Reisender | NY | SOL-10886
Finney | NY | SOL-10999
Davis Solar | NY | SOL-10958
Genesee | NY | SOL-10951
Landau I | NY | SOL-10891
Landau II | NY | SOL-10895
New Beginnings | NY | SOL-10890
Bullitt Farm Solar, LLC | NY | SOL-10998
Brodhead Solar, LLC | NY | SOL-10899
Svenski | NY | SOL-10894
Bantam | NY | SOL-10986
Bogart | NY | SOL-10887
Dubois | NY | SOL-10892
Salt Point | NY | SOL-10888
Wheatland 2A | NY | SOL-10971
Wheatland 2B | NY | SOL-10961
Brickchurch | NY | SOL-10889
McCarthy Solar | NY | SOL-10992
Costanza | NY | SOL-10907
Lockenhurst Pond | NY | SOL-11000
Drinkwater | NY | SOL-10896
Altamont | NY | SOL-11085
Krumkill North | NY | SOL-11086
Krumkill South | NY | SOL-11087
X092 | NY | SOL-11189
X093 | NY | SOL-10932
X095 | NY | SOL-10929
X181 | NY | SOL-10428
X415 | NY | SOL-10429
K198 | NY | SOL-10930
K203 | NY | SOL-11190
K213 | NY | SOL-11191
K217 | NY | SOL-10933
K307 | NY | SOL-10876
K610 | NY | SOL-11158
M025 | NY | SOL-10392
M028 | NY | SOL-10381
Q030 | NY | SOL-10878
Q130 | NY | SOL-10877
Q196 | NY | SOL-10879
Q220 | NY | SOL-10873
Q205 | NY | SOL-10922
Q400 | NY | SOL-10871
R003 | NY | SOL-10416
R007 | NY | SOL-10417
BK16 | NY | SOL-11093
Trenton - Trenton East | IL | SOL-11060
Trenton - Trenton West | IL | SOL-11061
Dakota - Dakota Solar 1 | IL | SOL-11113
X018 | NY | SOL-10418
Janiak Solar | NY | SOL-10898
County Route 11B | NY | SOL-10983
Barone | NY | SOL-11034
Cedarville | IL | SOL-11069
O'Brien Hill #1 | NY | SOL-11098
O'Brien Hill #2 | NY | SOL-11099
Trinity - Freeport | IL | SOL-11057
Ransom | NY | SOL-11157
Horseheads - Wedge | NY | SOL-11160
Otisville - Shoddy Hollow | NY | SOL-11185
Wellsville - Chenunda Creek | NY | SOL-11187
DC: Washington - Essex Condominium | DC | SOL-10036
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149
IL: Viola - Goldenrod - (PW) | IL | SOL-11132
IL: Marengo - Grant - (PW) | IL | SOL-11147
NY: Cambridge - Cambridge (PW) | NY | SOL-11126
NY: Whitesville - Independence North | NY | SOL-11186
IL: Beecher - Cottage Grove North (PW) | IL
IL: Beecher - Cottage Grove South (PW) | IL
IL: Harvard - 9618 US HWY 14 (PW) | IL
IL: Beecher - 701 E Goodenow Rd (PW) | IL
NY: Stormville - Green Haven - (IRA) | NY
IL: Hillsboro - Anacott (PW) | IL
IL: Manhattan - Gougar (PW) | IL
IL: Morrison - Sawyer (PW) | IL
IL: Kankakee - Jeffery (PW) | IL
IL: Freeport - 2240 South 18th Ave (PW) | IL

## Oct
Generate Capital |  |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
K026 | NY | SOL-10356
K041 | NY | SOL-10357
K043 | NY | SOL-10358
K058 | NY | SOL-10360
K115 | NY | SOL-10361
K152 | NY | SOL-10362
K166 | NY | SOL-10363
K206 | NY | SOL-10927
K251 | NY | SOL-10365
K269 | NY | SOL-10366
K273 | NY | SOL-10367
K287 | NY | SOL-10919
K298 | NY | SOL-10368
K335 | NY | SOL-10370
K345 | NY | SOL-10920
K445 | NY | SOL-10373
K495 | NY | SOL-10374
M020 | NY | SOL-10380
M092 | NY | SOL-10383
M143 | NY | SOL-10384
M144 | NY | SOL-10385
M167 | NY | SOL-10386
M188 | NY | SOL-10387
EMHC | NY | SOL-10351
Q008 | NY | SOL-10397
Q018 | NY | SOL-10398
Q021 | NY | SOL-10399
Q025 | NY | SOL-10400
Q074 | NY | SOL-10402
Q115 | NY | SOL-10872
Q139 | NY | SOL-10403
Q157 | NY | SOL-10404
Q192 | NY | SOL-10406
Q210 | NY | SOL-10407
Q229 | NY | SOL-10408
Q231 | NY | SOL-10870
Q405 | NY | SOL-10409
Q435 | NY | SOL-10923
Q485 | NY | SOL-10869
Q490 | NY | SOL-10411
Q620 | NY | SOL-10867
QMOA | NY | SOL-10415
X024 | NY | SOL-10419
X026 | NY | SOL-10420
X090 | NY | SOL-10925
X117 | NY | SOL-10422
X125 | NY | SOL-10423
X134 | NY | SOL-10424
X135 | NY | SOL-10425
X139 JHS 222 | NY | SOL-10426
X140 | NY | SOL-10926
X166 | NY | SOL-10427
Murphy | MN | SOL-10094
Terning | MN | SOL-10093
Boas Road 04 | NY | SOL-10908
Kelly Bridge Farm | NY | SOL-10911
Pool Brook Road | NY | SOL-10909
Sackett Lake | NY | SOL-10910
Burritt Road | NY | SOL-10913
Villa Roma 1 | NY | SOL-10914
Villa Roma 2 | NY | SOL-10915
Washington 1 | NY | SOL-10912
Washington 3 | NY | SOL-10828
Washington 4 | NY | SOL-10829
Big Tree | NY | SOL-10966
Canoga | NY | SOL-10965
County Route 84 | NY | SOL-10967
Donati | NY | SOL-10968
Henrietta | NY | SOL-10972
NY 70 | NY | SOL-10970
Reid | NY | SOL-10991
Sangolqui | NY | SOL-10975
State Highway 17B | NY | SOL-10988
State Route 14A | NY | SOL-10997
West Creek | NY | SOL-10995
Wildflower | NY | SOL-10982
Glen Mary 1 | NY | SOL-10993
Glen Mary 2 | NY | SOL-10994
Telegraph 1 | NY | SOL-11003
Telegraph 2 | NY | SOL-11004
Cafferty Hill | NY | SOL-10996
Dunkleman | NY | SOL-11008
Route 19 1 | NY | SOL-11001
Route 19 2 | NY | SOL-11002
Yellow Mills 1 | NY | SOL-11006
Yellow Mills 2 | NY | SOL-11005
Yellow Mills 3 | NY | SOL-11007
Catskill | NY | SOL-11021
Eddy Ridge | NY | SOL-11054
Ridgeway #1 | NY | SOL-11018
Rivard 1 | NY | SOL-11011
Rivard 2 | NY | SOL-11012
Ridgeway #2 | NY | SOL-11027
Spencer | NY | SOL-11017
Reisender | NY | SOL-10886
Finney | NY | SOL-10999
Davis Solar | NY | SOL-10958
Genesee | NY | SOL-10951
Landau I | NY | SOL-10891
Landau II | NY | SOL-10895
New Beginnings | NY | SOL-10890
Bullitt Farm Solar, LLC | NY | SOL-10998
Brodhead Solar, LLC | NY | SOL-10899
Svenski | NY | SOL-10894
Bantam | NY | SOL-10986
Bogart | NY | SOL-10887
Dubois | NY | SOL-10892
Salt Point | NY | SOL-10888
Wheatland 2A | NY | SOL-10971
Wheatland 2B | NY | SOL-10961
Brickchurch | NY | SOL-10889
McCarthy Solar | NY | SOL-10992
Costanza | NY | SOL-10907
Lockenhurst Pond | NY | SOL-11000
Drinkwater | NY | SOL-10896
Altamont | NY | SOL-11085
Krumkill North | NY | SOL-11086
Krumkill South | NY | SOL-11087
X092 | NY | SOL-11189
X093 | NY | SOL-10932
X095 | NY | SOL-10929
X181 | NY | SOL-10428
X415 | NY | SOL-10429
K198 | NY | SOL-10930
K203 | NY | SOL-11190
K213 | NY | SOL-11191
K217 | NY | SOL-10933
K307 | NY | SOL-10876
K610 | NY | SOL-11158
M025 | NY | SOL-10392
M028 | NY | SOL-10381
Q030 | NY | SOL-10878
Q130 | NY | SOL-10877
Q196 | NY | SOL-10879
Q220 | NY | SOL-10873
Q205 | NY | SOL-10922
Q400 | NY | SOL-10871
R003 | NY | SOL-10416
R007 | NY | SOL-10417
BK16 | NY | SOL-11093
Trenton - Trenton East | IL | SOL-11060
Trenton - Trenton West | IL | SOL-11061
Dakota - Dakota Solar 1 | IL | SOL-11113
X018 | NY | SOL-10418
Janiak Solar | NY | SOL-10898
County Route 11B | NY | SOL-10983
Barone | NY | SOL-11034
Cedarville | IL | SOL-11069
O'Brien Hill #1 | NY | SOL-11098
O'Brien Hill #2 | NY | SOL-11099
Trinity - Freeport | IL | SOL-11057
Ransom | NY | SOL-11157
Horseheads - Wedge | NY | SOL-11160
Otisville - Shoddy Hollow | NY | SOL-11185
Wellsville - Chenunda Creek | NY | SOL-11187
DC: Washington - Essex Condominium | DC | SOL-10036
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149
IL: Viola - Goldenrod - (PW) | IL | SOL-11132
IL: Marengo - Grant - (PW) | IL | SOL-11147
NY: Cambridge - Cambridge (PW) | NY | SOL-11126
NY: Whitesville - Independence North | NY | SOL-11186
IL: Beecher - Cottage Grove North (PW) | IL | SOL-11114
IL: Beecher - Cottage Grove South (PW) | IL | SOL-11115
IL: Harvard - 9618 US HWY 14 (PW) | IL | SOL-11110
IL: Beecher - 701 E Goodenow Rd (PW) | IL | SOL-11112
NY: Stormville - Green Haven - (IRA) | NY | SOL-11151
IL: Hillsboro - Anacott (PW) | IL
IL: Manhattan - Gougar (PW) | IL
IL: Morrison - Sawyer (PW) | IL
IL: Kankakee - Jeffery (PW) | IL
IL: Freeport - 2240 South 18th Ave (PW) | IL

## Nov
Generate Capital |  |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
K026 | NY | SOL-10356
K041 | NY | SOL-10357
K043 | NY | SOL-10358
K058 | NY | SOL-10360
K115 | NY | SOL-10361
K152 | NY | SOL-10362
K166 | NY | SOL-10363
K206 | NY | SOL-10927
K251 | NY | SOL-10365
K269 | NY | SOL-10366
K273 | NY | SOL-10367
K287 | NY | SOL-10919
K298 | NY | SOL-10368
K335 | NY | SOL-10370
K345 | NY | SOL-10920
K445 | NY | SOL-10373
K495 | NY | SOL-10374
M020 | NY | SOL-10380
M092 | NY | SOL-10383
M143 | NY | SOL-10384
M144 | NY | SOL-10385
M167 | NY | SOL-10386
M188 | NY | SOL-10387
EMHC | NY | SOL-10351
Q008 | NY | SOL-10397
Q018 | NY | SOL-10398
Q021 | NY | SOL-10399
Q025 | NY | SOL-10400
Q074 | NY | SOL-10402
Q115 | NY | SOL-10872
Q139 | NY | SOL-10403
Q157 | NY | SOL-10404
Q192 | NY | SOL-10406
Q210 | NY | SOL-10407
Q229 | NY | SOL-10408
Q231 | NY | SOL-10870
Q405 | NY | SOL-10409
Q435 | NY | SOL-10923
Q485 | NY | SOL-10869
Q490 | NY | SOL-10411
Q620 | NY | SOL-10867
QMOA | NY | SOL-10415
X024 | NY | SOL-10419
X026 | NY | SOL-10420
X090 | NY | SOL-10925
X117 | NY | SOL-10422
X125 | NY | SOL-10423
X134 | NY | SOL-10424
X135 | NY | SOL-10425
X139 JHS 222 | NY | SOL-10426
X140 | NY | SOL-10926
X166 | NY | SOL-10427
Murphy | MN | SOL-10094
Terning | MN | SOL-10093
Boas Road 04 | NY | SOL-10908
Kelly Bridge Farm | NY | SOL-10911
Pool Brook Road | NY | SOL-10909
Sackett Lake | NY | SOL-10910
Burritt Road | NY | SOL-10913
Villa Roma 1 | NY | SOL-10914
Villa Roma 2 | NY | SOL-10915
Washington 1 | NY | SOL-10912
Washington 3 | NY | SOL-10828
Washington 4 | NY | SOL-10829
Big Tree | NY | SOL-10966
Canoga | NY | SOL-10965
County Route 84 | NY | SOL-10967
Donati | NY | SOL-10968
Henrietta | NY | SOL-10972
NY 70 | NY | SOL-10970
Reid | NY | SOL-10991
Sangolqui | NY | SOL-10975
State Highway 17B | NY | SOL-10988
State Route 14A | NY | SOL-10997
West Creek | NY | SOL-10995
Wildflower | NY | SOL-10982
Glen Mary 1 | NY | SOL-10993
Glen Mary 2 | NY | SOL-10994
Telegraph 1 | NY | SOL-11003
Telegraph 2 | NY | SOL-11004
Cafferty Hill | NY | SOL-10996
Dunkleman | NY | SOL-11008
Route 19 1 | NY | SOL-11001
Route 19 2 | NY | SOL-11002
Yellow Mills 1 | NY | SOL-11006
Yellow Mills 2 | NY | SOL-11005
Yellow Mills 3 | NY | SOL-11007
Catskill | NY | SOL-11021
Eddy Ridge | NY | SOL-11054
Ridgeway #1 | NY | SOL-11018
Rivard 1 | NY | SOL-11011
Rivard 2 | NY | SOL-11012
Ridgeway #2 | NY | SOL-11027
Spencer | NY | SOL-11017
Reisender | NY | SOL-10886
Finney | NY | SOL-10999
Davis Solar | NY | SOL-10958
Genesee | NY | SOL-10951
Landau I | NY | SOL-10891
Landau II | NY | SOL-10895
New Beginnings | NY | SOL-10890
Bullitt Farm Solar, LLC | NY | SOL-10998
Brodhead Solar, LLC | NY | SOL-10899
Svenski | NY | SOL-10894
Bantam | NY | SOL-10986
Bogart | NY | SOL-10887
Dubois | NY | SOL-10892
Salt Point | NY | SOL-10888
Wheatland 2A | NY | SOL-10971
Wheatland 2B | NY | SOL-10961
Brickchurch | NY | SOL-10889
McCarthy Solar | NY | SOL-10992
Costanza | NY | SOL-10907
Lockenhurst Pond | NY | SOL-11000
Drinkwater | NY | SOL-10896
Altamont | NY | SOL-11085
Krumkill North | NY | SOL-11086
Krumkill South | NY | SOL-11087
X092 | NY | SOL-11189
X093 | NY | SOL-10932
X095 | NY | SOL-10929
X181 | NY | SOL-10428
X415 | NY | SOL-10429
K198 | NY | SOL-10930
K203 | NY | SOL-11190
K213 | NY | SOL-11191
K217 | NY | SOL-10933
K307 | NY | SOL-10876
K610 | NY | SOL-11158
M025 | NY | SOL-10392
M028 | NY | SOL-10381
Q030 | NY | SOL-10878
Q130 | NY | SOL-10877
Q196 | NY | SOL-10879
Q220 | NY | SOL-10873
Q205 | NY | SOL-10922
Q400 | NY | SOL-10871
R003 | NY | SOL-10416
R007 | NY | SOL-10417
BK16 | NY | SOL-11093
Trenton - Trenton East | IL | SOL-11060
Trenton - Trenton West | IL | SOL-11061
Dakota - Dakota Solar 1 | IL | SOL-11113
X018 | NY | SOL-10418
Janiak Solar | NY | SOL-10898
County Route 11B | NY | SOL-10983
Barone | NY | SOL-11034
Cedarville | IL | SOL-11069
O'Brien Hill #1 | NY | SOL-11098
O'Brien Hill #2 | NY | SOL-11099
Trinity - Freeport | IL | SOL-11057
Ransom | NY | SOL-11157 |  |  | 0
Horseheads - Wedge | NY | SOL-11160
Otisville - Shoddy Hollow | NY | SOL-11185
Wellsville - Chenunda Creek | NY | SOL-11187
DC: Washington - Essex Condominium | DC | SOL-10036
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149
IL: Viola - Goldenrod - (PW) | IL | SOL-11132
IL: Marengo - Grant - (PW) | IL | SOL-11147
NY: Cambridge - Cambridge (PW) | NY | SOL-11126
NY: Whitesville - Independence North | NY | SOL-11186
IL: Beecher - Cottage Grove North (PW) | IL | SOL-11114
IL: Beecher - Cottage Grove South (PW) | IL | SOL-11115
IL: Harvard - 9618 US HWY 14 (PW) | IL | SOL-11110
IL: Beecher - 701 E Goodenow Rd (PW) | IL | SOL-11112
NY: Stormville - Green Haven - (IRA) | NY | SOL-11151
IL: Hillsboro - Anacott (PW) | IL | SOL-11134
IL: Manhattan - Gougar (PW) | IL
IL: Morrison - Sawyer (PW) | IL
IL: Kankakee - Jeffery (PW) | IL
IL: Freeport - 2240 South 18th Ave (PW) | IL
Note on D89: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Since meter is reporting 0 we have taken total inverter energy as actual energy

## Dec
Generate Capital |  |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
K026 | NY | SOL-10356
K041 | NY | SOL-10357
K043 | NY | SOL-10358
K058 | NY | SOL-10360
K115 | NY | SOL-10361
K152 | NY | SOL-10362
K166 | NY | SOL-10363
K206 | NY | SOL-10927
K251 | NY | SOL-10365
K269 | NY | SOL-10366
K273 | NY | SOL-10367
K287 | NY | SOL-10919
K298 | NY | SOL-10368
K335 | NY | SOL-10370
K345 | NY | SOL-10920
K445 | NY | SOL-10373
K495 | NY | SOL-10374
M020 | NY | SOL-10380
M092 | NY | SOL-10383
M143 | NY | SOL-10384
M144 | NY | SOL-10385
M167 | NY | SOL-10386
M188 | NY | SOL-10387
EMHC | NY | SOL-10351
Q008 | NY | SOL-10397
Q018 | NY | SOL-10398
Q021 | NY | SOL-10399
Q025 | NY | SOL-10400
Q074 | NY | SOL-10402
Q115 | NY | SOL-10872
Q139 | NY | SOL-10403
Q157 | NY | SOL-10404
Q192 | NY | SOL-10406
Q210 | NY | SOL-10407
Q229 | NY | SOL-10408
Q231 | NY | SOL-10870
Q405 | NY | SOL-10409
Q435 | NY | SOL-10923
Q485 | NY | SOL-10869
Q490 | NY | SOL-10411
Q620 | NY | SOL-10867
QMOA | NY | SOL-10415
X024 | NY | SOL-10419
X026 | NY | SOL-10420
X090 | NY | SOL-10925
X117 | NY | SOL-10422
X125 | NY | SOL-10423
X134 | NY | SOL-10424
X135 | NY | SOL-10425
X139 JHS 222 | NY | SOL-10426
X140 | NY | SOL-10926
X166 | NY | SOL-10427
Murphy | MN | SOL-10094
Terning | MN | SOL-10093
Boas Road 04 | NY | SOL-10908
Kelly Bridge Farm | NY | SOL-10911
Pool Brook Road | NY | SOL-10909
Sackett Lake | NY | SOL-10910
Burritt Road | NY | SOL-10913
Villa Roma 1 | NY | SOL-10914
Villa Roma 2 | NY | SOL-10915
Washington 1 | NY | SOL-10912
Washington 3 | NY | SOL-10828
Washington 4 | NY | SOL-10829
Big Tree | NY | SOL-10966
Canoga | NY | SOL-10965
County Route 84 | NY | SOL-10967
Donati | NY | SOL-10968
Henrietta | NY | SOL-10972
NY 70 | NY | SOL-10970
Reid | NY | SOL-10991
Sangolqui | NY | SOL-10975
State Highway 17B | NY | SOL-10988
State Route 14A | NY | SOL-10997
West Creek | NY | SOL-10995
Wildflower | NY | SOL-10982
Glen Mary 1 | NY | SOL-10993
Glen Mary 2 | NY | SOL-10994
Telegraph 1 | NY | SOL-11003
Telegraph 2 | NY | SOL-11004
Cafferty Hill | NY | SOL-10996
Dunkleman | NY | SOL-11008
Route 19 1 | NY | SOL-11001
Route 19 2 | NY | SOL-11002
Yellow Mills 1 | NY | SOL-11006
Yellow Mills 2 | NY | SOL-11005
Yellow Mills 3 | NY | SOL-11007
Catskill | NY | SOL-11021
Eddy Ridge | NY | SOL-11054
Ridgeway #1 | NY | SOL-11018
Rivard 1 | NY | SOL-11011
Rivard 2 | NY | SOL-11012
Ridgeway #2 | NY | SOL-11027
Spencer | NY | SOL-11017
Reisender | NY | SOL-10886
Finney | NY | SOL-10999
Davis Solar | NY | SOL-10958
Genesee | NY | SOL-10951
Landau I | NY | SOL-10891
Landau II | NY | SOL-10895
New Beginnings | NY | SOL-10890
Bullitt Farm Solar, LLC | NY | SOL-10998
Brodhead Solar, LLC | NY | SOL-10899
Svenski | NY | SOL-10894
Bantam | NY | SOL-10986
Bogart | NY | SOL-10887
Dubois | NY | SOL-10892
Salt Point | NY | SOL-10888
Wheatland 2A | NY | SOL-10971
Wheatland 2B | NY | SOL-10961
Brickchurch | NY | SOL-10889
McCarthy Solar | NY | SOL-10992
Costanza | NY | SOL-10907
Lockenhurst Pond | NY | SOL-11000
Drinkwater | NY | SOL-10896
Altamont | NY | SOL-11085
Krumkill North | NY | SOL-11086
Krumkill South | NY | SOL-11087
X092 | NY | SOL-11189
X093 | NY | SOL-10932
X095 | NY | SOL-10929
X181 | NY | SOL-10428
X415 | NY | SOL-10429
K198 | NY | SOL-10930
K203 | NY | SOL-11190
K213 | NY | SOL-11191
K217 | NY | SOL-10933
K307 | NY | SOL-10876
K610 | NY | SOL-11158
M025 | NY | SOL-10392
M028 | NY | SOL-10381
Q030 | NY | SOL-10878
Q130 | NY | SOL-10877
Q196 | NY | SOL-10879
Q220 | NY | SOL-10873
Q205 | NY | SOL-10922
Q400 | NY | SOL-10871
R003 | NY | SOL-10416
R007 | NY | SOL-10417
BK16 | NY | SOL-11093
Trenton - Trenton East | IL | SOL-11060
Trenton - Trenton West | IL | SOL-11061
Dakota - Dakota Solar 1 | IL | SOL-11113
X018 | NY | SOL-10418
Janiak Solar | NY | SOL-10898
County Route 11B | NY | SOL-10983
Barone | NY | SOL-11034
Cedarville | IL | SOL-11069
O'Brien Hill #1 | NY | SOL-11098
O'Brien Hill #2 | NY | SOL-11099
Trinity - Freeport | IL | SOL-11057
Ransom | NY | SOL-11157
Horseheads - Wedge | NY | SOL-11160
Otisville - Shoddy Hollow | NY | SOL-11185
Wellsville - Chenunda Creek | NY | SOL-11187
DC: Washington - Essex Condominium | DC | SOL-10036
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149
IL: Viola - Goldenrod - (PW) | IL | SOL-11132
IL: Marengo - Grant - (PW) | IL | SOL-11147
NY: Cambridge - Cambridge (PW) | NY | SOL-11126
NY: Whitesville - Independence North | NY | SOL-11186
IL: Beecher - Cottage Grove North (PW) | IL | SOL-11114
IL: Beecher - Cottage Grove South (PW) | IL | SOL-11115
IL: Harvard - 9618 US HWY 14 (PW) | IL | SOL-11110
IL: Beecher - 701 E Goodenow Rd (PW) | IL | SOL-11112
NY: Stormville - Green Haven - (IRA) | NY | SOL-11151
IL: Hillsboro - Anacott (PW) | IL | SOL-11134
IL: Manhattan - Gougar (PW) | IL | SOL-11148
IL: Morrison - Sawyer (PW) | IL
IL: Kankakee - Jeffery (PW) | IL
IL: Freeport - 2240 South 18th Ave (PW) | IL
Note on D89: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Since meter is reporting 0 we have taken total inverter energy as actual energy

## Sites
Portfolio: | Generate Capital
Site DAS Name | Site | State | Update | DAS | SOL#
K026 | K026 | NY |  | PowerTrack | SOL-10356
K041 | K041 | NY |  | PowerTrack | SOL-10357
K043 Brooklyn | K043 | NY |  | PowerTrack | SOL-10358
K058 | K058 | NY |  | PowerTrack | SOL-10360
K115 | K115 | NY |  | PowerTrack | SOL-10361
K152 | K152 | NY |  | PowerTrack | SOL-10362
K166 | K166 | NY |  | PowerTrack | SOL-10363
K206 | K206 | NY |  | PowerTrack | SOL-10927
K251 | K251 | NY |  | PowerTrack | SOL-10365
K269 | K269 | NY |  | PowerTrack | SOL-10366
K273 | K273 | NY |  | PowerTrack | SOL-10367
K287 | K287 | NY |  | PowerTrack | SOL-10919
K298 | K298 | NY |  | PowerTrack | SOL-10368
K335 | K335 | NY |  | PowerTrack | SOL-10370
K345 | K345 | NY |  | PowerTrack | SOL-10920
K445 | K445 | NY |  | PowerTrack | SOL-10373
K495 | K495 | NY |  | PowerTrack | SOL-10374
M020 | M020 | NY |  | PowerTrack | SOL-10380
M092 | M092 | NY |  | PowerTrack | SOL-10383
M143 | M143 | NY |  | PowerTrack | SOL-10384
M144 | M144 | NY |  | PowerTrack | SOL-10385
M167 | M167 | NY |  | PowerTrack | SOL-10386
M188 | M188 | NY |  | PowerTrack | SOL-10387
Elmhurst Hospital | EMHC | NY |  | PowerTrack | SOL-10351
Q008 | Q008 | NY |  | PowerTrack | SOL-10397
Q018 | Q018 | NY |  | PowerTrack | SOL-10398
Q021 | Q021 | NY |  | PowerTrack | SOL-10399
Q025 | Q025 | NY |  | PowerTrack | SOL-10400
Q074 | Q074 | NY |  | PowerTrack | SOL-10402
Q115 | Q115 | NY |  | PowerTrack | SOL-10872
Q139 | Q139 | NY |  | PowerTrack | SOL-10403
Q157 | Q157 | NY |  | PowerTrack | SOL-10404
Q192 | Q192 | NY |  | PowerTrack | SOL-10406
Q210 | Q210 | NY |  | PowerTrack | SOL-10407
Q229 | Q229 | NY |  | PowerTrack | SOL-10408
Q231 | Q231 | NY |  | PowerTrack | SOL-10870
Q405 | Q405 | NY |  | PowerTrack | SOL-10409
Q435 | Q435 | NY |  | PowerTrack | SOL-10923
Q485 | Q485 | NY |  | PowerTrack | SOL-10869
Q490 | Q490 | NY |  | PowerTrack | SOL-10411
Q620 | Q620 | NY |  | PowerTrack | SOL-10867
Queens Museum of Art | QMOA | NY |  | PowerTrack | SOL-10415
X024 | X024 | NY |  | PowerTrack | SOL-10419
38 | X026 | NY |  | PowerTrack | SOL-10420
144 | X090 | NY |  | PowerTrack | SOL-10925
279 | X117 | NY |  | PowerTrack | SOL-10422
293 | X125 | NY |  | PowerTrack | SOL-10423
308 | X134 | NY |  | PowerTrack | SOL-10424
309 | X135 | NY |  | PowerTrack | SOL-10425
X-139 JHS 222 | X139 JHS 222 | NY |  | PowerTrack | SOL-10426
X140 | X140 | NY |  | PowerTrack | SOL-10926
358 | X166 | NY |  | PowerTrack | SOL-10427
Murphy (WaveSun) | Murphy | MN |  | PowerTrack | SOL-10094
Terning (MontSun) | Terning | MN |  | PowerTrack | SOL-10093
Boas Road 04 | Boas Road 04 | NY | FA | Green Power Monitor | SOL-10908
Kelly Bridge Farm | Kelly Bridge Farm | NY | FA | Green Power Monitor | SOL-10911
Pool Brook Farm | Pool Brook Road | NY | FA | Green Power Monitor | SOL-10909
Sackett Lake Farm 1 | Sackett Lake | NY | FA | Green Power Monitor | SOL-10910
Burritt Road | Burritt Road | NY | FA | Green Power Monitor | SOL-10913
Villa Roma 1 | Villa Roma 1 | NY | FA | Green Power Monitor | SOL-10914
Villa Roma 2 | Villa Roma 2 | NY | FA | Green Power Monitor | SOL-10915
Washington 1 | Washington 1 | NY | FA | Green Power Monitor | SOL-10912
Washington 3 | Washington 3 | NY | FA | Green Power Monitor | SOL-10828
Washington 4 | Washington 4 | NY | FA | Green Power Monitor | SOL-10829
Big Tree | Big Tree | NY | FA | Green Power Monitor | SOL-10966
Canoga | Canoga | NY | A | Green Power Monitor | SOL-10965
County Route 84 | County Route 84 | NY | FA | Green Power Monitor | SOL-10967
Donati | Donati | NY | FA | Green Power Monitor | SOL-10968
Henrietta | Henrietta | NY | FA | Green Power Monitor | SOL-10972
NY 70 | NY 70 | NY | FA | Green Power Monitor | SOL-10970
Reid (FFP) | Reid | NY |  | PowerTrack | SOL-10991
Sangolqui | Sangolqui | NY | FA | Green Power Monitor | SOL-10975
State Highway 17B | State Highway 17B | NY | A | Green Power Monitor | SOL-10988
State Route 14A | State Route 14A | NY | FA | Green Power Monitor | SOL-10997
West Creek | West Creek | NY | FA | Green Power Monitor | SOL-10995
Wildflower | Wildflower | NY |  | Green Power Monitor | SOL-10982
Glen Mary 1 | Glen Mary 1 | NY | FA | Green Power Monitor | SOL-10993
Glen Mary 2 | Glen Mary 2 | NY | FA | Green Power Monitor | SOL-10994
Telegraph 1 | Telegraph 1 | NY | FA | Green Power Monitor | SOL-11003
Telegraph 2 | Telegraph 2 | NY | FA | Green Power Monitor | SOL-11004
Cafferty Hill | Cafferty Hill | NY | FA | Green Power Monitor | SOL-10996
Dunkleman | Dunkleman | NY | FA | Green Power Monitor | SOL-11008
Route 19 #1 | Route 19 1 | NY | FA | Green Power Monitor | SOL-11001
Route 19 #2 | Route 19 2 | NY | FA | Green Power Monitor | SOL-11002
Yellow Mills 1 | Yellow Mills 1 | NY | FA | Green Power Monitor | SOL-11006
Yellow Mills 2 | Yellow Mills 2 | NY | FA | Green Power Monitor | SOL-11005
Yellow Mills 3 | Yellow Mills 3 | NY | FA | Green Power Monitor | SOL-11007
Catskill | Catskill | NY | FA | Green Power Monitor | SOL-11021
Eddy Ridge | Eddy Ridge | NY | FA | Green Power Monitor | SOL-11054
Ridgeway #1 | Ridgeway #1 | NY |  | Green Power Monitor | SOL-11018
Rivard 1 | Rivard 1 | NY |  | PowerTrack | SOL-11011
Rivard 2 | Rivard 2 | NY |  | PowerTrack | SOL-11012
Ridgeway #1 | Ridgeway #2 | NY |  | Green Power Monitor | SOL-11027
Spencer | Spencer | NY | FA | Green Power Monitor | SOL-11017
Reisender | Reisender | NY | FA | Green Power Monitor | SOL-10886
Finney | Finney | NY | FA | Green Power Monitor | SOL-10999
Davis Solar | Davis Solar | NY |  | Also Energy API | SOL-10958
Genesee | Genesee | NY | FA | Green Power Monitor | SOL-10951
Landau I | Landau I | NY | FA | Green Power Monitor | SOL-10891
Landau II | Landau II | NY |  | Green Power Monitor | SOL-10895
New Beginnings | New Beginnings | NY | FA | Green Power Monitor | SOL-10890
Guilin Farm Solar | Bullitt Farm Solar, LLC | NY |  | PowerTrack | SOL-10998
Brodhead Solar | Brodhead Solar, LLC | NY |  | PowerTrack | SOL-10899
Svenski | Svenski | NY | FA | Green Power Monitor | SOL-10894
Bantam | Bantam | NY | FA | Green Power Monitor | SOL-10986
Bogart | Bogart | NY | FA | Green Power Monitor | SOL-10887
Dubois | Dubois | NY | F | Green Power Monitor | SOL-10892
Salt Point | Salt Point | NY | FA | Green Power Monitor | SOL-10888
Wheatland 2A | Wheatland 2A | NY | FA | Green Power Monitor | SOL-10971
Wheatland 2B | Wheatland 2B | NY | FA | Green Power Monitor | SOL-10961
Brickchurch | Brickchurch | NY | FA | Green Power Monitor | SOL-10889
McCarthy Solar | McCarthy Solar | NY |  | Green Power Monitor | SOL-10992
Costanza | Costanza | NY | FA | Green Power Monitor | SOL-10907
Lockenhurst Pond | Lockenhurst Pond | NY |  | PowerTrack | SOL-11000
Drinkwater | Drinkwater | NY | FA | Green Power Monitor | SOL-10896
Altamont | Altamont | NY |  | PowerTrack | SOL-11085
Krumkill North | Krumkill North | NY |  | PowerTrack | SOL-11086
Krumkill South | Krumkill South | NY |  | PowerTrack | SOL-11087
X092 | X092 | NY |  | PowerTrack | SOL-11189
X093 | X093 | NY |  | PowerTrack | SOL-10932
X095 | X095 | NY |  | PowerTrack | SOL-10929
X181 | X181 | NY |  | PowerTrack | SOL-10428
X415 | X415 | NY |  | PowerTrack | SOL-10429
K198 | K198 | NY |  | PowerTrack | SOL-10930
K203 | K203 | NY |  | PowerTrack | SOL-11190
K213 | K213 | NY |  | PowerTrack | SOL-11191
K217 | K217 | NY |  | PowerTrack | SOL-10933
K307 | K307 | NY |  | PowerTrack | SOL-10876
K610 | K610 | NY |  | PowerTrack | SOL-11158
M025 | M025 | NY |  | PowerTrack | SOL-10392
M028 | M028 | NY |  | PowerTrack | SOL-10381
Q030 | Q030 | NY |  | PowerTrack | SOL-10878
Q130 | Q130 | NY |  | PowerTrack | SOL-10877
Q196 | Q196 | NY |  | PowerTrack | SOL-10879
Q220 | Q220 | NY |  | PowerTrack | SOL-10873
Q205 | Q205 | NY |  | PowerTrack | SOL-10922
Q400 | Q400 | NY |  | PowerTrack | SOL-10871
R003 | R003 | NY |  | PowerTrack | SOL-10416
R007 | R007 | NY |  | PowerTrack | SOL-10417
BK16 | BK16 | NY |  | PowerTrack | SOL-11093
Trenton East | Trenton - Trenton East | IL |  | PowerTrack | SOL-11060
Trenton West | Trenton - Trenton West | IL |  | PowerTrack | SOL-11061
6274 N Dakota Rd - Stephenson | Dakota - Dakota Solar 1 | IL |  | PowerTrack | SOL-11113
X018 | X018 | NY |  | PowerTrack | SOL-10418
Janiak Solar | Janiak Solar | NY |  | PowerTrack | SOL-10898
County Route 11B | County Route 11B | NY | FA | Green Power Monitor | SOL-10983
Barone | Barone | NY | FA | Green Power Monitor | SOL-11034
Cedarville | Cedarville | IL |  | PowerTrack | SOL-11069
O'Brien Hill #1 | O'Brien Hill #1 | NY |  | Green Power Monitor | SOL-11098
O'Brien Hill #2 | O'Brien Hill #2 | NY |  | Green Power Monitor | SOL-11099
Trinity Freeport | Trinity - Freeport | IL |  | PowerTrack | SOL-11057
Binghamton - Ransom | Ransom | NY |  | Green Power Monitor | SOL-11157
Wedge | Horseheads - Wedge | NY | FA | Green Power Monitor | SOL-11160
hoddy Hollow | Otisville - Shoddy Hollow | NY |  | Green Power Monitor | SOL-11185
Chenunda Creek | Wellsville - Chenunda Creek | NY | FA | Green Power Monitor | SOL-11187
The Essex - DC | DC: Washington - Essex Condominium | DC |  | PowerTrack | SOL-10036
Leoku | HI: Waipahu - 94-246 Leoku St - E.F.G. | HI |  | PowerTrack | SOL-10071
Waipahu | HI: Waipahu - 94-099 Waipahu St - PV | HI |  | PowerTrack | SOL-10068
Yager Road Whiteside Solar 1, LLC | IL: Prophetstown - 5170 Yager Road (PW) | IL |  | PowerTrack | SOL-11149
Goldenrod Solar Project, LLC | IL: Viola - Goldenrod - (PW) | IL |  | PowerTrack | SOL-11132
Grant Highway Solar 1, LLC | IL: Marengo - Grant - (PW) | IL |  | PowerTrack | SOL-11147
Cambridge - Cambridge (PW) | NY: Cambridge - Cambridge (PW) | NY |  | PowerTrack | SOL-11126
Whitesville - Independence North | NY: Whitesville - Independence North | NY |  | Green Power Monitor | SOL-11186
S Cottage Grove Ave - North | IL: Beecher - Cottage Grove North (PW) | IL |  | PowerTrack | SOL-11114
S Cottage Grove Ave - South | IL: Beecher - Cottage Grove South (PW) | IL |  | PowerTrack | SOL-11115
9521 US 14 - McHenry | IL: Harvard - 9618 US HWY 14 (PW) | IL |  | PowerTrack | SOL-11110
Goodenow West | IL: Beecher - 701 E Goodenow Rd (PW) | IL |  | PowerTrack | SOL-11112
NY: Stormville - Green Haven - (IRA) | NY: Stormville - Green Haven - (IRA) | NY |  | Power factors | SOL-11151
Anacott Solar, LLC | IL: Hillsboro - Anacott (PW) | IL |  | PowerTrack | SOL-11134
Gougar Road Solar 1, LLC | IL: Manhattan - Gougar (PW) | IL |  | PowerTrack | SOL-11148
SAWYER ROAD | IL: Morrison - Sawyer (PW) | IL |  | PowerTrack | SOL-11176
JEFFERY ROAD | IL: Kankakee - Jeffery (PW) | IL |  | PowerTrack | SOL-11173
Freeport | IL: Freeport - 2240 South 18th Ave (PW) | IL |  | PowerTrack | SOL-11084