## Year to Date
Accel International |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 538320.178 | 0 | 538320.178 | 0% | 712845.159 | -174524.981 | -24.48%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
CT: Meriden - Accel International | CT | 538320.178 | 0 | 538320.178 |  | 712845.159 | -167746.526 | -23.53%

## 1st Qtr
Accel International |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 138287.24 | 0 | 138287.24 | 0% | 143182.347 | -4895.107 | -3.419%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
CT: Meriden - Accel International | CT | 138287.24 | 0 | 138287.24 |  | 143182.347 | 1883.348 | 1.315%

## 2nd Qtr
Accel International |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 201933.929 | 0 | 201933.929 | 0% | 271830 | -69896.071 | -25.71%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
CT: Meriden - Accel International | CT | 201933.929 | 0 | 201933.929 |  | 271830 | -69896.071 | -25.71%

## 3rd Qtr
Accel International |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 88454.609 | 0 | 88454.609 | 0% | 187969.195 | -99514.586 | -52.94%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
CT: Meriden - Accel International | CT | 88454.609 | 0 | 88454.609 |  | 187969.195 | -99514.586 | -52.94%

## 4th Qtr
Accel International |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 109644.4 | 0 | 109644.4 | 0% | 109863.617 | -219.217 | -0.1995%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
CT: Meriden - Accel International | CT | 109644.4 | 0 | 109644.4 |  | 109863.617 | -219.217 | -0.1995%

## Jan
Accel International |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 32483.76 | 0 | 32483.76 | 0% | 34863.274 | -2379.514 | -6.825%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Meriden - Accel International | CT | 32483.76 | 0 | 32483.76 |  | 34863.274 |  | 0% | 1.Inverter 14 was being RMA'D since 06/10/24. On 01/29/25 technician replaced dc relay board and fan the inverter back online at 11:15 and producing in line with its peers. 2.Inverter 9 was being RMA'D since 09/23/24. On 01/29/25 technician replaced dc relay board and fan the inverter back online at 11:15 and producing in line with its peers. | 1.SR085759 2.SR091076

## Feb
Accel International |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 39758.94 | 0 | 39758.94 | 0% | 44157.881 | -4398.941 | -9.962%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Meriden - Accel International | CT | 39758.94 | 0 | 39758.94 |  | 44157.881 |  | 0% | 1.Inverter 1 tripped offline from 02/13 at 10AM due to 03x9B/Error in SolarEdge and offline through out the month. On 02/19 technician checked-in and RMA'D failed DC relay board. | 1.SR096986

## Mar
Accel International |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 66044.54 | 0 | 66044.54 | 0% | 64161.192 | 1883.348 | 2.935%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Meriden - Accel International | CT | 66044.54 | 0 | 66044.54 |  | 64161.192 | 1883.348 | 2.935% | 1.Inverter 1 tripped offline from 02/13 at 10AM due to 03x9B/Error in SolarEdge and offline through out the month. On 03/14 technician checked in and RMA'D the inverter. | 1.SR096986

## Apr
Accel International |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 71619.029 | 0 | 71619.029 | 0% | 81675 | -10055.971 | -12.31%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Meriden - Accel International | CT | 71619.029 | N/A |  |  | 81675 | -10055.971 | -12.31% | 1.Inverter 1 tripped offline from 02/13 at 10:00. and came back online after being replaced on 04/16. Inverter 1 was offline from 11:00 on 04/17 | 1. SR096986, SR099952 | SR099952

## May
Accel International |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 63253.06 | 0 | 63253.06 | 0% | 91905 | -28651.94 | -31.18%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Meriden - Accel International | CT | 63253.06 | N/A |  |  | 91905 | -28651.94 | -31.18% | 1.Inverter 1 has been offline since 04/17 2. Inverter 7 is underperforming by approximately 15 kW at peak production. String 7.2 is down by about 9–10 kW, while strings 7.1 and 7.3 are each down by approximately 2–3 kW. On June 11, a technician RMA'd three optimizers—two from string 7.2 and one from string 7.3. The remaining underperformance is attributed to overgrown foliage. | 1. SR099952 2. SR102634 | SR102634

## Jun
Accel International |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 67061.84 | 0 | 67061.84 | 0% | 98250 | -31188.16 | -31.74%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Meriden - Accel International | CT | 67061.84 | N/A |  |  | 98250 | -31188.16 | -31.74% | 1.Inverter 1 has been offline since 04/17. 2. Inverter 7 is underperforming by approximately 15 kW at peak production. String 7.2 is down by about 9–10 kW, while strings 7.1 and 7.3 are each down by approximately 2–3 kW. On June 11, a technician RMA'd three optimizers—two from string 7.2 and one from string 7.3. The remaining underperformance is attributed to overgrown foliage. | 1.SR099952 2.SR102634 | SR102634

## Jul
Accel International |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 70870.1 | 0 | 70870.1 | 0% | 91857.41 | -20987.31 | -22.85%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Meriden - Accel International | CT | 70870.1 | N/A |  |  | 91857.41 | -20987.31 | -22.85% | 1.Inverter 1 has been offline since 04/17. 2. Inverter 7 is underperforming by approximately 15 kW at peak production. String 7.2 is down by about 9–10 kW, while strings 7.1 and 7.3 are each down by approximately 2–3 kW. On June 11, a technician RMA'd three optimizers—two from string 7.2 and one from string 7.3. The remaining underperformance is attributed to overgrown foliage. | 1.SR099952 2.SR102634 | SR102634

## Aug
Accel International |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 11792.64 | 0 | 11792.64 | 0% | 81965.445 | -70172.805 | -85.61%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Meriden - Accel International | CT | 11792.64 | N/A |  |  | 81965.445 | -70172.805 | -85.61% | 1.Inverter 1 has been offline since 04/17. 2. Inverter 7 is underperforming by approximately 15 kW at peak production. String 7.2 is down by about 9–10 kW, while strings 7.1 and 7.3 are each down by approximately 2–3 kW. On June 11, a technician RMA'd three optimizers—two from string 7.2 and one from string 7.3. The remaining underperformance is attributed to overgrown foliage. 3. Site was intentionally kept offline from 08:45am on 08/06 due to vegetation maintenance till end of the month. | 1.SR099952 2.SR102634 3.SR105647 | SR102634 | SR105647

## Sep
Accel International |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 5791.869 | 0 | 5791.869 | 0% | 14146.34 | -8354.471 | -59.06%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Meriden - Accel International | CT | 5791.869 | 0 | 5791.869 |  | 14146.34 | -8354.471 | -59.06% | 1. Site was offline for whole month. | 1.SR105647

## Oct
Accel International |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 47681.77 | 0 | 47681.77 | 0% | 50235 | -2553.23 | -5.083%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
CT: Meriden - Accel International | CT | 47681.77 | 0 | 47681.77 |  | 50235 | -2553.23 | -5.083% | 1. Inverter 1 was RMAd. 2. Inverter 10 was offline from 10:00 on 10/16 to 13:00 on 10/17 and 1 string was isolated from 10/17 at 13:00 to end of the month. | 1. SR099952 2. SR109574 | 1. Pending 2 closed | SR109574

## Nov
Accel International |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 36297.9 | 0 | 36297.9 | 0% | 31455 | 4842.9 | 15.4%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
CT: Meriden - Accel International | CT | 36297.9 | 0 | 36297.9 |  | 31455 | 4842.9 | 15.4% | 1. Inverter 1 was RMAd. 2. Inverter 10 1 string was isolated from 10/17 at 13:00 to end of the month. 3. Inverter 6 started late at 09:30 on 11/04. 4. Inverter 11 was offline from 10:00 on 11/09 to 13:45 on 11/13. | 1. SR099952 2. SR109574 3. SR110593 4. SR110994 | 1. Pending 2 closed 3. Closed 4. closed | SR109574 | SR110593 | SR110994

## Dec
Accel International |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 25664.73 | 0 | 25664.73 | 0% | 28173.617 | -2508.887 | -8.905%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
CT: Meriden - Accel International | CT | 25664.73 | N/A |  |  | 28173.617 | -2508.887 | -8.905% | 1. Inverter 1 was RMA'd. | 1. SR099952 | 1. Pending

## Sites
Portfolio: | Accel International
Site DAS Name | Site | State | Update | DAS
Accel International | CT: Meriden - Accel International | CT | AF | PowerTrack