## Year to Date
Canton Ice House |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 514210.488 | 0 | 514210.488 | 0% | 0 | 514210.488 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Canton - Canton Ice House | MA | 514210.488 | 0 | 514210.488 |  | 0 | 159909.809

## 1st Qtr
Canton Ice House |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 82843.461 | 0 | 82843.461 | 0% | 0 | 82843.461 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Canton - Canton Ice House | MA | 82843.461 | 0 | 82843.461 |  | 0 | 0

## 2nd Qtr
Canton Ice House |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 159909.809 | 0 | 159909.809 | 0% | 0 | 159909.809 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Canton - Canton Ice House | MA | 159909.809 | 0 | 159909.809 |  | 0 | 159909.809

## 3rd Qtr
Canton Ice House |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 187621.379 | 0 | 187621.379 | 0% | 0 | 187621.379 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Canton - Canton Ice House | MA | 187621.379 | 0 | 187621.379 |  | 0 | 0

## 4th Qtr
Canton Ice House |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 83835.839 | 0 | 83835.839 | 0% | 0 | 83835.839 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Canton - Canton Ice House | MA | 83835.839 | 0 | 83835.839 |  | 0 | 0

## Jan
Canton Ice House |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 18838.55 | 0 | 18838.55 | 0% | 0 | 18838.55 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Canton - Canton Ice House | MA | 18838.55 | N/A |  |  | N/A |  |  | 1.Inverter 8 was being RMA'D since 12/17/24. | 1.SR093239

## Feb
Canton Ice House |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 18144.561 | 0 | 18144.561 | 0% | 0 | 18144.561 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Canton - Canton Ice House | MA | 18144.561 | N/A |  |  | N/A |  |  | 1. The site experienced a brief outage from 9:00 AM to 11:30 AM on 02/14. However, inverters 2, 6, 7, and 13 remained offline after the site came back online. Inverters 6 and 13 self-resolved on 02/15. On 02/18, a technician found that inverter 2 was still offline and is being RMA’d, while inverter 7 was also offline, with its DC relay board being RMA’d. 2. Inverter 8 was being RMA'D since 12/17/24. | 1.SR097109 2.SR093239 | SR093239

## Mar
Canton Ice House |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 45860.35 | 0 | 45860.35 | 0% | 0 | 45860.35 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Canton - Canton Ice House | MA | 45860.35 | N/A |  |  | N/A |  |  | 1. Inverter 2 tripped offline at 16:30 on 02/13 and is being RMA’d. After troubleshooting by the technician, the inverter was brought back online at 17:30 on 03/05.Additionally, Inverter 7 tripped offline at 16:15 on 02/13, with its DC relay board being RMA’d. 2. Inverter 1 is derating due to multiple tripping events for whole month. 3. Inverter 8 was being RMA'D since 12/17/24. | 1. SR097109, SR098499 2. SR089210 3. SR093239 | SR098499 | SR089210 | SR093239

## Apr
Canton Ice House |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 54979.099 | 0 | 54979.099 | 0% | 0 | 54979.099 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Canton - Canton Ice House | MA | 54979.099 | 0 | 54979.099 |  | 0 | 54979.099 |  | 1. Inverter 8 was being RMA'D since 12/17/24. 2. Inverter 7 tripped offline at 16:15 on 02/13, and its DC relay board is being RMA’d. 3. Inverter 1 is derating due to multiple tripping events for whole month. | 1. SR093239 2. SR098499 3. SR098210 | SR098499 | SR098210

## May
Canton Ice House |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 49649.05 | 0 | 49649.05 | 0% | 0 | 49649.05 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Canton - Canton Ice House | MA | 49649.05 | 0 | 49649.05 |  | 0 | 49649.05 |  | 1. Inverter 8 was being RMA'D since 12/17/24. 2. Inverter 7 tripped offline at 16:15 on 02/13, and its DC relay board is being RMA’d. 3. Inverter 1 is derating due to multiple tripping events for whole month. 4. Inverter 13 tripped offline at 13:45 on 05/02 due to a "Fault". A technician was on site on 05/08 to troubleshoot the inverter, and it was back online at 09:30 on the same day. 5. The left string of Inverter 13 was found disconnected at 09:30 on 05/08 when the technician was on site to troubleshoot the inverter. A return visit was scheduled, as two technicians are needed to lift/move the panels. 6. Inverter 13 tripped offline at 13:45 on 05/02 due to a "Fault", and during troubleshooting on 05/08, the technician found the left string disconnected at 09:30, the inverter was brought back online the same day, but a return visit was scheduled as two technicians are required to lift/move the panels. | 1. SR093239 2. SR098499 3. SR098210 4. SR100935 5. SR101224 6. SR101650 | SR098499 | SR098210 | SR100935 | SR101224 | SR101650

## Jun
Canton Ice House |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 55281.66 | 0 | 55281.66 | 0% | 0 | 55281.66 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Canton - Canton Ice House | MA | 55281.66 | 0 | 55281.66 |  | 0 | 55281.66 |  | 1. Inverter 8 was being RMA'D since 12/17/24. 2. Inverter 9 is offline from 06/06/25 and reporting "Fault" and is being RMA'd 3.The left string of Inverter 13 was found disconnected at 09:30 on 05/08 when the technician was on site to troubleshoot the inverter. A return visit was scheduled, as two technicians are needed to lift/move the panels. 4. Inverter 1 is offline at 10:30 on 04/29. Technician has replaced the Relay Board later the inverter is back online at 11:00 on 06/13 5. Inverter 7 tripped offline at 16:15 on 02/13, and its DC relay board is being RMA’d. | 1. SR093239 2. SR102615 3. SR101224 4. SR089210 5. SR098499 | SR102615 | SR101224 | SR089210 | SR098499

## Jul
Canton Ice House |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 63923.789 | 0 | 63923.789 | 0% | 0 | 63923.789 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Canton - Canton Ice House | MA | 63923.789 | N/A |  |  | N/A |  |  | 1. Inverter 8 was being RMA'D since 12/17/24. 2. Inverter 9 is offline from 06/06/25 and reporting "Fault" and is being RMA'd. Inverter came back online at 11:15 on 07/22 3. Inverter 7 tripped offline at 16:15 on 02/13, and its DC relay board is being RMA’d. inverter came back online at 13:00 on 07/22 4.Inverter 13 started late for production at 11:15 on 07/11 5.Inverters 6 , 4 are started late for production at 16:15 and 12:15 on 07/10 6. Inverter 1 and 13 were derating and DC relay board being RMA'd. | 1. SR093239 2. SR102615 3. SR101650 4. SR104271 6. SR089210 | SR102615 | SR101650 | SR104271 | SR089210

## Aug
Canton Ice House |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 71365.73 | 0 | 71365.73 | 0% | 0 | 71365.73 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Canton - Canton Ice House | MA | 71365.73 | N/A |  |  | N/A |  |  | 1. Inverter 8 was offline for whole month. 2. Inverter 13 was underproduced by 10kW compared to peers for whole month. 3. Inverter 1 was derated by 15 kW compared to peers for whole month. 3. Site was offline from 19:00 on 08/14 to 07:00 on 08/15. | 1. SR093239, SR098499 2. SR101650 3. SR089210 4. SR106324 | SR098499 | SR101650 | SR089210 | SR106324

## Sep
Canton Ice House |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 52331.86 | 0 | 52331.86 | 0% | 0 | 52331.86 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Canton - Canton Ice House | MA | 52331.86 | N/A |  |  | N/A |  |  | 1. Inverter 8 was offline for whole month. 2. Inverter 13 was underproduced by 10kW compared to peers for whole month. 3. Inverter 1 was derated by 15 kW compared to peers for whole month. | 1. SR093239, SR098499 2. SR101650 3. SR089210

## Oct
Canton Ice House |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 35866.439 | 0 | 35866.439 | 0% | 0 | 35866.439 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
MA: Canton - Canton Ice House | MA | 35866.439 | N/A |  |  | N/A |  |  | 1. Inverter 8 was offline for whole month. 2.Inverter 13 was underproduced by 10kW compared to peers for whole month. 3.Inverter 1 was on 10/01 and later back online at 10/15 at 14:45. 4. Inverter 1 was underproducing by 11kW due to one string down from 14:45 on 10/15 to end of the month and There are 12 broken modules on site across the arrays that need to be jumped out or replaced | 1.SR098499, SR093239 2.SR101224, SR101650 3.SR108811 4. PM10031 | 1.Pending 2.Pending 3.Closed | SR093239 | SR101224 | SR101650 | SR108811

## Nov
Canton Ice House |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 23984.7 | 0 | 23984.7 | 0% | 0 | 23984.7 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
MA: Canton - Canton Ice House | MA | 23984.7 | N/A |  |  | N/A |  |  | 1. Inverter 8 was offline for whole month. 2.Inverter 13 was underproduced by 10kW compared to peers for whole month. 3.Inverter 1 was underproducing by 11kW due to one string down from 14:45 on 10/15 to end of the month and There are 12 broken modules on site across the arrays that need to be jumped out or replaced | 1.SR098499 2.SR101650 3.PM10031 | 1.Pending 2.Pending 3.Completed | SR101650

## Dec
Canton Ice House |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 23984.7 | 0 | 23984.7 | 0% | 0 | 23984.7 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
MA: Canton - Canton Ice House | MA | 23984.7 | N/A |  |  | N/A |  |  | 1. Inverter 8 was offline for whole month. 2.Inverter 13 was underproduced by 10kW compared to peers for whole month. 3.Inverter 1 was underproducing by 11kW due to one string down from 14:45 on 10/15 to end of the month and There are 12 broken modules on site across the arrays that need to be jumped out or replaced 4. Site was offline at 12:00 to 12:45 on 12/19. | 1.SR098499 2.SR101650 3.PM10031 4. SR113210 | 1.Pending 2.Pending 3.Completed 4. Closed | SR101650 | SR113210

## Sites
Portfolio: | Canton Ice House
Site DAS Name | Site | State | Update | DAS
Canton Ice House | MA: Canton - Canton Ice House | MA | AF | PowerTrack