## Year to Date
Crawford Realty |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 649649.5299 | 0 | 649649.5299 | 0% | 788302.222 | -138652.6921 | -17.59%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Leominster - Crawford Realty | MA | 649649.5299 | 0 | 649649.5299 |  | 788302.222 | -138652.6921 | -17.59%

## 1st Qtr
Crawford Realty |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 89024.2499 | 0 | 89024.2499 | 0% | 158659.02 | -69634.7701 | -43.89%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Leominster - Crawford Realty | MA | 89024.2499 | 0 | 89024.2499 |  | 158659.02 | -69634.7701 | -43.89%

## 2nd Qtr
Crawford Realty |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 220037.87 | 0 | 220037.87 | 0% | 260899 | -40861.13 | -15.66%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Leominster - Crawford Realty | MA | 220037.87 | 0 | 220037.87 |  | 260899 | -40861.13 | -15.66%

## 3rd Qtr
Crawford Realty |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 232106.87 | 0 | 232106.87 | 0% | 239207.915 | -7101.045 | -2.969%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Leominster - Crawford Realty | MA | 232106.87 | 0 | 232106.87 |  | 239207.915 | -7101.045 | -2.969%

## 4th Qtr
Crawford Realty |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 108480.54 | 0 | 108480.54 | 0% | 129536.287 | -21055.747 | -16.25%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Leominster - Crawford Realty | MA | 108480.54 | 0 | 108480.54 |  | 129536.287 | -21055.747 | -16.25%

## Jan
Crawford Realty |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 22114.98 | 0 | 22114.98 | 0% | 41708.07 | -19593.09 | -46.98%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA | 22114.98 | N/A |  |  | 41708.07 | -19593.09 | -46.98% | 1. Inverter 4 stopped communicating at 10:36 AM on 08/16/24 in SolarEdge, currently production cannot be confirmed as the Site expired in AlsoEnergy. The inverter was replaced on 10/18/24. But still not communicating. 2. Low generation due to weather/snow. | 1. SR098937

## Feb
Crawford Realty |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 6301.1099 | 0 | 6301.1099 | 0% | 49081.57 | -42780.4601 | -87.16%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA | 6301.1099 | N/A |  |  | 49081.57 | -42780.4601 | -87.16% | 1. Inverter 4 stopped communicating at 10:36 AM on 08/16/24 in SolarEdge, currently production cannot be confirmed as the Site expired in AlsoEnergy. The inverter was replaced on 10/18/24. But still not communicating. 2. Low generation due to weather/snow. | 1. SR098937

## Mar
Crawford Realty |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 60608.16 | 0 | 60608.16 | 0% | 67869.38 | -7261.22 | -10.7%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA | 60608.16 | N/A |  |  | 67869.38 | -7261.22 | -10.7% | 1. Inverter 4 stopped communicating at 10:36 AM on 08/16/24 in SolarEdge, currently production cannot be confirmed as the Site expired in AlsoEnergy. The inverter was replaced on 10/18/24. But communication issue still persist, on 03/26 technician updated serial number and inverter comms were restored. 2. Inverter 3 central unit went offline on 03/25 due to an isolation fault. A technician found no visible damage but, after troubleshooting and consulting with Solaredge, suspected that recent heavy rains may have caused water intrusion in one or more MC4 connectors, leading to the fault. Central unit started for production on 03/26. | 1. SR098937 2. SR098962 | SR098962

## Apr
Crawford Realty |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 73678.55 | 0 | 73678.55 | 0% | 80569 | -6890.45 | -8.552%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA | 73678.55 | 0 | 73678.55 |  | 80569 | -6890.45 | -8.552%

## May
Crawford Realty |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 68037.11 | 0 | 68037.11 | 0% | 90274 | -22236.89 | -24.63%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA | 68037.11 | 0 | 68037.11 |  | 90274 | -22236.89 | -24.63% | 1. Inverter 3 left unit tripped at 14:00 on 05/03 and reporting "3 Phase Possible Arc Detection" and the relay board is being RMA'd | 1. SR100977

## Jun
Crawford Realty |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 78322.21 | 0 | 78322.21 | 0% | 90056 | -11733.79 | -13.03%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA | 78322.21 |  |  |  | 90056 | -11733.79 | -13.03% | 1. Inverter 3 left unit tripped at 14:00 on 05/03 and reporting "3 Phase Possible Arc Detection" and the relay board is being RMA'd. and it is offline for whole month | 1. SR100977

## Jul
Crawford Realty |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 84086.22 | 0 | 84086.22 | 0% | 88536.77 | -4450.55 | -5.027%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA | 84086.22 | N/A |  |  | 88536.77 | -4450.55 | -5.027% | 1.Inverter 3 left unit tripped at 14:00 on 05/03 | 1.SR100977

## Aug
Crawford Realty |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 83190.8899 | 0 | 83190.8899 | 0% | 83643.71 | -452.8201 | -0.5414%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA | 83190.8899 | N/A |  |  | 83643.71 | -452.8201 | -0.5414% | 1.Inverter 3 left unit tripped at 14:00 on 05/03 | 1.SR100977

## Sep
Crawford Realty |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 64829.76 | 0 | 64829.76 | 0% | 67027.435 | -2197.675 | -3.279%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA | 64829.76 | N/A |  |  | 67027.435 | -2197.675 | -3.279% | 1. Inverter 3 left unit tripped offline at 14:00 on 05/03, reporting '3 Phase Possible Arc Detection,' and remained offline throughout the month. | 1. SR100977

## Oct
Crawford Realty |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 49182.1 | 0 | 49182.1 | 0% | 52826 | -3643.9 | -6.898%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
MA: Leominster - Crawford Realty | MA | 49182.1 | 0 | 49182.1 |  | 52826 | -3643.9 | -6.898% | 1. Inverter 3 left unit tripped offline at 14:00 on 05/03, reporting '3 Phase Possible Arc Detection,' and remained offline throughout the month. | 1. SR100977 | 1.Pending

## Nov
Crawford Realty |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 29649.2 | 0 | 29649.2 | 0% | 38828 | -9178.8 | -23.64%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
MA: Leominster - Crawford Realty | MA | 29649.2 | 0 | 29649.2 |  | 38828 | -9178.8 | -23.64% | 1. Inverter 3 left unit tripped offline at 14:00 on 05/03, reporting '3 Phase Possible Arc Detection,' and remained offline throughout the month. | 1. SR100977 | 1.Pending

## Dec
Crawford Realty |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 29649.24 | 0 | 29649.24 | 0% | 37882.287 | -8233.047 | -21.73%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Closed
MA: Leominster - Crawford Realty | MA | 29649.24 | 0 | 29649.24 |  | 37882.287 | -8233.047 | -21.73% | 1. Inverter 3 left unit tripped offline at 14:00 on 05/03, reporting '3 Phase Possible Arc Detection,' and remained offline throughout the month. Solaredge is RMA'ing the relay board for the left unit. | 1.SR100977 | 1.closed

## Sites
Portfolio: | Crawford Realty
Site DAS Name | Site | State | Update | DAS
101 Crawford | MA: Leominster - Crawford Realty | MA | AF | PowerTrack