## Year to Date
KPCA Investment, LLC |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 2944309.769 | 3101311.224 | -157001.455 | -5.062% | 3312855.899 | -368546.13 | -11.12%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Chino - 3750-3770 Grand Ave | CA | 175089.0858 | 152820.62 | 22268.4658 | 14.57% | 226748 | -51658.9142 | -22.78%
Murrieta - 28150 Keller Rd | CA | 512072 | 516182.31 | -4110.31 | -0.7963% | 579636.8 | 0 | 0%
La Habra - 601 E Imperial Way | CA | 105627.63 | 83409.283 | 22218.347 | 26.64% | 119494.38 | -13866.75 | -11.6%
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 587326.6308 | 607649.7 | -20323.0692 | -3.345% | 637667.489 | 0 | 0%
Irwindale - 12761 Schabarum Ave | CA | 141563.87 | 114166.253 | 27397.617 | 24% | 166536.73 | -24972.86 | -15%
Santa Rosa - 2240 Mercury Way | CA | 485404.5523 | 532925.48 | -47520.9277 | -8.917% | 549276 | 0 | 0%
Dublin - 3100 Dublin Blvd | CA | 937226 | 1094157.578 | -156931.578 | -14.34% | 1033496.5 | -96270.5 | -9.315%

## 1st Qtr
KPCA Investment, LLC |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Chino - 3750-3770 Grand Ave | CA | 0 | 0 | 0 |  | 0 | 0
Murrieta - 28150 Keller Rd | CA | 0 | 0 | 0 |  | 0 | 0
La Habra - 601 E Imperial Way | CA | 0 | 0 | 0 |  | 0 | 0
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 0 | 0 | 0 |  | 0 | 0
Irwindale - 12761 Schabarum Ave | CA | 0 | 0 | 0 |  | 0 | 0
Santa Rosa - 2240 Mercury Way | CA | 0 | 0 | 0 |  | 0 | 0
Dublin - 3100 Dublin Blvd | CA | 0 | 0 | 0 |  | 0 | 0

## 2nd Qtr
KPCA Investment, LLC |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 1771758.0585 | 1834976.275 | -63218.2165 | -3.445% | 1939577.029 | -167818.9705 | -8.652%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Chino - 3750-3770 Grand Ave | CA | 105148.9374 | 88704.65 | 16444.2874 | 18.54% | 132650 | -27501.0626 | -20.73%
Murrieta - 28150 Keller Rd | CA | 301660 | 301975.25 | -315.25 | -0.1044% | 338989.4 | -37329.4 | -11.01%
La Habra - 601 E Imperial Way | CA | 60220.63 | 48057.75 | 12162.88 | 25.31% | 67344.57 | -7123.94 | -10.58%
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 357011.5841 | 364194.09 | -7182.5059 | -1.972% | 372880.589 | -15869.0049 | -4.256%
Irwindale - 12761 Schabarum Ave | CA | 84093.87 | 65700.18 | 18393.69 | 28% | 95470.97 | -11377.1 | -11.92%
Santa Rosa - 2240 Mercury Way | CA | 294721.0371 | 315356.7 | -20635.6629 | -6.544% | 324424 | -29702.9629 | -9.156%
Dublin - 3100 Dublin Blvd | CA | 568902 | 650987.655 | -82085.655 | -12.61% | 607817.5 | -38915.5 | -6.402%

## 3rd Qtr
KPCA Investment, LLC |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 1172551.7104 | 1266334.949 | -93783.2386 | -7.406% | 1373278.87 | -200727.1596 | -14.62%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Chino - 3750-3770 Grand Ave | CA | 69940.1485 | 64115.97 | 5824.1785 | 9.084% | 94098 | -24157.8515 | -25.67%
Murrieta - 28150 Keller Rd | CA | 210412 | 214207.06 | -3795.06 | -1.772% | 240647.4 | -30235.4 | -12.56%
La Habra - 601 E Imperial Way | CA | 45407 | 35351.533 | 10055.467 | 28.44% | 52149.81 | -6742.81 | -12.93%
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 230315.0468 | 243455.61 | -13140.5632 | -5.398% | 264786.9 | -34471.8532 | -13.02%
Irwindale - 12761 Schabarum Ave | CA | 57470 | 48466.073 | 9003.927 | 18.58% | 71065.76 | -13595.76 | -19.13%
Santa Rosa - 2240 Mercury Way | CA | 190683.5152 | 217568.78 | -26885.2648 | -12.36% | 224852 | -34168.4848 | -15.2%
Dublin - 3100 Dublin Blvd | CA | 368324 | 443169.923 | -74845.923 | -16.89% | 425679 | -57355 | -13.47%

## 4th Qtr
KPCA Investment, LLC |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Chino - 3750-3770 Grand Ave | CA | 0 | 0 | 0 |  | 0 | 0
Murrieta - 28150 Keller Rd | CA | 0 | 0 | 0 |  | 0 | 0
La Habra - 601 E Imperial Way | CA | 0 | 0 | 0 |  | 0 | 0
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 0 | 0 | 0 |  | 0 | 0
Irwindale - 12761 Schabarum Ave | CA | 0 | 0 | 0 |  | 0 | 0
Santa Rosa - 2240 Mercury Way | CA | 0 | 0 | 0 |  | 0 | 0
Dublin - 3100 Dublin Blvd | CA | 0 | 0 | 0 |  | 0 | 0

## Jan
KPCA Investment, LLC |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA
Murrieta - 28150 Keller Rd | CA
La Habra - 601 E Imperial Way | CA
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA
Irwindale - 12761 Schabarum Ave | CA
Santa Rosa - 2240 Mercury Way | CA
Dublin - 3100 Dublin Blvd | CA

## Feb
KPCA Investment, LLC |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA
Murrieta - 28150 Keller Rd | CA
La Habra - 601 E Imperial Way | CA
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA
Irwindale - 12761 Schabarum Ave | CA
Santa Rosa - 2240 Mercury Way | CA
Dublin - 3100 Dublin Blvd | CA

## Mar
KPCA Investment, LLC |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA
Murrieta - 28150 Keller Rd | CA
La Habra - 601 E Imperial Way | CA
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA
Irwindale - 12761 Schabarum Ave | CA
Santa Rosa - 2240 Mercury Way | CA
Dublin - 3100 Dublin Blvd | CA

## Apr
KPCA Investment, LLC |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 498732.2597 | 522792 | -24059.7403 | -4.602% | 576056.18 | -77323.9203 | -13.42%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA | 31190.7633 | 26716.3 | 4474.4633 | 16.75% | 40273 | -9082.2367 | -22.55% | 1. Meter A phase CT dropped 20 amps on 9/26/24. There is a 5 % variance between the meter and total inverter power. Will be addressed in next PM. | 1.SR098881
Murrieta - 28150 Keller Rd | CA | 87140 | 90233.95 | -3093.95 | -3.429% | 100122.5 | -12982.5 | -12.97% | 1.The site is producing as expected. The higher delta value indicates that the forecasted values are on the higher side.
La Habra - 601 E Imperial Way | CA | 17571.88 | 14932.1 | 2639.78 | 17.68% | 20943.08 | -3371.2 | -16.1% | 1.The site is producing as expected. The higher delta value indicates that the forecasted values are on the higher side.
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 97799.4949 | 102139.7 | -4340.2051 | -4.249% | 110380.3 | -12580.8051 | -11.4% | 1.Inverter 22 has been down a string (5 kW) since it was re-energized on 05/22/2024. The Operations Team is currently reviewing the issue. 2.Inverter 10 was offline from 04/01 and came back online at 10:30 on 04/04. It went offline again at 17:00 on 04/25 and remained offline for the rest of the month. A dispatch has been scheduled for next month. | 1.SR098879 2.SR099137,SR100773 | SR099137 | SR100773
Irwindale - 12761 Schabarum Ave | CA | 25974.62 | 20129.85 | 5844.77 | 29.04% | 29983.3 | -4008.68 | -13.37% | 1.The site is producing as expected. The higher delta value indicates that the forecasted values are on the higher side.
Santa Rosa - 2240 Mercury Way | CA | 78610.0015 | 86048.7 | -7438.6985 | -8.645% | 98920 | -20309.9985 | -20.53% | 1.Inverter 16 is having an history of multiple trip events. On 04/02, a technician addressed that faults occured due to PV imbalance issues and adjusted settings of comibner boxes. However, the inverter tripped again on 04/03 at 13:45, came online at 11:30 on 04/04,even after technician troubleshooted again inverter tripped at 12:45on 04/04. Issue got resolved after technician ensured all strands were compressed and torqued to 50 in-lbs. Inverter is back online at 14:00 on 04/22 | 1.SR099120,SR099410,SR099504 | SR099410 | SR099504
Dublin - 3100 Dublin Blvd | CA | 160445.5 | 182591.4 | -22145.9 | -12.13% | 175434 | -14988.5 | -8.544% | 1. Inverters 3, 5, and 7 may be swapped with 4, 6, and 8 in PowerTrack, as their performance suggests mismatched string counts—3, 5, and 7 (7-string) are performing like 8-string units, and vice versa. | 1.SR100567

## May
KPCA Investment, LLC |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 624624.6719 | 660255.13 | -35630.4581 | -5.396% | 673935.73 | -49311.0581 | -7.317%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA | 34717.2294 | 30123.32 | 4593.9094 | 15.25% | 45926 | -11208.7706 | -24.41% | 1.The A-phase CT on the meter recorded a drop of 20 amps on 09/26/2024. In May, the drop was reduced to 10 amps on the same phase. A 5% variance currently exwasts between the meter readings and the total inverter power. Thwas wassue was scheduled to be investigated during the upcoming preventive maintenance (PM) event. 2.Inverter 5 started late for production at 07:45 on 05/19.wassue got self resoled. | 1.SR098881 2.SR101671 | SR101671
Murrieta - 28150 Keller Rd | CA | 100090 | 104378.3 | -4288.3 | -4.108% | 118934.8 | -18844.8 | -15.84% | 1. Multiple inverters experiencied tripping events from 10:30AM to 15:30 due technician was onsite for preventive maintenance. 2. Inverter 5 was offline from 15:30 to 16:30 due technician was onsite for preventive maintenance. 3. The site was producing as expected. The higher delta value indicates that the forecasted values are on the higher side. | 1. PM13593 2. PM13593
La Habra - 601 E Imperial Way | CA | 19128.62 | 16120.48 | 3008.14 | 18.66% | 23850.17 | -4721.55 | -19.8% | 1.Inverter 3 down a string from 5/06. issue did not resolve. 2. Inverter 4 was offline from 10:55 to 11:20 on 05/06 due to technician was onsite for preventive maintenance. | 1.SR101329 2. PM13591.
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 128682.0512 | 133149.1 | -4467.0488 | -3.355% | 129050.2 | -368.1488 | -0.2853%
Irwindale - 12761 Schabarum Ave | CA | 27504.75 | 21662.73 | 5842.02 | 26.97% | 32927.56 | -5422.81 | -16.47% | 1. Multiple inverters experiencied tripping events from 11:30AM to 15:30 due technician was onsite for preventive maintenance. 2. The site was producing as expected. The higher delta value indicates that the forecasted values are on the higher side. | 1. PM13589
Santa Rosa - 2240 Mercury Way | CA | 110658.0214 | 118241.5 | -7583.4786 | -6.414% | 110018 | 640.0214 | 0.5817%
Dublin - 3100 Dublin Blvd | CA | 203844 | 236579.7 | -32735.7 | -13.84% | 213229 | -9385 | -4.401% | 1.Inverter 14 tripped offline at 11:15 and self resolved at 11:25 on 05/03. 2. Inverters 3, 5, and 7 may be swapped with inverters 4, 6, and 8 in PowerTrack. Invs 3, 5, and 7 are seven string inverters that are performing like eight string inverters, while 4, 6, and 8 are eight string inverters that are performing like seven strings. Will investigate during PM event. | 1.SR100962 2. SR100567 | SR100567

## Jun
KPCA Investment, LLC |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 648401.1269 | 651929.145 | -3528.0181 | -0.5412% | 689585.119 | -41183.9921 | -5.972%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA | 39240.9447 | 31865.03 | 7375.9147 | 23.15% | 46451 | -7210.0553 | -15.52% | 1.The A-phase CT on the meter recorded a drop of 20 amps on 09/26/2024. In May, the drop was reduced to 10 amps on the same phase. A 5% variance currently exwasts between the meter readings and the total inverter power. This issue was scheduled to be investigated during the upcoming preventive maintenance (PM) event. 2.Inverter 1 is underperforming by 5 kW down compared to its peer inverters since 06/16 at 14:00. | 1. SR098881 2. SR103049 | SR103049
Murrieta - 28150 Keller Rd | CA | 114430 | 107363 | 7067 | 6.582% | 119932.1 | -5502.1 | -4.588%
La Habra - 601 E Imperial Way | CA | 23520.13 | 17005.17 | 6514.96 | 38.31% | 22551.32 | 968.81 | 4.296% | 1.Inverter 3 down a string from 5/06. Issue was haven't resolved. | 1. SR101329
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 130530.038 | 128905.29 | 1624.748 | 1.26% | 133450.089 | -2920.051 | -2.188%
Irwindale - 12761 Schabarum Ave | CA | 30614.5 | 23907.6 | 6706.9 | 28.05% | 32560.11 | -1945.61 | -5.975% | 1.Inverter 2 tripped offline at 06:15 on 06/23, reporting a 'Steady State GFCI Fault – Fault0090.' The inverter came back online on 06/24. | 1. SR103317
Santa Rosa - 2240 Mercury Way | CA | 105453.0142 | 111066.5 | -5613.4858 | -5.054% | 115486 | -10032.9858 | -8.688%
Dublin - 3100 Dublin Blvd | CA | 204612.5 | 231816.555 | -27204.055 | -11.74% | 219154.5 | -14542 | -6.636% | 1.Inverters 3, 5, and 7 may be swapped with inverters 4, 6, and 8 in PowerTrack. Invs 3, 5, and 7 are seven string inverters that are performing like eight string inverters, while 4, 6, and 8 are eight string inverters that are performing like seven strings. Will investigate during PM event. | 1. SR100567

## Jul
KPCA Investment, LLC |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 623987.737 | 663153.109 | -39165.372 | -5.906% | 718627 | -94639.263 | -13.17%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA | 38033.494 | 34071.27 | 3962.224 | 11.63% | 48864 | -10830.506 | -22.16% | 1. Inverter 1 is underperforming by 5 kW down compared to its peer inverters since 06/16 at 14:00. 2.The A-phase CT on the meter recorded a drop of 20 amps on 09/26/2024. In May, the drop was reduced to 10 amps on the same phase. A 5% variance currently exist between the meter readings and the total inverter power. | 1. SR103049 2. SR104160 | SR104160
Murrieta - 28150 Keller Rd | CA | 115259 | 114481.1 | 777.9 | 0.6795% | 126237 | -10978 | -8.696%
La Habra - 601 E Imperial Way | CA | 24207.37 | 18656.803 | 5550.567 | 29.75% | 25624 | -1416.63 | -5.529%
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 123422.003 | 129061.81 | -5639.807 | -4.37% | 141665 | -18242.997 | -12.88% | 1. Inverter 16 is having reoccurring late starts from 6/12. 2. Inverter 20 is down a string since 7/7. | 1. SR103140 2. SR104320 | SR104320
Irwindale - 12761 Schabarum Ave | CA | 31536.37 | 25932.523 | 5603.847 | 21.61% | 37219 | -5682.63 | -15.27% | 1.Inverter 5 String 4 has low performance. | 1.SR102034
Santa Rosa - 2240 Mercury Way | CA | 97975.5 | 110139.48 | -12163.98 | -11.04% | 117314 | -19338.5 | -16.48%
Dublin - 3100 Dublin Blvd | CA | 193554 | 230810.123 | -37256.123 | -16.14% | 221704 | -28150 | -12.7% | 1.Inverters 3, 5, and 7 may be swapped with inverters 4, 6, and 8 in PowerTrack. Invs 3, 5, and 7 are seven string inverters that are performing like eight string inverters, while 4, 6, and 8 are eight string inverters that are performing like seven strings. | 1. SR100567

## Aug
KPCA Investment, LLC |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 548563.9734 | 603181.84 | -54617.8666 | -9.055% | 654651.87 | -106087.8966 | -16.21%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA | 31906.6545 | 30044.7 | 1861.9545 | 6.197% | 45234 | -13327.3455 | -29.46% | 1.Inverter 1 is underperforming by 5 kW down compared to its peer inverters since 06/16 at 14:00. 2.The A-phase CT on the meter recorded a drop of 20 amps on 09/26/2024. In May, the drop was reduced to 10 amps on the same phase. A 5% variance currently exist between the meter readings and the total inverter power. | 1.SR103049 2.SR104160 | SR104160
Murrieta - 28150 Keller Rd | CA | 95153 | 99725.96 | -4572.96 | -4.586% | 114410.4 | -19257.4 | -16.83% | 1.Site is producing as expected, may be issue with forecasted value
La Habra - 601 E Imperial Way | CA | 21199.63 | 16694.73 | 4504.9 | 26.98% | 26525.81 | -5326.18 | -20.08% | 1.Site is producing as expected, may be issue with forecasted value
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 106893.0438 | 114393.8 | -7500.7562 | -6.557% | 123121.9 | -16228.8562 | -13.18% | 1. Inverter 16 is having reoccurring late starts from 6/12. 2. Inverter 20 is down a string since 7/7. | 1.SR103140 2.SR104320 | SR104320
Irwindale - 12761 Schabarum Ave | CA | 25933.63 | 22533.55 | 3400.08 | 15.09% | 33846.76 | -7913.13 | -23.38% | 1.Inverter 5 String 4 has low performance. 2. Inverters 1 and 2 tripped offline at 7:00 on 08/27 and later back online on 08/28 at 07:00 | 1.SR102034 2.SR107041 | SR107041
Santa Rosa - 2240 Mercury Way | CA | 92708.0152 | 107429.3 | -14721.2848 | -13.7% | 107538 | -14829.9848 | -13.79%
Dublin - 3100 Dublin Blvd | CA | 174770 | 212359.8 | -37589.8 | -17.7% | 203975 | -29205 | -14.32% | 1.Low production due to weather on 08/16

## Sep
KPCA Investment, LLC |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA
Murrieta - 28150 Keller Rd | CA
La Habra - 601 E Imperial Way | CA
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA
Irwindale - 12761 Schabarum Ave | CA
Santa Rosa - 2240 Mercury Way | CA
Dublin - 3100 Dublin Blvd | CA

## Oct
KPCA Investment, LLC |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA
Murrieta - 28150 Keller Rd | CA
La Habra - 601 E Imperial Way | CA
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA
Irwindale - 12761 Schabarum Ave | CA
Santa Rosa - 2240 Mercury Way | CA
Dublin - 3100 Dublin Blvd | CA

## Nov
KPCA Investment, LLC |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA
Murrieta - 28150 Keller Rd | CA
La Habra - 601 E Imperial Way | CA
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA
Irwindale - 12761 Schabarum Ave | CA
Santa Rosa - 2240 Mercury Way | CA
Dublin - 3100 Dublin Blvd | CA

## Dec
KPCA Investment, LLC |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA
Murrieta - 28150 Keller Rd | CA
La Habra - 601 E Imperial Way | CA
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA
Irwindale - 12761 Schabarum Ave | CA
Santa Rosa - 2240 Mercury Way | CA
Dublin - 3100 Dublin Blvd | CA

## Sites
Portfolio: | KPCA Investment, LLC
Site DAS Name | Site | State | Update | DAS
Kaiser - KP3 - Chino Grand CA6581 | Chino - 3750-3770 Grand Ave | CA | AEF | PowerTrack
Murrietta MOB - CA5341 | Murrieta - 28150 Keller Rd | CA | AEF | PowerTrack
Kaiser - KP3 - La Habra - CA3841 Site | La Habra - 601 E Imperial Way | CA | AEF | PowerTrack
San Jose - Skyport | Kaiser - KP3 - SCA Skyport - CN7901 Site | CA |  | PowerTrack
Kaiser - KP3 - Irwindale MOB & Garage - CA5681 Site | Irwindale - 12761 Schabarum Ave | CA | AEF | PowerTrack
Santa Rosa 6 - CN7001 | Santa Rosa - 2240 Mercury Way | CA | AEF | PowerTrack
Kaiser - KP3 - Dublin - CN2A99 Site | Dublin - 3100 Dublin Blvd | CA |  | PowerTrack