## Year to Date
Lodestar |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 91171400.5414 | 79061151.1785 | 12110249.3629 | 15.32% | 88400866.918 | 2770533.6234 | 3.134%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Barkhamsted | CT | 1580112 | 1875751.1 | -295639.1 | -15.76% | 1788264.43 | -208152.43 | -11.64%
Bunce | CT | 3160363.5 | 2475177.8 | 685185.7 | 27.68% | 0 | 2262123.5
Norcap North | CT | 3317404 | 3699914.2 | -382510.2 | -10.34% | 3424910.3 | -107506.3 | -3.139%
Norcap South | CT | 3553633.5 | 3951759.9 | -398126.4 | -10.07% | 3289634.6 | 263998.9 | 8.025%
Platt Hill | CT | 3466773 | 3922230.4 | -455457.4 | -11.61% | 3959405.4 | -492632.4 | -12.44%
Powder Hill | CT | 3220508 | 3500014.7 | -279506.7 | -7.986% | 2690268 | 530240 | 19.71%
Sand Road | CT | 3359838 | 3156072.1 | 203765.9 | 6.456% | 3021906 | 337932 | 11.18%
Suffield | CT | 3359607 | 3381400.5 | -21793.5 | -0.6445% | 3472305.9 | -112698.9 | -3.246%
Ashby-Duffy | MA | 3048542 | 4135403.6 | -1086861.6 | -26.28% | 3239642.2 | -191100.2 | -5.899%
Ashland | MA | 3072605 | 3579560.4 | -506955.4 | -14.16% | 3454762.88 | -382157.88 | -11.06%
Barrington | MA | 665481 | 500475.55 | 165005.45 | 32.97% | 788100 | -122619 | -15.56%
Bedford - 205 Burlington Rd | MA | 322952 | 0 | 322952 |  | 0 | 0
Billerica - 6 Cook Street | MA | 330422 | 0 | 330422 |  | 0 | 0
Billerica - 780 Boston Road | MA | 370263 | 0 | 370263 |  | 0 | 0
Cheshire | MA | 677669.3726 | 778447.78 | -100778.4074 | -12.95% | 576413.27 | 101256.1026 | 17.57%
Lilly Lane | MA | 1368222.5 | 1387707.95 | -19485.45 | -1.404% | 1590773.2 | -222550.7 | -13.99%
Monument Valley | MA | 3129225.88 | 1523217.57 | 1606008.31 | 105.4% | 1120255.048 | 1191637.542 | 106.4%
Nationwide | MA | 4747086 | 5120385.3 | -373299.3 | -7.29% | 5146398.2 | -399312.2 | -7.759%
Pulpit Hill | MA | 7240815.25 | 7414548.5 | -173733.25 | -2.343% | 7200918.1 | 39897.15 | 0.5541%
Sandwich | MA | 4487053 | 171564.5 | 4315488.5 | 2515% | 5470370.56 | -983317.56 | -17.98%
Sturbridge Barn | MA | 1661662 | 1809737.2 | -148075.2 | -8.182% | 1892812.35 | -231150.35 | -12.21%
Sturbridge Garage | MA | 786032.75 | 858588.05 | -72555.3 | -8.451% | 885045.69 | -99012.94 | -11.19%
Halsey Valley | NY | 8105738 | 8587017.4 | -481279.4 | -5.605% | 8817000 | -711262 | -8.067%
Hunt Creek | NY | 5421556 | 6183427 | -761871 | -12.32% | 6128700 | -707144 | -11.54%
Smith Creek | NY | 6367892 | 6857500.7 | -489608.7 | -7.14% | 7014925.6 | -647033.6 | -9.224%
Bradford - 256 Presidential Dr | MA | 6788367.43 | 1382228.9071 | 5406138.5229 | 391.1% | 5454410.7 | -567656.868 | -10.41%
Charlton – 111 Brookfield Road - Bus Lot | MA | 806927.988 | 128503.3843 | 678424.6037 | 527.9% | 677997.25 | -118133.418 | -17.42%
Charlton – 154 Center Depot Road KMARD | MA | 684916.912 | 176882.001 | 508034.911 | 287.2% | 665635.16 | -194932.22 | -29.29%
Charlton – 142A Brookfield Rd (Mitchell) | MA | 747448.94 | 187579.0295 | 559869.9105 | 298.5% | 678799.58 | -155626.588 | -22.93%
Great Barrington – 3 Nolan Drive | MA | 1286085.6567 | 358533.4373 | 927552.2194 | 258.7% | 1330834.78 | -506855.2193 | -38.09%
Stockbridge – 92 State Line Road Truck Stop | MA | 2522809.647 | 680989.0193 | 1841820.6277 | 270.5% | 2606623.42 | -952915.967 | -36.56%
NY: New Windsor - Moores Hill | NY | 1513387.2151 | 1276533.2 | 236854.0151 | 18.55% | 2013754.3 | -500367.0849 | -24.85%

## 1st Qtr
Lodestar |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 16452264.0705 | 19010660.0585 | -2558395.9879 | -13.46% | 18375451.88 | -1923187.8095 | -10.47%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Barkhamsted | CT | 268344 | 421750.9 | -153406.9 | -36.37% | 378669.74 | -110325.74 | -29.14%
Bunce | CT | 601753.5 | 684621.1 | -82867.6 | -12.1% | 0 | 0
Norcap North | CT | 665544 | 901318.4 | -235774.4 | -26.16% | 696719.6 | -31175.6 | -4.475%
Norcap South | CT | 722340.5 | 975622.9 | -253282.4 | -25.96% | 656577.7 | 65762.8 | 10.02%
Platt Hill | CT | 558121 | 824707.8 | -266586.8 | -32.33% | 857153.4 | -299032.4 | -34.89%
Powder Hill | CT | 636559 | 764818.1 | -128259.1 | -16.77% | 566964 | 69595 | 12.28%
Sand Road | CT | 629363 | 693953.2 | -64590.2 | -9.308% | 602989 | 26374 | 4.374%
Suffield | CT | 646808 | 747386.4 | -100578.4 | -13.46% | 728845.7 | -82037.7 | -11.26%
Ashby-Duffy | MA | 531938 | 986411 | -454473 | -46.07% | 648393.4 | -116455.4 | -17.96%
Ashland | MA | 531484 | 790545.5 | -259061.5 | -32.77% | 680224.1 | -148740.1 | -21.87%
Barrington | MA | 112260.5 | 75219.05 | 37041.45 | 49.24% | 159190 | -46929.5 | -29.48%
Bedford - 205 Burlington Rd | MA | 54600 | 0 | 54600 |  | 0 | 0
Billerica - 6 Cook Street | MA | 47090 | 0 | 47090 |  | 0 | 0
Billerica - 780 Boston Road | MA | 52916 | 0 | 52916 |  | 0 | 0
Cheshire | MA | 105971.0388 | 161225.96 | -55254.9212 | -34.27% | 105817.65 | 153.3888 | 0.145%
Lilly Lane | MA | 287612.5 | 337821.29 | -50208.79 | -14.86% | 405645 | -118032.5 | -29.1%
Monument Valley | MA | 504123.785 | 150513.18 | 353610.605 | 234.9% | 0 | 0
Nationwide | MA | 727663 | 1141247.2 | -413584.2 | -36.24% | 1092285.2 | -364622.2 | -33.38%
Pulpit Hill | MA | 1299577.25 | 1581139.1 | -281561.85 | -17.81% | 1505519.1 | -205941.85 | -13.68%
Sandwich | MA | 953865 | 0 | 953865 |  | 1158752 | -204887 | -17.68%
Sturbridge Barn | MA | 306719.5 | 405365.2 | -98645.7 | -24.34% | 415888.3 | -109168.8 | -26.25%
Sturbridge Garage | MA | 150401.5 | 193175.9 | -42774.4 | -22.14% | 200379.4 | -49977.9 | -24.94%
Halsey Valley | NY | 1532926 | 1689825.8 | -156899.8 | -9.285% | 1609000 | -76074 | -4.728%
Hunt Creek | NY | 937590 | 1217312.3 | -279722.3 | -22.98% | 1067900 | -130310 | -12.2%
Smith Creek | NY | 1189719 | 1351964 | -162245 | -12% | 1473505.7 | -283786.7 | -19.26%
Bradford - 256 Presidential Dr | MA | 1294062.5 | 1382228.9071 | -88166.4071 | -6.379% | 1600941.7 | -306879.2 | -19.17%
Charlton – 111 Brookfield Road - Bus Lot | MA | 145538 | 128503.3843 | 17034.6157 | 13.26% | 198897.25 | -53359.25 | -26.83%
Charlton – 154 Center Depot Road KMARD | MA | 106050 | 176882.001 | -70832.001 | -40.04% | 192235.16 | -86185.16 | -44.83%
Charlton – 142A Brookfield Rd (Mitchell) | MA | 139150 | 187579.0295 | -48429.0295 | -25.82% | 200400.58 | -61250.58 | -30.56%
Great Barrington – 3 Nolan Drive | MA | 250735.4967 | 358533.4373 | -107797.9406 | -30.07% | 397534.78 | -146799.2833 | -36.93%
Stockbridge – 92 State Line Road Truck Stop | MA | 461438 | 680989.0193 | -219551.0193 | -32.24% | 775023.42 | -313585.42 | -40.46%
NY: New Windsor - Moores Hill | NY | 0 | 0 | 0 |  | 0 | 0

## 2nd Qtr
Lodestar |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 27409237.6402 | 20197106.8 | 7212130.8402 | 35.71% | 23526613.77 | 3882623.8702 | 16.5%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Barkhamsted | CT | 488022 | 499602.4 | -11580.4 | -2.318% | 552800.6 | -64778.6 | -11.72%
Bunce | CT | 939190.5 | 617730.3 | 321460.2 | 52.04% | 0 | 642704
Norcap North | CT | 966580.5 | 907589.1 | 58991.4 | 6.5% | 1056079.1 | -89498.6 | -8.475%
Norcap South | CT | 1004243.5 | 949566.9 | 54676.6 | 5.758% | 1034687.8 | -30444.3 | -2.942%
Platt Hill | CT | 1072739 | 1085877.8 | -13138.8 | -1.21% | 1208681 | -135942 | -11.25%
Powder Hill | CT | 989969 | 972850 | 17119 | 1.76% | 838176 | 151793 | 18.11%
Sand Road | CT | 980092 | 847138.8 | 132953.2 | 15.69% | 1002416 | -22324 | -2.227%
Suffield | CT | 994731 | 950464.3 | 44266.7 | 4.657% | 1089283 | -94552 | -8.68%
Ashby-Duffy | MA | 925117 | 1044535.7 | -119418.7 | -11.43% | 996418.8 | -71301.8 | -7.156%
Ashland | MA | 957468 | 995983.6 | -38515.6 | -3.867% | 1145089.9 | -187621.9 | -16.38%
Barrington | MA | 214385 | 115602.33 | 98782.67 | 85.45% | 248210 | -33825 | -13.63%
Bedford - 205 Burlington Rd | MA | 122934 | 0 | 122934 |  | 0 | 0
Billerica - 6 Cook Street | MA | 113063 | 0 | 113063 |  | 0 | 0
Billerica - 780 Boston Road | MA | 128576 | 0 | 128576 |  | 0 | 0
Cheshire | MA | 217590.4612 | 223989.77 | -6399.3088 | -2.857% | 202311.65 | 15278.8112 | 7.552%
Lilly Lane | MA | 490698.5 | 466177.7 | 24520.8 | 5.26% | 530125.9 | -39427.4 | -7.437%
Monument Valley | MA | 977275.215 | 181192.68 | 796082.535 | 439.4% | 0 | 664065.71
Nationwide | MA | 1738166 | 1389197.4 | 348968.6 | 25.12% | 1605958.6 | 132207.4 | 8.232%
Pulpit Hill | MA | 2205243.25 | 2088898.3 | 116344.95 | 5.57% | 2264471.1 | -59227.85 | -2.616%
Sandwich | MA | 1277538 | 0 | 1277538 |  | 1699406 | -421868 | -24.82%
Sturbridge Barn | MA | 497702 | 489727.6 | 7974.4 | 1.628% | 572486.3 | -74784.3 | -13.06%
Sturbridge Garage | MA | 245158.75 | 233090.92 | 12067.83 | 5.177% | 261868.52 | -16709.77 | -6.381%
Halsey Valley | NY | 2370262 | 2383502.8 | -13240.8 | -0.5555% | 2876000 | -505738 | -17.58%
Hunt Creek | NY | 1699800 | 1747439.1 | -47639.1 | -2.726% | 2078200 | -378400 | -18.21%
Smith Creek | NY | 1865000 | 1919297.3 | -54297.3 | -2.829% | 2163657.5 | -298657.5 | -13.8%
Bradford - 256 Presidential Dr | MA | 1901613.598 | 0 | 1901613.598 |  | 0 | 0
Charlton – 111 Brookfield Road - Bus Lot | MA | 247064.156 | 0 | 247064.156 |  | 0 | 0
Charlton – 154 Center Depot Road KMARD | MA | 214213.972 | 0 | 214213.972 |  | 0 | 0
Charlton – 142A Brookfield Rd (Mitchell) | MA | 224275.948 | 0 | 224275.948 |  | 0 | 0
Great Barrington – 3 Nolan Drive | MA | 462106.096 | 0 | 462106.096 |  | 0 | 0
Stockbridge – 92 State Line Road Truck Stop | MA | 869102.194 | 0 | 869102.194 |  | 0 | 0
NY: New Windsor - Moores Hill | NY | 9317 | 87652 | -78335 | -89.37% | 100286 | -90969 | -90.71%

## 3rd Qtr
Lodestar |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 32593211.6266 | 25572025.1 | 7021186.5266 | 27.46% | 30659277.17 | 1933934.4566 | 6.308%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Barkhamsted | CT | 543160 | 589062 | -45902 | -7.792% | 547057.7 | -3897.7 | -0.7125%
Bunce | CT | 1103132.5 | 677103.3 | 426029.2 | 62.92% | 0 | 1103132.5
Norcap North | CT | 1106369 | 1103002 | 3367 | 0.3053% | 1059127.5 | 47241.5 | 4.46%
Norcap South | CT | 1180807 | 1164374.3 | 16432.7 | 1.411% | 1039012.9 | 141794.1 | 13.65%
Platt Hill | CT | 1207796 | 1266820.4 | -59024.4 | -4.659% | 1235926.9 | -28130.9 | -2.276%
Powder Hill | CT | 1102702 | 1122677.5 | -19975.5 | -1.779% | 837084 | 265618 | 31.73%
Sand Road | CT | 1190384 | 1054242.6 | 136141.4 | 12.91% | 972780 | 217604 | 22.37%
Suffield | CT | 1139403 | 1104676.1 | 34726.9 | 3.144% | 1067560.1 | 71842.9 | 6.73%
Ashby-Duffy | MA | 1041735 | 1131681.4 | -89946.4 | -7.948% | 1016084.4 | 25650.6 | 2.524%
Ashland | MA | 1079434 | 1132409.4 | -52975.4 | -4.678% | 1121788.5 | -42354.5 | -3.776%
Barrington | MA | 239175.5 | 204493.41 | 34682.09 | 16.96% | 253900 | -14724.5 | -5.799%
Bedford - 205 Burlington Rd | MA | 115055 | 0 | 115055 |  | 0 | 0
Billerica - 6 Cook Street | MA | 121578 | 0 | 121578 |  | 0 | 0
Billerica - 780 Boston Road | MA | 132427 | 0 | 132427 |  | 0 | 0
Cheshire | MA | 252179.1203 | 260819.11 | -8639.9897 | -3.313% | 190558.51 | 61620.6103 | 32.34%
Lilly Lane | MA | 536905 | 531570.9 | 5334.1 | 1.003% | 528239.3 | 8665.7 | 1.64%
Monument Valley | MA | 1147298.9738 | 717249.51 | 430049.4638 | 59.96% | 624528 | 522770.9738 | 83.71%
Nationwide | MA | 1703438 | 1641454.5 | 61983.5 | 3.776% | 1596214.7 | 107223.3 | 6.717%
Pulpit Hill | MA | 2505827 | 2397500 | 108327 | 4.518% | 2242795.8 | 263031.2 | 11.73%
Sandwich | MA | 1591604 | 0 | 1591604 |  | 1690066.64 | -98462.64 | -5.826%
Sturbridge Barn | MA | 550027 | 559498.6 | -9471.6 | -1.693% | 564782.9 | -14755.9 | -2.613%
Sturbridge Garage | MA | 261055 | 265688.77 | -4633.77 | -1.744% | 260937.82 | 117.18 | 0.04491%
Halsey Valley | NY | 2945486 | 3007757.2 | -62271.2 | -2.07% | 2919000 | 26486 | 0.9074%
Hunt Creek | NY | 2053599 | 2177721.7 | -124122.7 | -5.7% | 2081600 | -28001 | -1.345%
Smith Creek | NY | 2290871 | 2397157.5 | -106286.5 | -4.434% | 2181391.5 | 109479.5 | 5.019%
Bradford - 256 Presidential Dr | MA | 2445408.273 | 0 | 2445408.273 |  | 2565731 | -120322.727 | -4.69%
Charlton – 111 Brookfield Road - Bus Lot | MA | 267285.984 | 0 | 267285.984 |  | 309300 | -42014.016 | -13.58%
Charlton – 154 Center Depot Road KMARD | MA | 231650.96 | 0 | 231650.96 |  | 295200 | -63549.04 | -21.53%
Charlton – 142A Brookfield Rd (Mitchell) | MA | 247055.824 | 0 | 247055.824 |  | 304909 | -57853.176 | -18.97%
Great Barrington – 3 Nolan Drive | MA | 381545.76 | 0 | 381545.76 |  | 602700 | -221154.24 | -36.69%
Stockbridge – 92 State Line Road Truck Stop | MA | 880432.104 | 0 | 880432.104 |  | 1224700 | -344267.896 | -28.11%
NY: New Windsor - Moores Hill | NY | 998384.6276 | 1065064.9 | -66680.2724 | -6.261% | 1326300 | -327915.3724 | -24.72%

## 4th Qtr
Lodestar |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 14716687.204 | 14281359.22 | 435327.984 | 3.048% | 15839524.098 | -1122836.894 | -7.089%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Barkhamsted | CT | 280586 | 365335.8 | -84749.8 | -23.2% | 309736.39 | -29150.39 | -9.411%
Bunce | CT | 516287 | 495723.1 | 20563.9 | 4.148% | 0 | 516287
Norcap North | CT | 578910.5 | 788004.7 | -209094.2 | -26.53% | 612984.1 | -34073.6 | -5.559%
Norcap South | CT | 646242.5 | 862195.8 | -215953.3 | -25.05% | 559356.2 | 86886.3 | 15.53%
Platt Hill | CT | 628117 | 744824.4 | -116707.4 | -15.67% | 657644.1 | -29527.1 | -4.49%
Powder Hill | CT | 491278 | 639669.1 | -148391.1 | -23.2% | 448044 | 43234 | 9.649%
Sand Road | CT | 559999 | 560737.5 | -738.5 | -0.1317% | 443721 | 116278 | 26.21%
Suffield | CT | 578665 | 578873.7 | -208.7 | -0.03605% | 586617.1 | -7952.1 | -1.356%
Ashby-Duffy | MA | 549752 | 972775.5 | -423023.5 | -43.49% | 578745.6 | -28993.6 | -5.01%
Ashland | MA | 504219 | 660621.9 | -156402.9 | -23.68% | 507660.38 | -3441.38 | -0.6779%
Barrington | MA | 99660 | 105160.76 | -5500.76 | -5.231% | 126800 | -27140 | -21.4%
Bedford - 205 Burlington Rd | MA | 30363 | 0 | 30363 |  | 0 | 0
Billerica - 6 Cook Street | MA | 48691 | 0 | 48691 |  | 0 | 0
Billerica - 780 Boston Road | MA | 56344 | 0 | 56344 |  | 0 | 0
Cheshire | MA | 101928.7524 | 132412.94 | -30484.1876 | -23.02% | 77725.46 | 24203.2924 | 31.14%
Lilly Lane | MA | 53006.5 | 52138.06 | 868.44 | 1.666% | 126763 | -73756.5 | -58.18%
Monument Valley | MA | 500527.9062 | 474262.2 | 26265.7062 | 5.538% | 495727.048 | 4800.8582 | 0.9684%
Nationwide | MA | 577819 | 948486.2 | -370667.2 | -39.08% | 851939.7 | -274120.7 | -32.18%
Pulpit Hill | MA | 1230167.75 | 1347011.1 | -116843.35 | -8.674% | 1188132.1 | 42035.65 | 3.538%
Sandwich | MA | 664046 | 171564.5 | 492481.5 | 287.1% | 922145.92 | -258099.92 | -27.99%
Sturbridge Barn | MA | 307213.5 | 355145.8 | -47932.3 | -13.5% | 339654.85 | -32441.35 | -9.551%
Sturbridge Garage | MA | 129417.5 | 166632.46 | -37214.96 | -22.33% | 161859.95 | -32442.45 | -20.04%
Halsey Valley | NY | 1257064 | 1505931.6 | -248867.6 | -16.53% | 1413000 | -155936 | -11.04%
Hunt Creek | NY | 730567 | 1040953.9 | -310386.9 | -29.82% | 901000 | -170433 | -18.92%
Smith Creek | NY | 1022302 | 1189081.9 | -166779.9 | -14.03% | 1196370.9 | -174068.9 | -14.55%
Bradford - 256 Presidential Dr | MA | 1147283.059 | 0 | 1147283.059 |  | 1287738 | -140454.941 | -10.91%
Charlton – 111 Brookfield Road - Bus Lot | MA | 147039.848 | 0 | 147039.848 |  | 169800 | -22760.152 | -13.4%
Charlton – 154 Center Depot Road KMARD | MA | 133001.98 | 0 | 133001.98 |  | 178200 | -45198.02 | -25.36%
Charlton – 142A Brookfield Rd (Mitchell) | MA | 136967.168 | 0 | 136967.168 |  | 173490 | -36522.832 | -21.05%
Great Barrington – 3 Nolan Drive | MA | 191698.304 | 0 | 191698.304 |  | 330600 | -138901.696 | -42.02%
Stockbridge – 92 State Line Road Truck Stop | MA | 311837.349 | 0 | 311837.349 |  | 606900 | -295062.651 | -48.62%
NY: New Windsor - Moores Hill | NY | 505685.5875 | 123816.3 | 381869.2875 | 308.4% | 587168.3 | -81482.7125 | -13.88%

## Jan
Lodestar |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 3838099.3873 | 5382433.8674 | -1544334.4801 | -28.69% | 4641331.91 | -803232.5227 | -17.31% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT | 42488 | 130906.1 | -88418.1 | -67.54% | 95618.24 | -53130.24 | -55.56% | 1. Combiner Boxes 1.2 (DCP 1), 1.3 (DCP 7), 1.5 (DCP 14), 1.7 (DCP 10), 1.10 (DCP 4), 1.11 (DCP 11), and 1.15 (DCP 12) have been offline since 12/22/24. On 01/02/25, the technician discovered blown glass fuses. As per Shoals' instructions, parts are needed to bring them back online, and they have remained offline throughout the month. 2. Combiner 1.14 (DCP-3) is showing constant value of 312Amps from 08/30 due to a faulty CT. 3. All inverters tripped on and off on 01/09 and 01/10, with Inverter 1.5 tripped offline at 10:30 AM on 01/09. On 01/11, the PE technician restored only Inverter 1.1, while the others remained offline. On 01/13, the PE technician worked on all inverters, brought Inverter 1.5 back online at 16:30. The remaining inverters were restored on 01/14/25. | 1.SR095215 2.SR089788 3.SR095444
Bunce | CT | 147884 | 196766.8 | -48882.8 | -24.84% | N/A |  |  | 1. Inverters 10,11 and 13 are started late for production at 11:45AM on 01/17 due to insulation fault. 2. Low generation due to rain/snow. | 1. SR095646
Norcap North | CT | 162639 | 288186.5 | -125547.5 | -43.56% | 178945.5 | -16306.5 | -9.113% | 1. Inverter 12 came back online at 13:30 on 01/02. The technician investigated the issue and cleared the fault. 2. Inverters 14 to 17 tripped offline at 11:45AM on 01/26. The technician replaced the shunt trip for HP1 with HP4. The inverters came back online at 11:15AM on 01/27. 3. Inverter 25 has been intermittently offline for the whole month due to a bus differential fault. Solectria has issued an RMA for the inverter. 4. Inverter 30 started production late at 13:15 on 01/27. The technician resolved the issue with Solectria. Solectria will issue an RMA if the inverter trips again. | 1. SR095170 2. SR095990 3. SR096190, SR094843 4. SR096007
Norcap South | CT | 184293.5 | 319084.7 | -134791.2 | -42.24% | 155781 | 28512.5 | 18.3% | 1.Inverter 36 offline on 01/01 due to insulation resistance fault and self resolve on 01/02 2. Low generation due to rain/snow. | 1.SR095132
Platt Hill | CT | 115129.745 | 228108.9 | -112979.155 | -49.53% | 231339.2 | -116209.455 | -50.23% | 1. The site tripped offline at 10:45AM on 01/03 and came back online at 07:00 AM on 01/06. The technician found that the surge protector breaker had tripped and reset it. 2. The site tripped offline at 05:45AM on 01/16 while the technician was onsite to remove the failed breaker. The site came back online at 08:30AM on 01/17 after the breaker was replaced. 3.Inverter 1 has started late for the production at 12:00 on 01/17 but two strings are kept offline for safety due to tree has felt on array | 1. SR095275 2. SR095529 3.SR095652
Powder Hill | CT | 157653 | 225761.3 | -68108.3 | -30.17% | 155676 | 1977 | 1.27% | 1. Inverter 7 started production late and later self-resolved at 09:15 AM on 01/13 due to a self-check startup failure. It failed to start again on 01/17 but was brought back online via a remote reset at 10:45 AM the same day. However, it tripped offline again at 11:15 AM on 01/27. The technician investigated the issue, and Inverter 7 was back online at 07:00 AM and 3 CT's were RMA'd on 01/28. 2. Inverter 8 dropped offline at 11:45 AM and was producing only 5 kW consistently. After a remote reset, the inverter came back online at 13:45 on 01/28. 3. Low generation due to rain/snow. | 1. SR095513 2. SR095081
Sand Road | CT | 151595 | 198096.8 | -46501.8 | -23.47% | 145302 | 6293 | 4.331% | 1. Site offline at 15:30 on 01/18. Technician found the Main AC Breaker tripped and the SEL-751 in the trip position with an "AC Loss" fault. Reset both the SEL and Main AC Breaker. The site is back online at 12:45 on 01/19. 2. Low generation due to rain/snow. | 1. SR095701
Suffield | CT | 177443 | 223979.4 | -46536.4 | -20.78% | 190993.6 | -13550.6 | -7.095% | 1. Low generation due to rain/snow.
Ashby-Duffy | MA | 153090 | 301950.1 | -148860.1 | -49.3% | 157476.5 | -4386.5 | -2.785% | 1. Inverter 2 remains offline for the whole month and will need to wait until the ground is unfrozen. 2. Inverter 55 tripped offline at 11:15 AM on 01/03 due to an electrical arc fault. After a reset, the inverter came back online at 10:30 AM on 01/06. 3. Inverter 54 tripped offline at 12:45 on 01/03 due to a high residual current. The technician found a field-made jumper connection with thermal damage. The MC M/F connectors were repaired and replaced. The inverter came back online at 10:30 on 01/06. 4.Inverter 39 string 5 blown a fuse and later technician replaced fuses on 01/15 5. Low generation due to rain/snow. | 1. SR093777 2. SR095277 3. SR095288 4.SR094302
Ashland | MA | 125168.5 | 243462.5 | -118294 | -48.59% | 133620.2 | -8451.7 | -6.325% | 1. Inverter 16 was offline since 11/13 due to Arc Protection and being RMA'd. 2. Inverter 30 tripped offline at 13:45 on 01/12 due to an insulation fault and later self-resolved, inverter back online at 14:15. 3.Inverter 66 tripped offline at 11:00 AM on 01/06 and self-resolved, inverter back online at 07:00 AM on 01/08. 4. Inverter 12 was offline intermittently whole month and being RMA'd. 5. Inverter 67 was being in RMA'd. 6. Inverter 57 was being in RMA'd. 7.Inverter 66 is bearly producing from 01/30 8. Low generation due to rain/snow. | 1. SR095816 2. SR095504 3. SR094685 4. SR093117 5. SR088450 6. SR091962 7.SR096271
Barrington | MA | 21905.5 | 31381.54 | -9476.04 | -30.2% | 35820 | -13914.5 | -38.85% | 1. Low generation due to weather/snow.
Bedford - 205 Burlington Rd | MA | 12393 | N/A |  |  | N/A
Billerica - 6 Cook Street | MA | 9769 | N/A |  |  | N/A
Billerica - 780 Boston Road | MA | 10676 | N/A |  |  | N/A
Cheshire | MA | 20350.2064 | 43079.92 | -22729.7136 | -52.76% | 24192.56 | -3842.3536 | -15.88% | 1. Low generation due to rain/snow.
Lilly Lane | MA | 66477 | 93441.89 | -26964.89 | -28.86% | 112568.7 | -46091.7 | -40.95% | 1. Inverter 61 has been intermittently offline throughout the month and has been RMA'd. 2. The site tripped offline at 18:00 on 01/02. The technician found that the switchgear was open and the SEL-351A had tripped. He reset the SEL and closed the switchgear. The site came back online at 09:00 AM on 01/03. | 1. SR095846, SR095210 2. SR095259
Monument Valley | MA | 92298 | 36912.89 | 55385.11 | 150% | N/A |  |  | 1. Site production dropped at 15:15 on 01/28 as Sungrow technicians were onsite working on BESS. They continued work on 01/29, and production returned to normal at 15:30 on 01/29. 2. Expected generation values are lower than actual values. AlsoEnergy stated that expected values are calculated based on inverter data and weather conditions and recommended an onsite visit. However, due to communication issues with the inverters, the expected values remain low. | 1. SR092970 2. SR087370
Nationwide | MA | 149646 | 334678.8 | -185032.8 | -55.29% | 297479.6 | -147833.6 | -49.7% | 1. Inverter 16 tripped offline at 08:45AM on 01/19, inverter was self-resolved at 10:15AM on 01/21. 2. Low generation due to rain/snow. | 1. SR095712
Pulpit Hill | MA | 316117.75 | 470954.2 | -154836.45 | -32.88% | 355177.1 | -39059.35 | -11% | 1. Inverter 83 had a string 8 down since 11/27. It will be investigated during the next onsite visit. 2. Inverter 49 did not start production on 01/26. The technician investigated and found that the inverter was online but not communicating due to a Fault Protect 0130/090. Solectria will issue an RMA for the power head. The inverter has been tagged out and de-energized. 3. Inverter 42 did not start production on 01/29 reporting Bus Differential Fault. Technician investigated and found that the inverter was online but not communicating. Solectria processed an RMA. 4. Low generation due to rain/snow. | 1. SR093591 2. SR095984 3. SR096108
Sandwich | MA | 284645 | N/A |  |  | 295751 | -11106 | -3.755% | 1. PAD 4 is discharging at 15kW and CES performed calibration on 01/02. 2. The site was taken offline from 8:45 to 15:15 on 01/17 for SIM replacement. Afterward, the technician requested tech support to check production reporting issues on meters 3 and 4. AlsoEnergy confirmed PowerTrack settings were consistent across HEILA BESS Controllers 2, 3, and 4, indicating the issue is likely with the controllers. HEILA will now inspect remotely using the new SIM. | 1.SR095262 2.SR095545
Sturbridge Barn | MA | 75410.5 | 125791.1 | -50380.6 | -40.05% | 110058.4 | -34647.9 | -31.48% | 1. Site tripped offline and SEL Relay was opened on 01/02 at 18:00 later technician re-energized the relay at 08:15am on 01/03 2.Inverter 32 tripped offline at 13:30 on 01/25 due to "ARC Protection", later technician found and replaced rusty homerun MC connectors, and the inverter came back online at 10:30 on 01/27. 3. Low generation due to rain/snow. | 1.SR095261 2.SR095978
Sturbridge Garage | MA | 36683.75 | 59181.43 | -22497.68 | -38.01% | 55606.07 | -18922.32 | -34.03% | 1.Inverter 3 tripped offline at 12PM on 01/02 due to Bus(sum) over voltage fault and back online on 01/04. On 01/23 Technicians checked in and replaced RMA'd Inverter with new Inverter. Inverter was again offline from 01/24 due to stuck in standby mode and back online at 12PM on 01/27. 2.Site tripped offline at 17:48 and on battery mode, later auto-reclosed at 18:10 on 01/02. 3.Inverter 8 tripped offline at 10:30AM on 01/12 due to insulation resistance low fault and back online at 11:30AM on 01/13. 4. Low generation due to rain/snow. | 1.SR093378, SR096015 2.SR095260 3.SR095505
Halsey Valley | NY | 352603 | 438815.8 | -86212.8 | -19.65% | 384000 | -31397 | -8.176% | 1.Inverter 13 was offline from 12/20/24 due to insulation resistance low fault and after technician powered on, inverter back online at 9:30AM on 01/16/25. 2.Inverter 18, string 4 in CB18, was isolated due to poor voltage and a disconnected module caused by severe dirt and ice buildup in the MC4 connections. After inspection on 01/16, the technician replaced both MC4 connectors, reconnected the circuit, and powered on the inverter. It is now performing in line with its peers. 3. Low generation due to rain/snow. | 1.SR094997 2.SR094509
Hunt Creek | NY | 155889 | 294214.5 | -138325.5 | -47.02% | 228700 | -72811 | -31.84% | 1. Inverter 18 has multiple tripping events from 12/06/24 due to Floating capacitor voltage is high. 2.Site tripped offline at 07:00AM and after technician checked-in, site back online at 11:45 on 01/06. 3.Site tripped offline at 06:30AM and after technician closed the SEL Relay, site back online at 11:15 on 01/22. Inverters 2,3,4,5,6,8,10,14,15,16,17,19,22,25,27,28 and 29 are tripped offline at 09:15AM on 01/21 due to Grid Voltage unbalance and back online at 11:15AM on 01/22. 4.Inverters 5,23 and 27 tripped offline at 13:30 on 01/24 due to Grid voltage unbalance and back online on 01/25. 5. Low generation due to rain/snow. | 1.SR094254 2.SR093451 3.SR095801 4.SR095965
Smith Creek | NY | 264193 | 337115.3 | -72922.3 | -21.63% | 398598.4 | -134405.4 | -33.72% | 1.Site was taken offline from 10:45 to 16:45 on 01/06 due to technincian checked-in for hot spot remediation. 2. Inverters 1,3,6,12 and 27 tripped offline at 9:15AM on 01/21 due to Grid voltage unbalance and back online at 14:00 on 01/22. Site tripped offline at 06:30AM and after technician closed the SEL Relay, site back online at 14:00 on 01/22. | 1.SR095332 2.SR095805
Bradford - 256 Presidential Dr | MA | 306816.5 | 339000 | -32183.5 | -9.494% | 401656.5 | -94840 | -23.61% | 1.Inverter 128 was not communicating since 12/07/24. Communications card has been RMA'd and will be replaced during a combined dispatch. 2. Low generation due to rain/snow. | 1.SR096051
Charlton – 111 Brookfield Road - Bus Lot | MA | 36616 | 27710.0996 | 8905.9004 | 32.14% | 56965.72 | -20349.72 | -35.72% | 1. Site stopped communicating at 1:25AM on 01/29 and on 03/31 technician powercycled the DAS comms were restored. 2. Low generation due to rain/snow. | 1. SR096103
Charlton – 154 Center Depot Road KMARD | MA | 31310 | 53271.4949 | -21961.4949 | -41.23% | 54358.81 | -23048.81 | -42.4% | 1. Low generation due to weather/snow.
Charlton – 142A Brookfield Rd (Mitchell) | MA | 35707.4359 | 52376.025 | -16668.5891 | -31.82% | 57257.31 | -21549.8741 | -37.64% | 1. Site lost communication on 01/10 and comms were back on 01/16 after technician powercycled DAS. 2. Low generation due to rain/snow. | 1. SR095421
Great Barrington – 3 Nolan Drive | MA | 55040 | 97230.9306 | -42190.9306 | -43.39% | 112112.88 | -57072.88 | -50.91% | 1. Low generation due to weather/snow.
Stockbridge – 92 State Line Road Truck Stop | MA | 86169 | 190974.8474 | -104805.8474 | -54.88% | 216276.62 | -130107.62 | -60.16% | 1. Low generation due to weather/snow.
NY: New Windsor - Moores Hill | NY

## Feb
Lodestar |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 4097242.2184 | 5706989.1617 | -1609746.9433 | -28.21% | 5844278.04 | -1747035.8216 | -29.89% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT | 65600 | 127981.8 | -62381.8 | -48.74% | 118820.5 | -53220.5 | -44.79% | 1. Combiner Boxes 1.2 (DCP 1), 1.3 (DCP 7), 1.5 (DCP 14), 1.7 (DCP 10), 1.10 (DCP 4), 1.11 (DCP 11), and 1.15 (DCP 12) have been offline since 12/22. On 02/10, technician refitted them with a new contactor. Except for 1.2 (DCP 1), all combiner boxes came back online at 12:15 PM. 2. Low generation due to weather/snow. | 1.SR095215
Bunce | CT | 152247 | 205046.7 | -52799.7 | -25.75% | N/A |  |  | 1.Site was taken offline from 13:00 to 14:45 on 02/22 due to planned outage. 2. The site is experiencing multiple trips due to voltage fluctuations. Whenever the meter voltage drops below 610V, the site trips, and when the voltage returns to the nominal value, the site comes back online. This phenomenon has been occurring since Eversource performed maintenance on 02/22. Site production returned to normal on 02/27 after Eversource was dispatched on 02/26. | 1.SR097327 2.SR097832 | SR097832
Norcap North | CT | 196301.5 | 283245.5 | -86944 | -30.7% | 212347.1 | -16045.6 | -7.556% | 1.Inverter 25 experienced multiple offline incidents throughout the month due to a bus differential high fault and was subsequently RMA'd by Solectria. On 02/26, technicians replaced the RMA'd inverter with a new unit and inverter started producing in line with its peers. 2. Inverter 1 was offline on 02/16 and 02/17 due to a bus differential high fault and came back online on 02/18. It went offline again from 02/20 to 02/23 and on 02/27 and 02/28 due to the same fault. Solectria initiated the RMA process for the inverter on 02/21. 3. Low generation due to rain/snow. | 1.SR096190 2.SR097171, SR097549 & SR097792 | SR097171 | SR097549 | SR097792
Norcap South | CT | 217072.5 | 306757.9 | -89685.4 | -29.24% | 202120.5 | 14952 | 7.398% | 1. Inverter 36 started late for production on 02/01, 02/04, 02/07 and was offline on 02/13 & 02/27 due to Insulation Resistance Low fault. Self-resolved on 02/28. 2. Low generation due to rain/snow. | 1.SR096465
Platt Hill | CT | 142609.255 | 252288 | -109678.745 | -43.47% | 273596.9 | -130987.645 | -47.88% | 1.Site was tripped offline at 13:30 on 02/04 due to main breaker trip and back online at 10:30 on 02/05 after tehnician closed the breaker. Again site tripped offline at 20:00 on 02/16 and after technician reset main breaker site back online at 11:30 on 02/18. 2. Low generation due to rain/snow. | 1.SR096295
Powder Hill | CT | 173406 | 236232.6 | -62826.6 | -26.6% | 178140 | -4734 | -2.657% | 1.Site was tripped offline on battery mode from 12:45 to 13:30 on 02/07. 2.Three CT's of inverter 7 were RMA'd from 01/28. Received parts and need to dispatch. | 1.SR096471 2.SR095513 | SR095513
Sand Road | CT | 157864 | 194906.2 | -37042.2 | -19.01% | 179737 | -21873 | -12.17% | 1.Site was taken offline from 10:45 to 11:45 on 02/21 due to technicians checked in to collect DGA samples. 2.Site stopped communicating at 12PM on 02/22 and back online at 08:15 on 02/23 after technician reset main breaker and SEL relay. 3.Inverter 9 started late for production at 13:00 on 02/27 due to insulation Fault. | 1.SR097562 2.SR097648 3.SR097870 | SR097648 | SR097870
Suffield | CT | 160474 | 229753.5 | -69279.5 | -30.15% | 221930.9 | -61456.9 | -27.69% | 1.On 02/26, the technician replaced CB 14's String 9 (faulty) and String 13 (open circuit). 2. Low generation due to rain/snow | 1.SR089923, SR090122 | SR090122
Ashby-Duffy | MA | 85456 | 296805.6 | -211349.6 | -71.21% | 209076.1 | -123620.1 | -59.13% | 1.Inverter 2 was offline since 12/19 and will remains offline until the ground is unfrozen. 2.Inverter 39 string 5 blew a fuse and requires underground wiring replacement. Work will be scheduled once the ground thaws. 3. Low generation due to rain/snow. | 1. SR093777,SR097797 2.SR094302, SR097796 | SR097797 | SR094302 | SR097796
Ashland | MA | 115560 | 235192.7 | -119632.7 | -50.87% | 225868 | -110308 | -48.84% | 1.Inverter 49 was being RMA'D since 10/16/23. 2.Inverter 67 was being RMA'd. 3.Inverter 57 was being RMA'd. 4.Inverter 12 was offline intermittently whole month and being RMA'd. 5.Inverter 16 was offline since 11/13 due to Arc Protection and being RMA'd. 6.Inverter 66 is bearly producing due to protect 0260 fault from 01/30 and back to normal after technician replaced MC4 connectors that were causing arc fault on 02/04. 7.Inverter 21 was offline on 02/06 due to ARC Protection fault and back online at 11:45 on 02/07 after technician replaced blown DC fuse and fuse holders. 8.Inverter 24 has multiple trip events through out the month due to Insulation Resistance Low fault. 9. Low generation due to rain/snow. | 1.SR088449 2.SR088450 3.SR091962 4.SR093117, SR097799 5.SR095816 6.SR096271 7.SR096370 8.SR097060 | SR088450 | SR091962 | SR093117 | SR097799 | SR095816 | SR096271 | SR096370 | SR097060
Barrington | MA | 22100 | 27320.93 | -5220.93 | -19.11% | 54460 | -32360 | -59.42% | 1. Low generation due to rain/snow.
Bedford - 205 Burlington Rd | MA | 6760 | N/A |  |  | N/A
Billerica - 6 Cook Street | MA | 5612 | N/A |  |  | N/A
Billerica - 780 Boston Road | MA | 6214 | N/A |  |  | N/A |  |  | 1.Inverter 4 was offline on 02/27 due to Insulation resistance too low fault and resumed production at 13:40 on 02/28. | 1.SR097899
Cheshire | MA | 16209.0436 | 46433.28 | -30224.2364 | -65.09% | 34106.99 | -17897.9464 | -52.48% | 1. Low generation due to rain/snow.
Lilly Lane | MA | 70582.5 | 102338.9 | -31756.4 | -31.03% | 133421.2 | -62838.7 | -47.1% | 1.Inverter 61 was being RMA'd from 01/22. 2.Inverter 67 was offline from 11:15 to 15:30 on 02/17 due to a grid over-frequency fault. On 02/26, it went offline again due to an insulation resistance low fault. The technician repaired broken MC4 connectors and cleared an arc fault, restoring the inverter online at 13:45 on 02/27. 3.On 02/24, Inverter 69 was offline due to an insulation resistance low fault. The technician repaired the jumper cable and ensured sufficient slack, restoring the inverter online at 14:30 on 02/24. 4.Inverter 50 was offline on 02/25 due to Insulation resistance low fault and back online at 13:15 on 02/26 after technician cleared the arc fault and repaired the bad MC4 connections. 5. Low generation due to rain/snow. | 1.SR095846, SR097795 2.SR097191 3.SR097690 4.SR097747 | SR097795 | SR097191 | SR097690 | SR097747
Monument Valley | MA | 117707.1058 | 46997.43 | 70709.6758 | 150.5% | N/A |  |  | 1.Site was taken offline from 8:00 to 9:15 on 02/21. Technicians was onsite to collect DGA samples. 2. Expected generation values are lower than actual values. AlsoEnergy stated that expected values are calculated based on inverter data and weather conditions and recommended an onsite visit. However, due to communication issues with the inverters, the expected values remain low. | 1.SR097561 2. SR087370 | SR087370
Nationwide | MA | 52369 | 335928.3 | -283559.3 | -84.41% | 339349.6 | -286980.6 | -84.57% | 1. Inverter 13 was offline on 02/27 and back online on 02/28. 2. Low generation due to rain/snow. | 1.SR097881
Pulpit Hill | MA | 334214.25 | 482625.5 | -148411.25 | -30.75% | 489731.3 | -155517.05 | -31.76% | 1.Inverter 83 had a string 8 down since 11/27. It will be investigated during the next onsite visit. 2.Inverter 49 did not start production on 01/26. The technician investigated and found that the inverter was online but not communicating due to a Fault Protect 0130/090. Solectria will issue an RMA for the power head. The inverter has been tagged out and de-energized. 3. Inverter 42 did not start production on 01/29 reporting Bus Differential Fault. Technician investigated and found that the inverter was online but not communicating. Solectria processed an RMA. 4. Low generation due to rain/snow. | 1.SR093591, SR097798 2.SR095984 3.SR096108, SR097793 | SR097798 | SR095984 | SR096108 | SR097793
Sandwich | MA | 315624 | N/A |  |  | 367963 | -52339 | -14.22% | 1.Inverters on Pad 4 are all showing some ground/communication faults within the XGI portal from 02/11 and self resolved on 02/24. 2.On 2/20, Pad 1&4 are showing active fault. Later pad 1 got self- resolved and Pad 4 was reset by CES. 3.On 02/20, the technician checked in to take DC measurements on Pad 4 but had to check out due to inclement weather. On 02/24, the technician returned to troubleshoot incorrect meter values for Pad 4 caused by damaged conductor insulation and a loose terminal jumper near the Verivolt IsoBlock. The technician repaired the damage, restored the connection, and confirmed correct voltage and amperage readings on the Pad 4 meter. The technician also discovered that Pad 3's Power Limiting factor was set to 81.4% instead of 100%. With CES' approval, the setting was adjusted to 100%, increasing inverter output to 166kW. The technician then power cycled the Pad 3 Heila Controller and worked with CES to reset site mode settings, restoring automatic system dispatch. The technician monitored the site for 30 minutes to confirm normal operation. | 1.SR096680 2.SR097547 3.SR095262 | SR097547 | SR095262
Sturbridge Barn | MA | 77009 | 121747.9 | -44738.9 | -36.75% | 133486.9 | -56477.9 | -42.31% | 1.Inverter 32 was offline on 02/14 due to an ARC protection fault and came back online at 13:15 on 02/19 after a technician swapped the ARC board between Inverters 31 and 32 to check if the fault followed the board. Both inverters are online and producing. 2.Site tripped offline and was on battery mode at 11:00 on 02/17 and back online at 10:30 on 02/18 after technician closed the reclosure. 3. Low generation due to rain/snow. | 1.SR097066 2.SR097198 | SR097198
Sturbridge Garage | MA | 36142.5 | 58118.59 | -21976.09 | -37.81% | 65907.13 | -29764.63 | -45.16% | 1. Low generation due to weather/snow.
Halsey Valley | NY | 433614 | 486830.4 | -53216.4 | -10.93% | 528000 | -94386 | -17.88% | 1. Low generation due to weather/snow.
Hunt Creek | NY | 238580 | 348340.5 | -109760.5 | -31.51% | 340300 | -101720 | -29.89% | 1. Inverter 27 was tripped offline from 9AM to 10:45AM on 02/17 due to Grid voltage unbalance fault. 2.All inverters tripped offline at 14:15 on 02/15 due to Grid voltage unbalance fault and back online on 02/16. Again all inverters tripped offline between 9:15 to 13:00 on 02/23 due to Grid voltage unbalance fault. 3. Inverter 18 was ofline since 12/08/24 due to floating capacitor high voltage. Will investigate next time onsite. | 1.SR097182 2.SR097150 3. SR094254 | SR097150 | SR094254
Smith Creek | NY | 329908 | 395368.9 | -65460.9 | -16.56% | 472752.2 | -142844.2 | -30.22% | 1.All inverters tripped offline at 14:15 on 02/15 due to Grid voltage unbalance fault and back online on 02/16. Again all inverters tripped offline between 9:15 to 13:00 on 02/23 due to Grid voltage unbalance fault. | 1.SR097151
Bradford - 256 Presidential Dr | MA | 341831 | 434992 | -93161 | -21.42% | 529201.8 | -187370.8 | -35.41% | 1.Inverter 128 was not communicating since 12/07/24. Communications card has been RMA'd and will be replaced during a combined dispatch. 2.Inverter 84 was not communicating from 02/02, after tehnician powercycled inverter regained communication on 02/24 at 11:00AM. | 1.SR096051,SR097794 2.SR097657 | SR097794 | SR097657
Charlton – 111 Brookfield Road - Bus Lot | MA | 33288 | 40369.2841 | -7081.2841 | -17.54% | 61889.87 | -28601.87 | -46.21% | 1. Site stopped communicating on 02/10 and power factors able to troubleshoot the issue and comms were restored on 02/.12. 2. Site tripped offline at 11:20AM on 02/17 and technician re-energized the site and it is back online on 02/18. | 1. SR096287 2. SR097195 | SR097195
Charlton – 154 Center Depot Road KMARD | MA | 20320 | 53693.111 | -33373.111 | -62.16% | 59765.73 | -39445.73 | -66% | 1. Inverter 13 was not communicating from 07/30/24, based on meter inverter was offline. The inverter was RMA'd by QE solar on 02/26. 2. Site tripped offline at 11:00AM ON 02/17. On 02/18 technician closed the recloser and site was back online at 8:50AM. 3. Site stopped communicating at 9:30PM on 02/25 and comms were restored on 02/26 after DAS powercycled. 4. Low generation due to weather/snow. | 1. SR096880 2. SR097194 3. SR097744 | SR097194 | SR097744
Charlton – 142A Brookfield Rd (Mitchell) | MA | 33022.5641 | 58822.546 | -25799.9819 | -43.86% | 62829.33 | -29806.7659 | -47.44% | 1. Site stopped communicating on 02/01 and comms were restored on 02/04 after DAS powercycled. 2. Site stopped communicating at 6:30PM on 02/25 and comms were restored on 02/26 after DAS powercycled. 3. Low generation due to weather/snow. | 1. SR096242 2. SR097809 | SR097809
Great Barrington – 3 Nolan Drive | MA | 50410 | 106085.9679 | -55675.9679 | -52.48% | 123737.26 | -73327.26 | -59.26% | 1. Site stopped commnicating at 11:25AM on 02/14. On 02/18 technician found recloser open position and closed back. The site back online on the same day. 2. Site stopped communicating at 1:20PM on 02/23. Valuses are struck for inverters 1 to 7. Site comms restored on 02/25 but inverter 5 remains offline. On 02/26 technician investigated the issue and inverter was being RMA'd. 3. Low generation due to weather/snow. | 1. SR097148 2. SR097662 | SR097662
Stockbridge – 92 State Line Road Truck Stop | MA | 89135 | 192765.1228 | -103630.1228 | -53.76% | 225738.73 | -136603.73 | -60.51% | 1. Inverters 1 to 28 stopped communication at 07:00AM on 02/03, production can be verified at meter level. Communications were self resolved on 02/07 2. On 02/16, Phase A voltage dropped to 0V while current held steady at ~40A, indicating the meter wasn't capturing full inverter output. On 02/18, the technician found the recloser tripped and restored it, bringing Phase A voltage and current back to normal by 8:10 AM. 3. Inverter 7 tripped offline at 3:35PM on 02/14 and inverter 5 tripped offline at 1:55PM on 02/15. On 02/18 technician cleared faults for both inverters, inverter 7 back online at 9:45AM but inverter 5 remains offline. On 02/21 techncian reset the inverter 5 and it is back online at 2:10PM on the sameday. 4. Inverter 5 tripped offline at 4:40PM on 02/21. On 02/24 technician found inverter reporting arc fault and he isolated the string 4 and inverter back online at 8:50AM on the same day. 5. Inverter 7 tripped offline at 9:40AM on 02/25. On 02/26 technician troubleshooted and cleared the fault, inverter back online at 3:40PM on the sameday. 6. Inverter 44 tripped offline at 14:40 due to "PF 100 production down" on 02/26. On 02/28 technician reset the inverter and it is back online at 2:00PM. 7. Low generation due to weather/snow. | 1. SR096270 2. SR097154 3. SR097154, SR097155, SR097338 4. SR097338, SR097654 5. SR097807 6. SR097851 | SR097154 | SR097154 | SR097155 | SR097338 | SR097338 | SR097654 | SR097807 | SR097851
NY: New Windsor - Moores Hill | NY

## Mar
Lodestar |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 8516922.4648 | 7921237.0293 | 595685.4354 | 7.52% | 7889841.93 | 627080.5348 | 7.948% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT | 160256 | 162863 | -2607 | -1.601% | 164231 | -3975 | -2.42% | 1. Combiner box 1.2(DCP-1) is offline since 12/22/24. On 03/13 technician troubleshooted by plugging CT measurement wire and combiner box resumed communicating at 11:00AM. | 1. SR098455, SR095215 | SR095215
Bunce | CT | 301622.5 | 282807.6 | 18814.9 | 6.653% | NA
Norcap North | CT | 306603.5 | 329886.4 | -23282.9 | -7.058% | 305427 | 1176.5 | 0.3852% | 1. Inverter 1 was experienced multiple tripping events in previous month due to bus differential high fault and solectria initiated an RMA. On 03/06 technician replaced inverter with a new one and it is started producing from 9:45AM on the same day. 2. Site tripped offline at 14:15 on 03/11 and back online after technician re-energizing at 17:15 on the same day. 3. The site had a brief outage between 14:40 to 15:03 on 03/22. | 1. SR097792 2. SR098395 3. SR098889 | SR098395 | SR098889
Norcap South | CT | 320974.5 | 349780.3 | -28805.8 | -8.235% | 298676.2 | 22298.3 | 7.466% | 1.Inverter 36 experienced late start and offline issues throughout the month. The inverter typically self-resolves on alternate days. On 03/21, a technician performed troubleshooting and brought the inverter back online. 2. The site had a brief outage between 14:40 to 15:03 on 03/22. | 1. SR096465 2. SR098890 | SR098890
Platt Hill | CT | 300382 | 344310.9 | -43928.9 | -12.76% | 352217.3 | -51835.3 | -14.72% | 1. Site tripped offline at 23:45 on 03/06. On 03/08 after re-energize the site was back online at 10:30AM. 2. Site tripped offline at 12:30PM on 03/11. On 03/12 technician reset the main breaker and site back online at 9:00AM. 3. Site tripped offline at 9:30AM on 03/21 and later technician re-energized the site at 14:00 on the same day. 4. Site tripped offline at 6:15AM on 03/24. On 03/25 technician re-energized and it is back online at 10:15AM. 5. Inverter 5 started late for production at 12:30PM due to insulation fault on 03/31. | 1. SR098238 2. SR098398 3. SR098862 4. SR098926 5. SR099192 | SR098398 | SR098862 | SR098926 | SR099192
Powder Hill | CT | 305500 | 302824.2 | 2675.8 | 0.8836% | 233148 | 72352 | 31.03% | 1. Three CTs for Inverter 7 were RMA'd on 01/28. On 03/12, the site was offline from 11:00 AM to 12:30 PM as a technician was onsite replacing the three CTs for Inverter 7. | 1. SR095513
Sand Road | CT | 319904 | 300950.2 | 18953.8 | 6.298% | 277950 | 41954 | 15.09%
Suffield | CT | 308891 | 293653.5 | 15237.5 | 5.189% | 315921.2 | -7030.2 | -2.225% | 1. Site stopped communicating at 18:30 on 03/28. On 03/29 technician found recloser in open state and phase A&B are faulted. Technician cleared the fault and closed the recloser, site back online at 13:15 on same day. | 1. SR099128
Ashby-Duffy | MA | 293392 | 387655.3 | -94263.3 | -24.32% | 281840.8 | 11551.2 | 4.098% | 1. Inverter 2 was offline since 12/19 and will remains offline until the ground is unfrozen. 2. Inverter 24 started late for the production at 10:00AM on 03/06 due to insulation fault. 3. Inverter 38 stopped communicating at 1:30AM from 03/11. Will investigate while next time onsite. 4. Inverters 43, 47, and 59 were derated by 4–5 kW each starting at 10:30 AM on 03/12 due to excessive temperature. On 03/19, technician attempted to troubleshoot the issue, but it was unsuccessful, and SMA RMA’d the fans for these inverters. On 03/28, the technician replaced the fans, but the issue persisted. Further testing with SMA indicated a likely power supply failure in these inverters, and the powerheads have been RMA’d. | 1. SR097797 2. SR098200 3. SR098383 4. SR098407 | SR098200 | SR098383 | SR098407
Ashland | MA | 290755.5 | 311890.3 | -21134.8 | -6.776% | 320735.9 | -29980.4 | -9.347% | 1.Inverter 49 was being RMA'D since 10/16/23. 2.Inverter 67 was being RMA'd. 3.Inverter 57 was being RMA'd. 4.Inverter 12 was being RMA'd. 5.Inverter 16 was offline since 11/13 due to Arc Protection and being RMA'd. 6. Inverter 24 experiencing tripping events since 02/14. On 03/04 technician troubleshooted the issue with solectria and issue has been resolved from 03/05. 7. Site was offline from 7:30AM to 10:45AM on 03/18 due to technician was onsite to collect transformer DGA samples. 8. Inverters 40 to 46 tripped offline at 1:45PM due to grid voltage out of range. On 03/12 technician swapped the leads with the breaaker and inverters back online at 10:4AM on the same day. 9. Inverter 37 was started late for the production at 10:45AM on 03/18 due to insulation fault. 10. Inverter 65 started late for the production at 15:00 on 03/20 due to Insuation resistance low. | 1. SR088450 2. SR088450 3.SR091962 4.SR093117, SR097799 5. SR095816 6. SR097060 7. SR097563 8. SR098396 9. SR098679 10. SR098821 | SR088450 | SR091962 | SR093117 | SR097799 | SR095816 | SR097060 | SR097563 | SR098396 | SR098679 | SR098821
Barrington | MA | 68255 | 16516.58 | 51738.42 | 313.3% | 68910 | -655 | -0.9505% | 1. During morning hours weather station reporting low irradiance values. Working with Also energy and they are investigating. | 1. SR099616
Bedford - 205 Burlington Rd | MA | 35447 | NA |  |  | NA
Billerica - 6 Cook Street | MA | 31709 | NA |  |  | NA
Billerica - 780 Boston Road | MA | 36026 | NA |  |  | NA
Cheshire | MA | 69411.7888 | 71712.76 | -2300.9712 | -3.209% | 47518.1 | 21893.6888 | 46.07%
Lilly Lane | MA | 150553 | 142040.5 | 8512.5 | 5.993% | 159655.1 | -9102.1 | -5.701% | 1.Inverter 61 was being RMA'd from 01/22. | 1. SR097795
Monument Valley | MA | 294118.6792 | 66602.86 | 227515.8192 | 341.6% | NA |  |  | 1. Site stopped communicating at 3:00AM on 03/07. Technician found recloser open and after a reset site was back online at 13:45 on the same day. 2. Expected generation values are lower than actual values. AlsoEnergy stated that expected values are calculated based on inverter data and weather conditions and recommended an onsite visit. However, due to communication issues with the inverters, the expected values remain low. | 1. SR098250 2. SR087370 | SR087370
Nationwide | MA | 525648 | 470640.1 | 55007.9 | 11.69% | 455456 | 70192 | 15.41% | 1.Inverter 13 experienced late start issues intermittently throughout the month. | 1. SR097881
Pulpit Hill | MA | 649245.25 | 627559.4 | 21685.85 | 3.456% | 660610.7 | -11365.45 | -1.72% | 1. Inverter 49 did not start production on 01/26. The powerhead was being RMA'd since 01/29. On 03/04 technician replaced inverter 49 and it was back online at 14:45. 2. Inverter 42 was RMA'd since 02/26. On 03/04 technician replaced inverter and it is back online at 02:00PM. 3. The site was offline from 11:00AM to 13:45 due to technician was onsite for inverters 42 and 49 replacement on 03/04. 4. Inverter 83 had a string 8 down since 11/27. It will be investigated during the next onsite visit. | 1. SR095984 2. SR097793 3. SR097793, SR095984 4. SR093591, SR097798 | SR097793 | SR097793 | SR095984 | SR093591 | SR097798
Sandwich | MA | 353596 | NA |  |  | 495038 | -141442 | -28.57% | 1. Site tripped offline at 14:00 on 03/07 and started for production on 03/08. As per Erik site was back online by reset from sandwich. 2. PAD 4 tripped offline at 17:30 on 03/11 and remained offline throughout the month. Interface board and DSP board need to be replaced. | 1. SR098286 2. SR098405 | SR098405
Sturbridge Barn | MA | 154300 | 157826.2 | -3526.2 | -2.234% | 172343 | -18043 | -10.47% | 1. Inverter 25 tripped offline at 14:45 on 03/02. On 03/03, a technician worked with Solectria support and removed the parallel bus bar to put the inverter in independent mode. The inverter came back online at 14:30 on the same day. 2. Site tripped offline at 1:00AM and later technician re-energized the site and it was back online at 8:00AM. 3. Inverter 32 tripped offline at 13:00 on 03/06 and back online at 6:30AM on 03/07 after a reset. | 1. SR097966 2. SR098186 3. SR098223 | SR098186 | SR098223
Sturbridge Garage | MA | 77575.25 | 75875.88 | 1699.37 | 2.24% | 78866.2 | -1290.95 | -1.637%
Halsey Valley | NY | 746709 | 764179.6 | -17470.6 | -2.286% | 697000 | 49709 | 7.132% | 1. Site tripped offline at 9:00AM and back online at 2:00PM due to utility outage on 03/10. | 1. SR098333
Hunt Creek | NY | 543121 | 574757.3 | -31636.3 | -5.504% | 498900 | 44221 | 8.864% | 1. Inverter 18 was ofline since 12/08/24 due to floating capacitor high voltage. Will investigate next time onsite. 2. Inverters 5,3 and 27 tripped offline at 15:20 due to Grid voltage unbalance. Inverters self resolved at 16:30 on 03/14. 3. Multiple inverters tripped offline due to Grid voltage unbalance at 13:30 on 03/08. Inveretrs self resolved at 16:00 on the sameday. 4. Inverter 27 tripped offline at 10:45AM and self-resolved back online at 16:00 on 03/09. 5. Multiple inverters tripped offline at 8:15 AM and self resolved at 11:00AM on 03/26. | 1. SR094254 2. SR095965 3. SR098301 4. SR098316 5. SR098993 | SR095965 | SR098301 | SR098316 | SR098993
Smith Creek | NY | 595618 | 619479.8 | -23861.8 | -3.852% | 602155.1 | -6537.1 | -1.086% | 1. Multiple inverters tripped offline due to Grid voltage unbalance at 13:30 on 03/08. Inveretrs self resolved at 16:00 on the sameday. | 1. SR098300
Bradford - 256 Presidential Dr | MA | 645415 | 608236.9071 | 37178.0929 | 6.112% | 670083.4 | -24668.4 | -3.681% | 1. Inverter 128 was not communicating since 12/07/24. Communications card has been RMA'd and will be replaced during a combined dispatch. 2. Site had brief outage in between 12:20PM to 12:25PM. But inverters 1 to 4, 42 and 104 was not came back online. Inverters self resolved and started for production on 03/08. 3. Inverters 1 to 55 stopped communicating at 12:45 on 03/14, production not confirmed. On 03/18 technician powercyled DAS and comms were restored. | 1. SR096051,SR097794, SR099300 2. SR098265 3. SR098601 | SR097794 | SR099300 | SR098265 | SR098601
Charlton – 111 Brookfield Road - Bus Lot | MA | 75634 | 60424.0006 | 15209.9994 | 25.17% | 80041.66 | -4407.66 | -5.507% | 1. Site was offline on 03/06 and later technician found SEL in open position and closed it. The site was back online at 1:35PM on the sameday. | 1. SR098211
Charlton – 154 Center Depot Road KMARD | MA | 54420 | 69917.3952 | -15497.3952 | -22.17% | 78110.62 | -23690.62 | -30.33% | 1. Inverter 13 was not communicating from 07/30/24, based on meter inverter was offline. The inverter was RMA'd by QE solar on 02/26. 2. Site was offline on 03/06 and later technician found SEL in open position and closed it. The site was back online at 12:25PM on the sameday. 3. Site lost communication on 03/18 and technician teoubleshooted the issue but comms issue persit. On 03/19 the site comms were back at 9:15AM. | 1. SR096880 2. SR098203 3. SR098685 | SR098203 | SR098685
Charlton – 142A Brookfield Rd (Mitchell) | MA | 70420 | 76380.4585 | -5960.4585 | -7.804% | 80313.94 | -9893.94 | -12.32% | 1. Inverter 1 is not communicating since 03/01. On 03/06 technician investigated but issue persist. Solectria has recommended replacing the powerhead to regain communication. | 1. SR098182
Great Barrington – 3 Nolan Drive | MA | 145285.4967 | 155216.5388 | -9931.0421 | -6.398% | 161684.64 | -16399.1433 | -10.14% | 1. Inverter 5 was being RMA'd since 02/26. On 03/26 technician replaced inverter 5 and it is back online and producing. 2. Inverter 14 was underproducing by 5kW compared to its peers. Will investigate next time onsite. 3. Inverter 24 tripped offline at 7:30AM on 03/13. On 03/14 technician investigated and found inverter was faulted with protect 90 and it was being RMA'd by solectria. 4. Inverters and meter stopped communicating from 5:00PM on 03/14. On 03/16 technician found site was online but no communication. On 03/26 technician worked with powerfactors and communications were regained. | 1. SR097843 2. SR098468 3. SR098503 4. SR098604 | SR098468 | SR098503 | SR098604
Stockbridge – 92 State Line Road Truck Stop | MA | 286134 | 297249.0491 | -11115.0491 | -3.739% | 333008.07 | -46874.07 | -14.08% | 1. Inverters 25 and 38 tripped offline at 8:05 reporting "PF100-production down" on 03/06 and self resolved and started for production on 03/07. 2. Inverter 44 didn't started for production on 03/12. On 03/14 technician re-energized and inverter was back online on the sameday. 3. Site stopped communicating at 6:30PM on 03/16. On 03/18 tech powercycled DAS and communications were restored. | 1. SR098230 2. SR098492 3. SR099148 | SR098492 | SR099148
NY: New Windsor - Moores Hill | NY

## Apr
Lodestar |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 8834355.5522 | 6753984.55 | 2080371.0022 | 30.8% | 7209999.91 | 1624355.6422 | 22.53% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT | 169174 | 167270.5 | 1903.5 | 1.138% | 171195.3 | -2021.3 | -1.181%
Bunce | CT | 296486.5 | 247773 | 48713.5 | 19.66% | N/A |  |  | 1.Site was offline from 03:26 on 04/16 to 09:15 on 04/17.Site was back online after the technician has Reset the SEL and closed in the Recloser. | 1.SR099883
Norcap North | CT | 313660 | 312566.3 | 1093.7 | 0.3499% | 324191.4 | -10531.4 | -3.249% | 1.Inverter 34 was offline from 04/01 to 13:15 on 04/02 and inverter was offline again on 04/03. On 04/04, a technician visited the site, noted that further troubleshooting is required, and confirmed the inverter is being RMAD.On 04/15 ,technicians swapped inverter 34 and it is back online at 11:30 on 04/15. 2.Inverter 13 was offline from 04/01. On 04/15, a technician visited the site and conducted troubleshooting in coordination with Solectria and advised that a firmware upgrade is necessary to proceed.Additional troubleshooting is required 3.Inverter 30 was offline from 04/09.On 04/14, a technician upon contacting Solectria, mentioned that inverter will remain offline and it was being RMA'D from 04/14.On 04/18,technician replaced rma'd inverter 30, new inverter is online and operating from 04/18. 4.Inverter 12 tripped offline at 14:45 on 04/18 due to an arc fault. The issue was cleared by a technician on 04/21, and the inverter was back online at 15:00 on 04/21 5.Inverter 1 is derating by 6kW from 14:00 on 04/19 due to an external fan error Additionally, inverter 7 is derated to 22 kW from 12:30 ,both issues got self resolved on 04/20 | 1.SR099262,SR099397,SR100147 2.SR099306,SR100148 3.SR099586,SR099921 4.SR099998 5.SR100023 | SR099397 | SR100147 | SR099306 | SR100148 | SR099586 | SR099921 | SR099998 | SR100023
Norcap South | CT | 330292 | 325075.9 | 5216.1 | 1.605% | 317829.1 | 12462.9 | 3.921% | 1.Inverter 55 derated to 24 kW starting at 12:30 on 04/19. On 04/20, a technician visited the site and noted that a higher PV output day is required to perform effective troubleshooting | 1.SR100021
Platt Hill | CT | 354320 | 354561.8 | -241.8 | -0.0682% | 382722.5 | -28402.5 | -7.421%
Powder Hill | CT | 328808 | 319049.2 | 9758.8 | 3.059% | 265344 | 63464 | 23.92% | 1. Inverter 9 is underperforming approximately 12kW and Inverter 9 tripped offline at 09:45 on 04/29,technician contacted solectria team and confirmed that it will need 3 CTS to bring back the inverter online | 1.SR100605,SR100633 | SR100633
Sand Road | CT | 324229 | 292043 | 32186 | 11.02% | 308583 | 15646 | 5.07% | 1.Site remained offline from 00:15 to 09:45 on 04/16.Site was back online after technician closed the breaker | 1.SR099859
Suffield | CT | 335727 | 319914.3 | 15812.7 | 4.943% | 334689.9 | 1037.1 | 0.3099%
Ashby-Duffy | MA | 312117 | 392272.6 | -80155.6 | -20.43% | 295108.7 | 17008.3 | 5.763% | 1. Inverter 2 was offline since 12/19 and will remains offline until the ground is unfrozen. 2. Inverter 24 started late for the production on 04/03 , 04/22 and 04/26 due to insulation fault. 3. Inverter 38 stopped communicating at 1:30AM from 03/11. Will investigate while next time onsite. 4. Inverters 43, 47, and 59 were derated by 4–5 kW each starting at 10:30 AM on 03/12, due to high temperatures. On 03/19, a technician attempted to troubleshoot the issue but was unsuccessful, and SMA issued RMAs for the fans. The fans were replaced on 03/28, but the issue persisted. Further testing with SMA indicated likely power supply failures, and the powerheads were RMA’d. On 04/02, the technician replaced the RMA’d units for INV 59 and INV 47; production and communication were successfully verified through SMA and AlsoEnergy. INV 43 was also replaced, but the replacement unit had a faulty communications hard drive. It was swapped with the original unit’s drive, and production and communication were verified through SMA and AlsoEnergy 5. Inverter 39 is underperforming 3kW compared to its peers. | 1. SR097797 2. SR098200 3. SR098383 4. SR098407, SR100146 5. SR099765 | SR098200 | SR098383 | SR098407 | SR100146 | SR099765
Ashland | MA | 331279.5 | 338334.4 | -7054.9 | -2.085% | 349936.7 | -18657.2 | -5.332% | 1.Inverter 49 was being RMA'D since 10/16/23. 2.Inverter 67 was being RMA'd. 3.Inverter 57 was being RMA'd. 4.Inverter 12 was being RMA'd. 5.Inverter 16 was offline since 11/13 due to Arc Protection and being RMA'd. 6. Inverter 65 started late for the production on 04/01 , 04/04 due to Insuation resistance low. 7. Inverter 56 modules are being undergoing replacment. 8. Inverter 46 had a delayed start on 04/08 . It tripped offline at 10:00 on 04/12 due to "Insulation Resistance Low," came back online at 11:00 on 04/14 , then tripped again at 13:45 on 04/26 with the same fault and returned online at 14:00 on 04/27 9. Inverter 8 having multiple tripping events on 04/03 and 04/22 . | 1. SR088449 2. SR088450 3.SR091962 4.SR093117, SR097799 5. SR095816 6. SR098821 7. SR099331 8. SR099519 9. SR100159 | SR088450 | SR091962 | SR093117 | SR097799 | SR095816 | SR098821 | SR099331 | SR099519 | SR100159
Barrington | MA | 69022.5 | 13735.87 | 55286.63 | 402.5% | 74480 | -5457.5 | -7.327% | 1. During the morning hours, the weather station has been reporting low irradiance values. We are currently working with AlsoEnergy, and they are investigating the issue. | 1. SR099616
Bedford - 205 Burlington Rd | MA | 40866 | N/A |  |  | N/A
Billerica - 6 Cook Street | MA | 37661 | N/A |  |  | N/A
Billerica - 780 Boston Road | MA | 42603 | N/A |  |  | N/A
Cheshire | MA | 72208.7112 | 75657.47 | -3448.7588 | -4.558% | 59684.24 | 12524.4712 | 20.98%
Lilly Lane | MA | 160353 | 155638.7 | 4714.3 | 3.029% | 178160.1 | -17807.1 | -9.995% | 1. The site tripped offline at 08:15 on 04/26 due to the "No AC voltage". After the technician arrived and opened the control cabinet of the Vista switch, it was found that the SEL relay had opened and tripped. Later, the technician closed the relay, and power was restored. The site is back online at 11:45 on 04/26. 2. Inverter 61 was being RMA'd from 01/22. | 1. SR100436 2. SR097795 | SR097795
Monument Valley | MA | 313209.505 | 61391.81 | 251817.695 | 410.2% | N/A |  |  | 1. Expected generation values are lower than actual values. AlsoEnergy stated that expected values are calculated based on inverter data and weather conditions and recommended an onsite visit. However, due to communication issues with the inverters, the expected values remain low. | 1. SR087370
Nationwide | MA | 553059 | 457546.6 | 95512.4 | 20.87% | 507015.9 | 46043.1 | 9.081% | 1.Inverter 16 tripped offline from 12:00 to 13:15 on 04/13 and later self-resolved. 2. The site was taken offline from 10:30 to 12:30 on 04/15 as the technician opened the recloser to isolate both transformers and later took DGA samples. 3. The site was offline at 14:00 on 04/22. When the technician arrived, he found that the recloser had tripped. After the technician reclosed the relay, the site came back online at 10:30 on 04/24. 4. Inverter 13 experienced late start issues intermittently throughout the month. | 1. SR099745 2. SR097560 3. SR100184 4. SR097881 | SR097560 | SR100184 | SR097881
Pulpit Hill | MA | 730135 | 693972.8 | 36162.2 | 5.211% | 685244.1 | 44890.9 | 6.551% | 1.Inverter 2 tripped offline at 09:45 on 04/18 and remained offline throughout the month. When the technician arrived on-site on 04/24, they stated that they would attempt to update the firmware remotely. Since that did not resolve the issue, they initiated an RMA for the inverter. 2. Inverter 9 tripped offline at 10:30 on 04/23 and came back online at 09:15 on 04/24. Additionally, inverters 33 and 37 tripped offline at 11:00 on 04/23. When the technician arrived on-site, he tested the AC and DC voltages, which appeared normal. Later, the inverters came back online at 05:45 on 04/24. 3. Inverters 81 and 83 were derating at 40 kW and reporting the alarm "External Fan Err - ExtFanerr." After the technician arrived on-site on 04 and completed the PM inspection for the day, they worked on inverters 81 and 83. The technician found blocked fans on both inverters, restored inverter 83 to full operation, and initiated an RMA for the fan on inverter 81. | 1. SR099993, SR100279, SR100391 2. SR100230 3. SR100353 | SR100279 | SR100391 | SR100230 | SR100353
Sandwich | MA | 342502 | N/A |  |  | 528189 | -185687 | -35.16% | 1. PAD 4 tripped offline at 17:30 on 03/11 and remained offline throughout the month. Interface board and DSP board need to be replaced. 2. HEILA BESS controller 2 has tripped offline at 16:15 on 04/15 and later CES has reset the pad 2 on 04/16 at 07:00. 3. Pad 3 is in charging from clipped solar and running at a reduced capability state from 04/21 4.BESS Pad 3 has tripped offline on 04/08, on 04/29 technician noted that Module 5 battery needs to be discharged to at least 73V DC. | 1. SR098405 2.SR099855 3.SR100063 4.SR100358 | SR099855 | SR100063 | SR100358
Sturbridge Barn | MA | 163275.5 | 162749 | 526.5 | 0.3235% | 176761.7 | -13486.2 | -7.63% | 1. Site tripped offline at 08:15 on 04/26 due to no AC voltage and later technician reenergized the site. Site is back online at 12:15 on 04/26. | 1. SR100435
Sturbridge Garage | MA | 82222.5 | 78086.2 | 4136.3 | 5.297% | 88006.27 | -5783.77 | -6.572% | 1. Site tripped offline at 8:15 on 04/26 and later back online by auto reclose at 10:00 on 04/26. 2. Inverter 2 was offline on 04/27 and later back online on 04/28. 3. Inverter 1 was deenrgized at 10:45 and later reernergized at 15:15 due to technician on site. | 1.SR100437 2.SR100463 3. PM8093 | SR100463
Halsey Valley | NY | 760486.28 | 784321.5 | -23835.22 | -3.039% | 868000 | -107513.72 | -12.39% | 1. The site tripped offline at 08:50 on 04/20 due to a main breaker trip. A technician later closed the relay on site on 04/21, and the site came back online at 09:45 on 04/21. 2. Site tripped offline at 00:30 on 04/28 due to utility outage and later utility outage has been resolved and site is back online at 01:15 on 04/28. | 1.SR100033 2.SR100475 | SR100475
Hunt Creek | NY | 561177 | 576760.4 | -15583.4 | -2.702% | 629400 | -68223 | -10.84% | 1.Inverter 18 was ofline since 12/08/24 due to floating capacitor high voltage. Will investigate next time onsite. | 1. SR094254
Smith Creek | NY | 609919 | 625263.2 | -15344.2 | -2.454% | 665458 | -55539 | -8.346%
Bradford - 256 Presidential Dr | MA | 627768.989 | N/A |  |  | N/A |  |  | 1. Pad 1 tripped offline at 08:00 on 04/04.On 04/09, a technician closed the relay and pad 1 was back online at 09:00 on 04/009 2. Inverters 24 and 114 are derating by 16kW each compared to its peers throughout the month | 1.SR099534 2.SR101357 | SR101357
Charlton – 111 Brookfield Road - Bus Lot | MA | 80771.1 | N/A |  |  | N/A |  |  | 1. Inverter 4 has been offline since 04/19 due to an arc fault. On 04/21 , the technician checked AC/DC voltages and found no issues. In the field, a damaged panel on String 6 was identified as the likely cause. The technician bypassed the panel and cleared the fault brought back online at 09:00 the same day. 2. Site tripped offline at 08:10 on 04/26 due to "Grid line voltage out of range." Upon arrival, the technician found the SEL relay in the OPEN position. After confirming it was safe, the relay was closed at the SEL control board. Power was restored, and the site is back online at 13:00 the same day. | 1. SR100018 2. SR100440 | SR100440
Charlton – 154 Center Depot Road KMARD | MA | 70886.1 | N/A |  |  | N/A |  |  | 1. Site was offline at 08:10 on 04/26 due to the grid line voltage out of range. A technician closed the relay, and the site came back online at 13:00 on 04/26. 2. Inverter 4 was offline from 04/30 due to Problem with energy production. | 1.SR100441 2.SR100710 | SR100710
Charlton – 142A Brookfield Rd (Mitchell) | MA | 73137.9 | N/A |  |  | N/A
Great Barrington – 3 Nolan Drive | MA | 141021.6 | N/A |  |  | N/A |  |  | 1. Inverter 14 was underproducing by 5kW compared to its peers. Will investigate next time onsite. 2. Inverter 24 offline on 04/30 due to "Bus(sum) Over Voltage Fault (Fault0130)" and remained offline through the month. Powerhead replacement is required to bring it back online. 3. Site stopped communicating at 13:00 on 04/05. On 04/06, the technician found the site was producing power but not communicating with Powerdash. The DIGI modem had no cell signal. Power cycling did not restore signal. After contacting Powerdash support, the technician removed the unused external antenna, checked the connector, and repositioned the internal antenna away from the metal enclosure. The SIM card was reinserted and the modem power cycled again, restoring signal to 3/5 bars. Powerdash confirmed all equipment was back online and stated that if the issue reoccures, they will provide an external antenna replacement. 4. Inverter 18 tripped offline at 16:00 on 04/09 and remained offline through the month. On 04/16, the technician found the inverter offline with Fault 0010. AC and DC voltages were within normal ranges (Strings 1–10: 707–712 VDC). Solectria support advised changing IdcMax(mA) from 216 to 398, but the fault reappeared. Solectria is reviewing photos to determine if the inverter will be RMA’d. A return visit is required once the replacement unit arrives. 5. Site has 4 meters; 2 record the bulk of production. RGM 1 is reporting 0 kW, and RGM 2 is showing low production. | 1. SR098468 2. SR098503, SR099298 3. SR099438 4. SR099815, SR099920 5. SR101029 | SR098503 | SR099298 | SR099438 | SR099815 | SR099920 | SR101029
Stockbridge – 92 State Line Road Truck Stop | MA | 205976.867 | N/A |  |  | N/A |  |  | 1. Site tripped offline on 04/22 at 11:00 AM due to equipment fault and critical alarm. Technician confirmed utility power was present and found the customer recloser open. No breakers were tripped, and it was safe to re-energize. The technician closed the recloser, and equipment came back online. Communications and production were confirmed by the Ameresco monitoring team. Site was restored at 16:00 the same day 2. Site stopped communicating at 06:00 on 04/12. On 04/15, the technician found the entire site offline with no visible damage. The site recloser was closed, and the site was back online by 12:00 PM, producing and communicating normally. It is recommended to replace the 5-year-old recloser batteries and perform a full site inspection. 3. Inverter 38 tripped offline at 8:05am on 04/03 due to an PF100 Production Down and resumed production at 5:30pm 04/04. | 1. SR100140 2. SR099806 3. SR099359 | SR099806 | SR099359
NY: New Windsor - Moores Hill | NY

## May
Lodestar |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 8563110.6215 | 6128708.66 | 2434401.9615 | 39.72% | 8159055.43 | 404055.1915 | 4.952% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT | 146345 | 151700 | -5355 | -3.53% | 187719.6 | -41374.6 | -22.04% | 1.Site tripped offline at 15:40 on 05/03 and later self resolved and back online at 16:15 on the same day 2.Combiner box DCP 1.16 is offline from 05/13 and back online at 11:15 on 05/14 after technician has reset the combiner box. Issue reocurred on 05/15.On 05/20,technician found Combiner 16 was producing but continues to read erroneous values. This is indicating a faulty CT in the recombiner that would need further troubleshooting or replacement. 3. Site was offline from 09:00 to 11:00 on 05/20 as technicians were on site for preventive maintanance | 1.SR100967 2.SR101378,SR101504 3.SR101739,PM8010 | SR101378 | SR101504 | SR101739
Bunce | CT | 298241.5 | 170854.3 | 127387.2 | 74.56% | 0 | 298241.5 |  | 1.The weather station's module and ambient temperature readings have been stuck at 184.95°F and 120°F, respectively, since 05/02.Dispatch has been scheduled for the following month. 2. Inverter 15 tripped offline at 9:45 on 05/30 due to grid voltage imbalance and remained offline for rest of the month.Dispatch has been scheduled for the following month. 3.Site was offline from 09:28 to 09:50 on 05/23 | 1.SR101404 2.SR102179 | SR102179
Norcap North | CT | 301406 | 279733 | 21673 | 7.748% | 361445.6 | -60039.6 | -16.61% | 1.Inverter 1 was derating at 40 kW since 05/02 due to an external fan fault. During a site visit on 05/08, the technician confirmed the fan was non-operational and indicated that further troubleshooting is necessary 2. Inverter 12 tripped offline at 10:00 on 05/27 and back online at 13:15 on 05/29 inverter back online after technician coordinated with Solectria for troubleshooting, during which the arc fault was cleared. 3.Inverter 18 was derating by 20kW from 05/28 due to external fan fault.Dispatch has been scheduled for the following month. 4.Inverter 26 was derated constantly at 40kW and due to External fan fault on 05/07.Issue got resolved on 05/08 after technician cleared the fan faults | 1.SR100943 2.SR101960 3.SR102051 4.SR101111 | SR101960 | SR102051 | SR101111
Norcap South | CT | 311807 | 292824.4 | 18982.6 | 6.483% | 353736.8 | -41929.8 | -11.85%
Platt Hill | CT | 325672 | 333533.1 | -7861.1 | -2.357% | 419927.5 | -94255.5 | -22.45% | 1.Site tripped offline at 15:40 on 05/03 and back online at 10:15 on 05/05.Site was back online after technician has reset and closed in the main AC breaker. | 1.SR100968
Powder Hill | CT | 299984 | 301833.2 | -1849.2 | -0.6127% | 285876 | 14108 | 4.935% | 1.Inverter 9 has been offline since 05/01. During a site visit on 04/30, the technician attempted a replacement, but the unit faulted again. The inverter will remain offline until the necessary parts are procured 2.Inverter 12 is underproducing by about 12kw since 5/13.Dispatch has been scheduled for the following month. | 1.SR100633 2.SR102083 | SR102083
Sand Road | CT | 311887.9505 | 267765.4 | 44122.5505 | 16.48% | 345518 | -33630.0495 | -9.733% | 1.Site was offline from 09:28 on 05/23 to 14:15 on 05/24 as technicians were on site for preventive maintanance | 1.PM8112
Suffield | CT | 309689 | 293001.3 | 16687.7 | 5.695% | 370616.2 | -60927.2 | -16.44% | 1.low production/generation due to rain on 05/05,05/06 and 05/09
Ashby-Duffy | MA | 278428 | 317015 | -38587 | -12.17% | 346494.4 | -68066.4 | -19.64% | 1.Inverter 39 is underproducing by about 5 kW .Dispatch scheduled in the following month 2. Inverter 24 was offline for most of the days of the month and often starts late 3.Inveters 1, 2, 6, 8, 22, 35, 38, 44, 46, 48, 49, 50, 51, 52 tripped offline at 14:45 on 05/31 with arc faults.Dispatch has been scheduled for the following month. | 1.SR099765 2.SR101869 3.SR102226 | SR101869 | SR102226
Ashland | MA | 297877.5 | 302492.5 | -4615 | -1.526% | 395984.4 | -98106.9 | -24.78% | 1.Inverter 49 was being RMA'D since 10/16/23. 2.Inverter 67 was being RMA'd. 3.Inverter 57 was being RMA'd. 4.Inverter 12 was being RMA'd. 5.Inverter 16 was offline since 11/13 due to Arc Protection and being RMA'd. 6.Technicians resumed delamination checks from Row 18, marking Rows 19–23 with 2,111 faulty modules logged. Additional visits are needed to complete the field. 7.Inverters 30, 46 and 64 started late for production at 10:50 on 05/04 ,later self resolved. 8. Inverter 9 and 46 were offline on 05/06 to 14:30 on 05/07 due to isolation fault.Issue got self resolved | 1.SR088449 2.SR088450,SR102089 3.SR091962 4.SR097799,SR093117 5.SR095816 6.SR099331,SR101423 7.SR100982 8.SR101104 | SR088450 | SR102089 | SR091962 | SR097799 | SR093117 | SR095816 | SR099331 | SR101423 | SR100982 | SR101104
Barrington | MA | 68376.5 | 37937.87 | 30438.63 | 80.23% | 88630 | -20253.5 | -22.85% | 1.The weather station has been reporting very low values from morning to midday from 02/28/25.On 05/14,technician found sensor had fallen down and reattached.Weather station issue was resolved since then. 2.Inverter 2 is derated and constantly producing 200kW from 05/08.On 05/14,issue got resolved after technician has troubleshoot the isssue. | 1.SR099616 2.SR101178 | SR101178
Bedford - 205 Burlington Rd | MA | 38548 | N/A |  |  | N/A
Billerica - 6 Cook Street | MA | 33772 | N/A |  |  | N/A
Billerica - 780 Boston Road | MA | 39963 | N/A |  |  | N/A |  |  | 1.Inverter 4 was offline from 05/06 to 10:50 on 05/07 .Inverter 4 was back online after technician has completed the troubleshooting.Additionally ,Inverter 4 has a history of late start ups throughout the month. | 1.SR101062
Cheshire | MA | 65020.75 | 66082.88 | -1062.13 | -1.607% | 72176.47 | -7155.72 | -9.914% | 1.Site production was low on 05/05 and 05/06 due to rain
Lilly Lane | MA | 150622.5 | 141067.2 | 9555.3 | 6.774% | 174942.4 | -24319.9 | -13.9% | 1.Inverter 69 was offline from 12:40 to 13:15 on 05/25 due to PV abnormal input. | 1.SR101921
Monument Valley | MA | 308672.71 | 56841.47 | 251831.24 | 443% | 0 | 308672.71 |  | 1. Expected generation values are lower than actual values. AlsoEnergy stated that expected values are calculated based on inverter data and weather conditions and recommended an onsite visit. However, due to communication issues with the inverters, the expected values remain low. | 1.SR087370
Nationwide | MA | 557878 | 442386.1 | 115491.9 | 26.11% | 549147.6 | 8730.4 | 1.59% | 1.Inverter 13 was being offline for alternate days throughout the month.On 05/13,technician found Inverter was faulted with isolation fault and technician spoke with sungrow support and they stated the problem is in the array .On 05/21,technician tried to troubleshoot but failed and intiated RMA'D from 05/21 2.Inverter 9 was started late for production at 15:15 on 05/06 .issue got self resolved.Inverter is having history of late startups 3.Multiple inverters experienced brief production drops on 05/21 and 05/23 while technicians were onsite performing preventive maintenance | 1.SR101031,PM8011 2.SR101061 3.PM8011 | SR101061
Pulpit Hill | MA | 673176.5 | 639653.9 | 33522.6 | 5.241% | 781076.6 | -107900.1 | -13.81% | 1. Inverters 81 and 83 were derating at 40 kW due to an external fan fault since 04/24. On 05/07, the technician replaced the fan for Inverter 81 and the power head for Inverter 2. All inverters resumed normal production from 11:00 the same day | 1.SR100353, SR101879 | SR101879
Sandwich | MA | 469119 | N/A |  |  | 627279 | -158160 | -25.21% | 1. BESS Pad 3 has tripped offline on 04/08, on 04/29 technician noted that Module 5 battery needs to be discharged to at least 73V DC. 2. HEILA BESS controller 4 tripped offline at 10:45am on 05/18. and later self resolved and back online at 07:00 on 05/19. | 1. SR100358 2. SR101648 | SR101648
Sturbridge Barn | MA | 152276 | 149278 | 2998 | 2.008% | 199702.9 | -47426.9 | -23.75% | 1. Inverter 17 tripped offline at 08:00 on 05/26, reporting "Insulation Resistance Low - IsolationErr." A technician later checked the site and replaced the damaged MC4 connector. The inverter was back online at 13:00 on 05/27. | 1. SR101935
Sturbridge Garage | MA | 77321 | 70679.64 | 6641.36 | 9.396% | 86417.16 | -9096.16 | -10.53% | 1. Inverter R 2-2 tripped offline at 07:00 on 05/25, reporting a Bus (sum) overvoltage fault. A technician inspected the site on 05/27, and the inverter was left offline. It will be RMA'd. | 1. SR101916
Halsey Valley | NY | 734511.72 | 715084.5 | 19427.22 | 2.717% | 1022000 | -287488.28 | -28.13% | 1. Inverters 13 and 25 trippped offline at 07:00 on 05/21 and Later self resolved and back online at 17:30 on 05/21. | 1. SR101787
Hunt Creek | NY | 512431 | 522549.3 | -10118.3 | -1.936% | 742100 | -229669 | -30.95% | 1.Inverter 18 was ofline since 12/08/24 due to floating capacitor high voltage. Will investigate next time onsite. 2. Inverters 2, 5, 8, 14, 15, 19, 23, 27, 3, 17, 22 have tripped offline at 17:15 on 05/05 due to "Grid voltage imbalance". Later self resolved and back online at 19:15 on 05/05. 3. Inverters 4, 16, 31 and 32 tripped offline at 08:30 on 05/06 Later self resolved and back online at 09:00 on 05/06. 4. All inverters except Inverters 7, 20, 21 have tripped offline at 19:30 on 05/27 and reporting "Grid voltage unbalance"and Later self resolved and back online at 07:45 on 05/28. | 1. SR094254 2. SR101041 3. SR101051 4. SR102009 | SR101041 | SR101051 | SR102009
Smith Creek | NY | 563289 | 576395.6 | -13106.6 | -2.274% | 748264.8 | -184975.8 | -24.72% | 1. Inverters 1 and 24 are tripped offline at 17:15 05/05 and reporting " Grid voltage Unbalance" and later self resolved are back online at 19:15 on 05/05. 2. Inverters 1, 6, 8, 11, 13, 17, 20, 22, 23, 24, 28 have tripped offline at 19:30 on 05/27and reporting "Grid voltage unbalance" and later self resolved and all inverters back online on 05/28. | 1. SR101042 2. SR102010 | SR102010
Bradford - 256 Presidential Dr | MA | 578903.108 | N/A |  |  | N/A |  |  | 1. Site was offline from 07:00 on 05/03 due to a "Grid line voltage out of range (GridV.OutLim)" fault and was restored at 14:00 on 05/06 after the technician re-energized the breaker. 2. Inverter 18 went offline at 13:00 on 05/06 due to "Low insulation resistance" and was back online at 16:10 the same day 3. Inverter 134 was offline from 05/09 due to a "Bus imbalance fault" and was back online at 17:00 on 05/15 after the technician troubleshot and re-energized it. Additionally, the communication card for Inverter 128 was replaced, but further troubleshooting is needed to restore communication. 4. Inverters 24 and 114 are derating by 16kW each compared to its peers. 5. Site tripped offline at 10:00 on 05/30 and was back online at 15:00 on 05/31 after the technician re-energized it by closing the SEL. | 1. SR100988 2. SR101074 3. SR101231 4. SR101357 5. SR102183 | SR101074 | SR101231 | SR101357 | SR102183
Charlton – 111 Brookfield Road - Bus Lot | MA | 75038.016 | N/A |  |  | N/A |  |  | 1. Inverter 4 tripped offline at 16:00 on 05/24 due to an arc fault. A technician checked the site on 05/27 and re-energized the inverter after bypassing a module on string 4.8. The inverter was back online at 15:00 on 05/27. | 1. SR101920
Charlton – 154 Center Depot Road KMARD | MA | 65512.064 | N/A |  |  | N/A |  |  | 1. Inverter 4 back online at 06:00 on 05/01. 2. Site was offline from 06:00 on 05/15 and on 05/16, the technician reset and re-close the site recloser and the site back online at 07:00 the same day. | 1. SR100710 2. SR101508 | SR101508
Charlton – 142A Brookfield Rd (Mitchell) | MA | 69400.064 | N/A |  |  | N/A
Great Barrington – 3 Nolan Drive | MA | 151014.336 | N/A |  |  | N/A |  |  | 1. Inverter 14 was underproducing by 5kW compared to its peers. Will investigate next time onsite. 2. Inverter 24 back online on 05/01 and inverter being RMA'd. 3. Inverter 18 tripped offline at 16:00 on 04/09 and remained offline through the month. On 04/16, the technician found the inverter offline with Fault 0010. AC and DC voltages were within normal ranges (Strings 1–10: 707–712 VDC). Solectria support advised changing IdcMax(mA) from 216 to 398, but the fault reappeared. Solectria is reviewing photos to determine if the inverter will be RMA’d. A return visit is required once the replacement unit arrives. 4. Site has 4 meters; 2 record the bulk of production. RGM 1 is reporting 0 kW, and RGM 2 is showing low production. | 1. SR098468 2. SR099298 3. SR099815, SR099920 4. SR101029 | SR099298 | SR099815 | SR099920 | SR101029
Stockbridge – 92 State Line Road Truck Stop | MA | 296927.403 | N/A |  |  | N/A |  |  | 1.Inverter 36 stopped communicating at 10:00 on 05/26, possibly due to an onsite communication issue and a device fault. On 05/28, the technician inspected the unit and found a failed communication board. The board was replaced using a spare from stock, and the inverter was brought back online at 10:00 the same day. 2. Inverter 51 offline on 05/31 due to an "Insulation resistance is low". | 1. SR101985 2. SR102231 | SR102231
NY: New Windsor - Moores Hill | NY

## Jun
Lodestar |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 10011771.4665 | 7314413.59 | 2697357.8765 | 36.88% | 8157558.43 | 1854213.0365 | 22.73%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT | 172503 | 180631.9 | -8128.9 | -4.5% | 193885.7 | -21382.7 | -11.03% | 1.Combiner box 1.15(DCP - 12) tripped offline at 14:15 on 06/09 and offline through out the month | 1.SR102739
Bunce | CT | 344462.5 | 199103 | 145359.5 | 73.01% | 0 | 344462.5 |  | 1. Weather station module temperature and ambient temperature are stuck reading at 184.95 and 120 degrees Fahrenheit since 5/2. On 06/03 both sensors were RMA'd. 2. Inverter 15 tripped offline at 9:45AM on 05/30 and back online on 06/03. | 1. SR101404 2. SR102179 | SR102179
Norcap North | CT | 351514.5 | 315289.8 | 36224.7 | 11.49% | 370442.1 | -18927.6 | -5.109% | 1. Inverter 18 was derating by 20kW since 05/28, on 06/02 the fan was RMA'd. 2. Inverter 1 was derated to 40kW since 05/02 and on 06/02 the fan was RMA'd. | 1. SR102051 2. SR100943 | SR100943
Norcap South | CT | 362144.5 | 331666.6 | 30477.9 | 9.189% | 363121.9 | -977.4 | -0.2692%
Platt Hill | CT | 392747 | 397782.9 | -5035.9 | -1.266% | 406031 | -13284 | -3.272%
Powder Hill | CT | 361177 | 351967.6 | 9209.4 | 2.617% | 286956 | 74221 | 25.86% | 1. Inverter 12 was underproducing by 12kW since 05/13 . Will need to investigate next time onsite. 2. Inverter 6 tripped offline at 11:51AM due to High frequency fault and back online at 13:15 on 06/09. | 1. SR102083 2. SR102609 | SR102609
Sand Road | CT | 343975.0495 | 287330.4 | 56644.6495 | 19.71% | 348315 | -4339.9505 | -1.246% | 1. Site stopped communication at 8:30 on 06/20. On 06/21 and site was re-energized. | 1. SR103213
Suffield | CT | 349315 | 337548.7 | 11766.3 | 3.486% | 383976.9 | -34661.9 | -9.027%
Ashby-Duffy | MA | 334572 | 335248.1 | -676.1 | -0.2017% | 354815.7 | -20243.7 | -5.705%
Ashland | MA | 328311 | 355156.7 | -26845.7 | -7.559% | 399168.8 | -70857.8 | -17.75% | 1. Inverter 53 didn't started for production on 06/15 and self-resolved on 06/16. On 06/17 inverter started late for production at 17:45. | 1. SR102994
Barrington | MA | 76986 | 63928.59 | 13057.41 | 20.42% | 85100 | -8114 | -9.535%
Bedford - 205 Burlington Rd | MA | 43520 | N/A |  |  | N/A |  |  | 1. Inverter 6 tripped offline at 14:20 due to "Grid Relay protection" fault and inverterwas RMA'd on 06/30. | 1. SR103728
Billerica - 6 Cook Street | MA | 41630 | N/A |  |  | N/A
Billerica - 780 Boston Road | MA | 46010 | N/A |  |  | N/A
Cheshire | MA | 80361 | 82249.42 | -1888.42 | -2.296% | 70450.94 | 9910.06 | 14.07% | 1. Inverter 1 tripped offline due to ARC fault at 16:00 on 06/24 and was RMA'd on 06/27. | 1. SR103462
Lilly Lane | MA | 179723 | 169471.8 | 10251.2 | 6.049% | 177023.4 | 2699.6 | 1.525%
Monument Valley | MA | 355393 | 62959.4 | 292433.6 | 464.5% | 0 | 355393 |  | 1. Expected generation values are lower than actual values. AlsoEnergy stated that expected values are calculated based on inverter data and weather conditions and recommended an onsite visit. However, due to communication issues with the inverters, the expected values remain low. | 1. SR087370
Nationwide | MA | 627229 | 489264.7 | 137964.3 | 28.2% | 549795.1 | 77433.9 | 14.08% | 1. Site stopped communications at 15:45 on 06/10 and on 06/12 the site was re-energized. 2. Inverter 16 didn't started for production on 06/03 and on it was RMA'd on 06/12. | 1. SR102793 2. SR102374 | SR102374
Pulpit Hill | MA | 801931.75 | 755271.6 | 46660.15 | 6.178% | 798150.4 | 3781.35 | 0.4738%
Sandwich | MA | 465917 | N/A |  |  | 543938 | -78021 | -14.34% | 1. All 4 SKIDS tripped offline at 9:15 on 06/14 and back online on 06/18. 2. Helia Bess controller 1 tripped offline at 11:45 and self -resolved at 12:15 on 06/22. 3. Site tripped offline at 9:25 on 06/25 and back online on the same day after CES reset them. | 1. SR102978 2. SR103272 3. SR103522 | SR103272 | SR103522
Sturbridge Barn | MA | 182150.5 | 177700.6 | 4449.9 | 2.504% | 196021.7 | -13871.2 | -7.076%
Sturbridge Garage | MA | 85615.25 | 84325.08 | 1290.17 | 1.53% | 87445.09 | -1829.84 | -2.093%
Halsey Valley | NY | 875264 | 884096.8 | -8832.8 | -0.9991% | 986000 | -110736 | -11.23% | 1. Inverter 38 tripped offline at 14:30 due to Islanding fault on 06/04 and remained offline throughout the month. 2. Inverter 8 tripped offline at 15:15 on 06/23 due to Islanding fault and remained offline throughout the month. 3. Site tripped offline at 13:00 on 06/30 and back online at 13:30 on the sameday. 4. Inverter 37 tripped offline at 13:15 on 06/30. | 1. SR102471 2. SR103328 3. SR103767 4. SR103780 | SR103328 | SR103767 | SR103780
Hunt Creek | NY | 626192 | 648129.4 | -21937.4 | -3.385% | 706700 | -80508 | -11.39% | 1. Multiple inverters tripped offline at 8:47 due to "Grid voltage unbalance" fault and self -resolved at 10:30 on the same day. | 1. SR102985
Smith Creek | NY | 691792 | 717638.5 | -25846.5 | -3.602% | 749934.7 | -58142.7 | -7.753%
Bradford - 256 Presidential Dr | MA | 694941.501 | N/A |  |  | N/A |  |  | 1. Site tripped offline at 11 on 06/02 and back online on 06/03. 2. Inverter 34 was derating by 16kW and inverters 34,42,83,85,113 are producing low 10kW each compared to its peer inverters. On 06/06 fuses were replaced for each inverter. 3. Site tripped offline at 13:00 on 06/14 and re-energized on 06/15. | 1. SR102294 2. SR102555 3. SR102977 | SR102555 | SR102977
Charlton – 111 Brookfield Road - Bus Lot | MA | 91255.04 | N/A |  |  | N/A
Charlton – 154 Center Depot Road KMARD | MA | 77815.808 | N/A |  |  | N/A |  |  | 1. Inverter 4 was didn't started for production on multiple days throughout the month self-resolving on alterante days. | 1. SR102764
Charlton – 142A Brookfield Rd (Mitchell) | MA | 81737.984 | N/A |  |  | N/A
Great Barrington – 3 Nolan Drive | MA | 170070.16 | N/A |  |  | N/A |  |  | 1. Inverter 14 is underperforming by about 5kw. Will investigate next time onsite 2. Inverter 5 tripped offline at 9:25 on 06/25 and back online on 06/27, additionally screen was RMA'd. | 1. SR098468 2. SR103531 | SR103531
Stockbridge – 92 State Line Road Truck Stop | MA | 366197.924 | N/A |  |  | N/A |  |  | 1. Inverter 51 was offline on 05/31 and back online at 15:15 on 06/01. | 1. SR102231
NY: New Windsor - Moores Hill | NY | 9317 | 87652 | -78335 | -89.37% | 100286 | -90969 | -90.71%

## Jul
Lodestar |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 11349245.4976 | 8602352.66 | 2746892.8376 | 31.93% | 10936019.43 | 413226.0676 | 3.779%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT | 186443 | 201126.7 | -14683.7 | -7.301% | 196367.1 | -9924.1 | -5.054%
Bunce | CT | 395526 | 230167.4 | 165358.6 | 71.84% | 0 | 395526 |  | 1. Weather station module temperature and ambient temperature are stuck reading at 184.95 and 120 degrees Fahrenheit since 5/2. On 06/03 both sensors were RMA'd. | 1. SR101404
Norcap North | CT | 384768.5 | 352819.8 | 31948.7 | 9.055% | 380013.8 | 4754.7 | 1.251%
Norcap South | CT | 401750 | 374227.8 | 27522.2 | 7.354% | 372022.7 | 29727.3 | 7.991%
Platt Hill | CT | 408298 | 439072.1 | -30774.1 | -7.009% | 458149.7 | -49851.7 | -10.88% | 1. The site tripped offline at 14:30 on 07/17 due to a breaker is open. After closing the breaker, the site came back online at 14:30 on 07/18. 2. The Site tripped offline at 13:49 on 07/27 due to a main breaker trip. After resetting the breaker, the site was back online at 13:00 on 07/28. 3. Inverter 4 tripped offline at 15:30 on 07/29 due to a breaker is open. After closing the breaker inverter is back online at 13:50 on 07/30. | 1. SR104572 2. SR105130 3. SR105293 | SR105130 | SR105293
Powder Hill | CT | 391992 | 388112.2 | 3879.8 | 0.9997% | 306552 | 85440 | 27.87% | 1. Inverter H tripped offline at 12:45 on 07/11 and Reporting "Open Phase Detected". later self resolved and back online at 06:00 on 07/12. 2. inverter E dropped to under 5kw at 15:15 and late tripped offline at 17:00 on 07/15 in afternoon, reporting "critical hardware failure and open phase detected" and offline throughout the month. 3. Inverter K tripped offline at 15:15 on 07/29 and reporting "critical over temperature" and later back online at 06:00 on 07/30. 4. Inverter 12 was underproducing by 12kW since 05/13 . Will need to investigate next time onsite. | 1. SR104334 2. SR104476 3. SR105295 4. SR102083 | SR104476 | SR105295 | SR102083
Sand Road | CT | 418403 | 357496.8 | 60906.2 | 17.04% | 370289 | 48114 | 12.99% | 1. Inverter 16 tripped offline from 09:45 to 12:00 on 07/17, and Inverter 13 tripped offline from 11:30 to 12:30 on 07/17. The issue occurred while a technician was onsite replacing modules and was later self-resolved. 2. Inverters 11 and 12 tripped offline at 08:45 on 07/22 and later self-resolved, and back online at 12:15 on 07/22. The issue occurred while a technician was onsite for replacing modules. | 1. SR103650 2. SR103081 | SR103081
Suffield | CT | 399035 | 378947.5 | 20087.5 | 5.301% | 387460.6 | 11574.4 | 2.987%
Ashby-Duffy | MA | 336275 | 371832.1 | -35557.1 | -9.563% | 362461.4 | -26186.4 | -7.225%
Ashland | MA | 377172.649 | 391041.8 | -13869.151 | -3.547% | 410590.6 | -33417.951 | -8.139%
Barrington | MA | 84302 | 69683.55 | 14618.45 | 20.98% | 92730 | -8428 | -9.089% | 1. The weather station readings have been dropping to their minimum values during high-irradiance afternoons.
Bedford - 205 Burlington Rd | MA | 41407 | N/A |  |  | N/A |  |  | 1. Inverter 6 tripped offline at 14:20 on 06/29 due to "Grid Relay protection" fault and inverter was RMA'd since 06/30. 2. inverter 2 and 5 are dropped production by 10Kw down may be due to string down. | 1. SR103728 2. SR103770 | SR103770
Billerica - 6 Cook Street | MA | 44826 | N/A |  |  | N/A
Billerica - 780 Boston Road | MA | 44164 | N/A |  |  | N/A |  |  | 1. Inverter 4 was offline at 05:30 to 15:10 on 07/28 and reporting isolation fault and later self resolved. 2. Inverter 2 was offline at 12:45 on 06/29 and later breaker reset then inverter is back online at 09:15 on 07/24. | 1. SR105176 2. SR104757 | SR104757
Cheshire | MA | 86532.5 | 89935.52 | -3403.02 | -3.784% | 74014.19 | 12518.31 | 16.91% | 1. Inverter 1 tripped offline due to an arc fault at 16:00 on 06/24 and was RMA'd on 06/27. After replacing the inverter is back online at 12:45 on 07/11. additionally Inverter 1 again tripped offline at 18:00 on 07/15 and reporting "Grid line voltage out of range" later self resolve and back online at 06:00 07/16. and again tripped offline at 13:45 on 07/28, 07/29 and 07/30 during afternoon and reporting "Grid line voltage out of range" and back online at 06:00 on 07/31. | 1. SR103462, SR104505, SR105297 | SR104505 | SR105297
Lilly Lane | MA | 184516.5 | 180305.3 | 4211.2 | 2.336% | 187429.3 | -2912.8 | -1.554%
Monument Valley | MA | 392384 | 73366.91 | 319017.09 | 434.8% | 0 | 392384 |  | 1. Expected generation values are lower than actual values. AlsoEnergy stated that expected values are calculated based on inverter data and weather conditions and recommended an onsite visit. However, due to communication issues with the inverters, the expected values remain low. and later inverters communication back online at 22:00 on 07/31. | 1. SR087370
Nationwide | MA | 649672 | 567033.9 | 82638.1 | 14.57% | 598737.2 | 50934.8 | 8.507% | 1. Inverter 16 did not start production on 06/03 and was RMA'd on 06/12. After the inverter was replaced, it came back online at 12:30 on 07/23. 2. Inverter 30 is underperforming by 10-15kw since 6/24. 3. Inverter 13 didn't start for production since 05/12 and was RMA'd on 05/21. After the inverter was reenergized it came back online at 12:30 on 07/23. | 1. SR102374, SR102374 2. SR104275 3. SR101031 | SR102374 | SR104275 | SR101031
Pulpit Hill | MA | 872565.25 | 829378 | 43187.25 | 5.207% | 807930.8 | 64634.45 | 8%
Sandwich | MA | 540494 | N/A |  |  | 602820.66 | -62326.66 | -10.34% | 1. HEILA BESS Controller 1 was tripped offline from 11:45 to 16:00 on 07/04, and again offline from 14:01 to 16:30 on 07/13. | 1. SR104017
Sturbridge Barn | MA | 193221.5 | 188419.6 | 4801.9 | 2.549% | 209208.2 | -15986.7 | -7.642%
Sturbridge Garage | MA | 88351.75 | 89379.68 | -1027.93 | -1.15% | 92585.88 | -4234.13 | -4.573%
Halsey Valley | NY | 974970 | 1050705 | -75735 | -7.208% | 1064000 | -89030 | -8.367%
Hunt Creek | NY | 745992 | 781605.1 | -35613.1 | -4.556% | 755800 | -9808 | -1.298%
Smith Creek | NY | 827503 | 867977.3 | -40474.3 | -4.663% | 803883.3 | 23619.7 | 2.938%
Bradford - 256 Presidential Dr | MA | 835717 | N/A |  |  | 917757 | -82040 | -8.939% | 1. Inverter 34 is underproducing by about 10kw down Since 06/30. 2. Inverters 24, 34, and 114 were producing only 10 kW each, which was low compared to their peer inverters. On 07/15, a technician replaced the fans in all three inverters, after which they began producing as expected. 3. Inverter 104 tripped offline at 11:00 on 07/14 and reporting "Power module fault (Fault0010)" and later self resolved and back online at 06:00 on 07/15. 4. Inverter 1 tripped offline at 11:05 on 07/24 and reporting "Reading power module fault Protect0120 and increased DC voltages" and later self resolved and back online at 06:00 on 07/25.. | 1. SR103781 2. SR104336 3. SR104425 4. SR104951 | SR104336 | SR104425 | SR104951
Charlton – 111 Brookfield Road - Bus Lot | MA | 96510 | N/A |  |  | 113800 | -17290 | -15.19% | 1. Inverter 4 is tripped offline at 14:00 on 07/08 and reporting "ARC failure detected" and later back online at 08:00 on 07/09. | 1. SR104163
Charlton – 154 Center Depot Road KMARD | MA | 81443 | N/A |  |  | 109700 | -28257 | -25.76% | 1. Inverter 4 was didn't started for production on multiple days throughout the month self-resolving on alterante days. 2. Inverter 3 was offline at 07:00 on 07/22 and later self resolved and back online at 06:00 on 07/23. 3. inverter 13 was offline since 2/5/25 and inverter is being under RMA'd. | 1. SR102764 2. SR104762 3. SR097803 | SR104762 | SR097803
Charlton – 142A Brookfield Rd (Mitchell) | MA | 86190 | N/A |  |  | 111016 | -24826 | -22.36% | 1. Inverter 13 was tripped offline at 13:00 on 07/17 and inverter is being under RMA'd. | 1. SR104528, SR104686 | SR104686
Great Barrington – 3 Nolan Drive | MA | 179246 | N/A |  |  | 214100 | -34854 | -16.28% | 1. Inverter 14 is underperforming by about 5kw. Will investigate next time onsite. 2. Inverter 18 is was offline since 04/09/25 and reporting "Protect0070" and inverter is being under RMA'd. 3. Inverter 5 has tripped offline at 12:00 on 06/29 and inverter is being under RMA'd. 4. Inverter 27 has tripped offline at 15:00 on 07/04 and reporting " Grid relay fault (Fault0100)" and inverter is being under RMA'd. | 1. SR098468 2. SR099815, SR099920 3. SR103531 4. SR104024 | SR099815 | SR099920 | SR103531 | SR104024
Stockbridge – 92 State Line Road Truck Stop | MA | 332916 | N/A |  |  | 434000 | -101084 | -23.29% | 1. Inverters 5, 16 and 51 have tripped offline at 16:00 on 07/01 and reporting "Insulation resistance low" all inverters self resolved and back online at 11:00 on 07/02. 2. Site tripped offline at 10:15 on 07/24 and later back online at 12:00 on 07/28. Additionally All inverters was offline at 06:00 on 07/29 and reporting "Grid line voltage out of range (GridV.OutLim) and later back online at 06:00 on 07/31. | 1. SR103870 2. SR104952 | SR104952
NY: New Windsor - Moores Hill | NY | 266658.8486 | 329718.6 | -63059.7514 | -19.13% | 502600 | -235941.1514 | -46.94% | 1. Inverter 1 had heavy shading through out the day for whole month 2. All inverters tripped offline at 18:00 on 07/03 and reporting "Arc fault detected" and all inverters are came back online on 07/04 3. Inverter 6 tripped offline at 11:45 on 07/08 and reporting "Ground fault detection failure". It came back online on 07/09 4.Site was offline from 09:15 to 13:30 on 07/09 and again offline from 07:30 to 14:15 on 07/10due to EPC to replace a CT 5. Inverters 5,8,9,10,11 &15 tripped offline at 12:30 pon 07/14 and reporting "Arc fault detected" and "Internal communication 2 failure Inverter Faults Detected". Selfresolved on 07/15 6. The meter is currently capturing excess data (~400-500 kW) irrespective of inverter production. | 2.SR103999 3. SR104162 4.SR104187 5.SR104400 6. SR107288 | SR104162 | SR104187 | SR104400 | SR107288

## Aug
Lodestar |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 11639630.601 | 9131482.54 | 2508148.061 | 27.47% | 10659080.84 | 980549.761 | 9.199%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT | 191207 | 208633.3 | -17426.3 | -8.353% | 185704.4 | 5502.6 | 2.963% | 1. Inverter 1.5 was offline from 11:30 on 07/30 and came back online at 12:45 on 08/07. 2. The site tripped offline at 15:00 on 08/14 and came back online at 08:15 on 08/15. | 1. SR105374 2. SR106308 | SR106308
Bunce | CT | 389723 | 236606.5 | 153116.5 | 64.71% | 0 | 389723 |  | 1. Weather station module temperature and ambient temperature are stuck reading at 184.95 and 120 degrees Fahrenheit since 5/2. On 06/03 both sensors were RMA'd. | 1. SR101404
Norcap North | CT | 389806 | 387770.8 | 2035.2 | 0.5248% | 360508.3 | 29297.7 | 8.127% | 1. Inverter 1 has been derating by approximately 20 kW throughout the month. 2. Inverter 17 has been derating by approximately 20 kW throughout the month. 3. Inverter 23 was offline from 08/15 and came back online at 16:30 on 08/19. It went offline again on 08/20 and remained offline throughout the month. 4. The site tripped offline at 15:00 on 08/13 and came back online at 17:30 on the same day. | 1. SR104474 2. SR104730 3. SR106337, SR106597 4. SR106215 | SR104730 | SR106337 | SR106597 | SR106215
Norcap South | CT | 418210 | 407006 | 11204 | 2.753% | 354060.4 | 64149.6 | 18.12% | 1. Inverter 55 is derating by 24kW during mid of the day. | 1.SR100021
Platt Hill | CT | 426178 | 448681.1 | -22503.1 | -5.015% | 409778 | 16400 | 4.002% | 1. Inverter 9 tripped offline at 15:00 on 08/09 and came back online at 09:30 on 08/12. 2. The site tripped offline at 08:30 on 08/15 and came back online at 08:30 on 08/16. | 1. SR105954 2. SR106327 | SR106327
Powder Hill | CT | 396122 | 398638.2 | -2516.2 | -0.6312% | 284916 | 111206 | 39.03% | 1. Inverter E was offline from 17:00 on 07/15 and came back online at 09:30 on 08/12. 2. Inverter H tripped offline at 12:00 and came back online at 15:15 on 08/17. It tripped offline again at 12:30 on 08/23 and came back online at 13:15 the same day. 3. Inverter H tripped offline at 15:45 and came back online at 17:15 on 08/29. 4. Inverter F started production late at 15:15 on 08/21. | 1. SR104476 2. SR106398 3. SR107215 4. SR106665 | SR106398 | SR107215 | SR106665
Sand Road | CT | 424370 | 377766.8 | 46603.2 | 12.34% | 328508 | 95862 | 29.18%
Suffield | CT | 404465 | 396667.1 | 7797.9 | 1.966% | 363443 | 41022 | 11.29% | 1. Inverter 2.3 tripped offline at 15:00 on 08/10 and came back online at 14:15 on 08/11. 2. Inverter 2.2 tripped offline at 14:30 on 08/15 and came back online at 15:00 on 08/19. 3. Inverters 1.1 to 1.5 tripped offline at 10:00 on 07/31 and came back online at 13:15 on 08/01. | 1. SR105975 2. SR106358 3. SR105428 | SR106358 | SR105428
Ashby-Duffy | MA | 377451 | 393481.8 | -16030.8 | -4.074% | 357114.9 | 20336.1 | 5.695% | 1. Inverter 62 is underproducing approximately by 11kW from 10:45 on 06/12 and later producing as expected along with its peers from 11:30 on 08/11. 2. Inverter 39 was producing with strings 5 and 6 offline throughout the month. Approval is needed for further troubleshooting. 3. Inverter 53 tripped offline at 16:30 on 08/13 and came back online at 15:30 on 08/15. 4. Inverter 24 started producing late at 14:30 on 08/21. 5. Inverter 17 tripped offline at 08:15 on 08/25 and has remained offline since. 6. The site tripped offline at 11:45 on 08/26 and came back online at 12:30 on 08/26. | 1. SR103047 2. SR103282 3. SR106227 4. SR106661 5. SR106834, SR107298 6. SR106937 | SR103282 | SR106227 | SR106661 | SR106834 | SR107298 | SR106937
Ashland | MA | 396717.351 | 412725.1 | -16007.749 | -3.879% | 385434.9 | 11282.451 | 2.927% | 1. Inverter 53 barely produced on 08/16 and 08/17 due to multiple trippings, and later produced as expected with its peers from 08/18. | 1. SR106388
Barrington | MA | 84723.5 | 73902.88 | 10820.62 | 14.64% | 87310 | -2586.5 | -2.962% | 1. The weather station readings have been dropping to their minimum values during high-irradiance afternoons.
Bedford - 205 Burlington Rd | MA | 41810 | N/A |  |  | N/A |  |  | 1. Inverter 6 has been offline since 15:20 on 06/29 and is under RMA. 2. Inverters 2 and 5 have been running with one string down each throughout the month. | 1. SR103728 2. SR103770 | SR103770
Billerica - 6 Cook Street | MA | 43905 | N/A |  |  | N/A
Billerica - 780 Boston Road | MA | 50605 | N/A |  |  | N/A
Cheshire | MA | 90091 | 91412.71 | -1321.71 | -1.446% | 65697.52 | 24393.48 | 37.13% | 1. Inverter 1 tripped offline at 13:45 on 08/14 and came back online at 06:45 on 08/15. | 1. SR105297
Lilly Lane | MA | 192604.5 | 190502.7 | 2101.8 | 1.103% | 178327.1 | 14277.4 | 8.006% | 1. Inverter 61 remained offline throughout the month. 2. Inverter 69 remained offline throughout the month. 3. Inverter 65 was offline on 08/12 and came back online at 06:00 on 08/13. | 1. SR097795 2. SR101921 3. SR106070 | SR101921 | SR106070
Monument Valley | MA | 418949 | 351825.2 | 67123.8 | 19.08% | 334160 | 84789 | 25.37% | 1. The site went offline at 22:15 on 08/24 and came back online at 14:15 on 08/25. 2. Pad 2 inverters (5 to 8) tripped offline at 17:00 on 08/26 and came back online at 08:45 on 08/27. They tripped offline again at 17:15 on 08/31. | 1. SR106814 2. SR106982 | SR106982
Nationwide | MA | 599949 | 586875.8 | 13073.2 | 2.228% | 537586.9 | 62362.1 | 11.6%
Pulpit Hill | MA | 896255 | 856112.8 | 40142.2 | 4.689% | 792721.8 | 103533.2 | 13.06% | 1. Inverter 42 has been derating at 40 kW since 09:45 on 07/15 and later operated as expected with its peers from 15:00 on 08/05. 2. Inverter 33 tripped offline at 16:30 on 08/08 and came back online at 06:00 on 08/09. | 1. SR104475, SR104472 2. SR105929 | SR104472 | SR105929
Sandwich | MA | 600365 | N/A |  |  | 584061.98 | 16303.02 | 2.791% | 1. The site went offline at 20:15 on 08/13 and came back online at 11:00 on 08/14. | 1. SR106232
Sturbridge Barn | MA | 193972.5 | 201045.5 | -7073 | -3.518% | 191453.3 | 2519.2 | 1.316% | 1. The site tripped offline at 14:45 on 08/01 and came back online at 16:15 on 08/02. | 1. SR105514
Sturbridge Garage | MA | 94273.75 | 94927.05 | -653.3 | -0.6882% | 88089.14 | 6184.61 | 7.021% | 1. Inverter 13 tripped offline at 09:00 on 08/06 and came back online at 06:30 on 08/07. 2. Inverter 13 tripped offline at 11:30 on 08/11 and came back online at 06:30 on 08/12. It tripped offline again at 15:15 on 08/24 and came back online at 06:15 on 08/25. | 1. SR105746 2. SR106014 | SR106014
Halsey Valley | NY | 1067704 | 1062244 | 5460 | 0.514% | 1015000 | 52704 | 5.193% | 1. Inverters 13, 25, and 37 were offline on 08/20 and came back online at 09:15 on 08/21. | 1. SR106596
Hunt Creek | NY | 714377 | 763991.4 | -49614.4 | -6.494% | 723000 | -8623 | -1.193% | 1. Inverter 18 remained offline throughout the month. 2. Inverters 4, 5, 15, 17, 23, 27, and 28 tripped offline at 16:30 on 08/09 and came back online at 07:30 on 09/10. 3. Inverters 2, 3, 4, 5, 6, 8, 10, 14, 15, 16, 17, 19, 22, 23, 24, 25, 27, 28, and 29 tripped offline at 11:15 on 08/15 and came back online at 16:15 on 08/15. 4. The site tripped offline at 15:45 on 08/13 and came back online at 17:45 on the same day. 5. Inverters 02, 03, 04, 05, 08, 10, 15, 16, 17, 19, 22, 23, 24, 25, and 28 tripped offline at 11:45 on 08/23 and came back online at 15:00 on 08/23. | 1. SR094254 2. SR105953 3. SR105953 4. SR106221 5. SR106777 | SR105953 | SR105953 | SR106221 | SR106777
Smith Creek | NY | 798659 | 832137.8 | -33478.8 | -4.023% | 747340.2 | 51318.8 | 6.867% | 1. Inverter 13 tripped offline at 16:30 on 08/09 and came back online at 18:30 on the same day. 2. The site tripped offline at 15:30 and came back online at 16:50 on 08/13. 3. Inverter 1 tripped offline at 11:45 on 08/23 and came back online at 15:00 on the same day. 4. The site tripped offline at 09:15 on 08/30 and came back online at 09:45 on the same day. | 1. SR105947 2. SR106220 3. SR106776 4. SR107228 | SR106220 | SR106776 | SR107228
Bradford - 256 Presidential Dr | MA | 887481 | N/A |  |  | 884144 | 3337 | 0.3774% | 1. Inverter 18 went offline on 08/14 and came back online at 07:00 on 08/15. 2. Inverter 34 is underproducing by about 10kw down Since 06/30. | 1. SR106321 2. SR103781 | SR103781
Charlton – 111 Brookfield Road - Bus Lot | MA | 91070 | N/A |  |  | 103500 | -12430 | -12.01% | 1. The site tripped offline at 15:00 on 08/01 and came back online at 09:00 on 08/04. | 1. SR105519
Charlton – 154 Center Depot Road KMARD | MA | 84807 | N/A |  |  | 100200 | -15393 | -15.36% | 1. The site tripped offline at 15:00 on 08/01 and came back online at 12:00 on 08/02. 2. Inverter 13 was offline since 2/5/25 and inverter is being under RMA'd. | 1. SR105518 2. SR097803 | SR097803
Charlton – 142A Brookfield Rd (Mitchell) | MA | 86676 | N/A |  |  | 101821 | -15145 | -14.87% | 1. The site tripped offline at 15:00 on 08/01 and came back online at 14:00 on 08/02. 2. Inverter 1 has been offline since 13:00 on 07/17 and is currently under RMA. | 1. SR105520 2. SR104528, SR104686 | SR104528 | SR104686
Great Barrington – 3 Nolan Drive | MA | 62374 | N/A |  |  | 207000 | -144626 | -69.87% | 1. Inverter 18 has been offline since 04/09/25 and is currently under RMA. 2. Inverter 5 has been offline since 12:00 on 06/29 and is currently under RMA. 3. Inverter 14 has been underperforming by about 5 kW throughout the month. 4. Inverter 27 has been offline since 15:00 on 07/04 and is currently under RMA. 5. Inverter 16 has been offline since 14:00 on 08/05 and is currently under RMA. | 1. SR099815, SR099920 2. SR103531 3. SR098468 4. SR104024 5. SR105724, SR105808 | SR099920 | SR103531 | SR098468 | SR104024 | SR105724 | SR105808
Stockbridge – 92 State Line Road Truck Stop | MA | 342062 | N/A |  |  | 428600 | -86538 | -20.19% | 1. Inverter 40 was offline on 08/06 and came back online at 07:00 on 08/07. It started production late at 13:00 on 08/19. The inverter went offline at 12:00 on 08/27 and came back online at 07:00 on 08/28. 2. The site tripped offline at 11:00 on 08/11 and came back online at 14:00 on 08/12. 3. The site tripped offline at 15:00 on 08/21 and came back online at 09:00 on 08/22. 4. The site tripped offline at 16:00 on 08/29 and remained offline for the rest of the month. | 1. SR105747 2. SR106005 3. SR106677 4. SR107218 | SR106005 | SR106677 | SR107218
NY: New Windsor - Moores Hill | NY | 382668 | 358528 | 24140 | 6.733% | 459600 | -76932 | -16.74% | 1. All trackers were stuck at -51° and affected production during the evening for all inverters except Inverter 1. 2. The site tripped offline at 15:00 and came back online at 17:00 on 08/13. 3. The meter is currently capturing excess data (~400-500 kW) irrespective of inverter production. | 1. SR105950 2. SR106216 3. SR107288 | SR106216 | SR107288

## Sep
Lodestar |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 9604335.528 | 7838189.9 | 1766145.628 | 22.53% | 9064176.9 | 540158.628 | 5.959%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT | 165510 | 179302 | -13792 | -7.692% | 164986.2 | 523.8 | 0.3175% | 1. The site went offline at 17:45 on 09/14 and came back online at 10:15 on 09/15. | 1. SR107947
Bunce | CT | 317883.5 | 210329.4 | 107554.1 | 51.14% | 0 | 317883.5 |  | 1. The site went offline at 13:45 on 09/06 and came back online at 12:00 on 09/08. 2.Weather station module temperature and ambient temperature are stuck reading at 184.95 and 120 degrees Fahrenheit since 5/2. On 06/03 both sensors were RMA'd. | 1. SR107560 2.SR101404 | SR101404
Norcap North | CT | 331794.5 | 362411.4 | -30616.9 | -8.448% | 318605.4 | 13189.1 | 4.14% | 1. Inverter 1 has been derating by approximately 20 kW throughout the month. 2. Inverter 17 has been derating by approximately 20 kW throughout the month. 3. Inverter 12 tripped offline at 15:30 on 09/30. 4. Inverter 12 tripped offline at 16:45 on 09/04 and came back online at 07:15 on 09/11. 5. Inverter 23 was offline throughout the month. | 1. SR104474 2. SR104730 3. SR108793 4. SR107482 5. SR106597 | SR104730 | SR108793 | SR107482 | SR106597
Norcap South | CT | 360847 | 383140.5 | -22293.5 | -5.819% | 312929.8 | 47917.2 | 15.31% | 1. Inverter 55 is derating by 24kW during mid of the day. | 1.SR100021
Platt Hill | CT | 373320 | 379067.2 | -5747.2 | -1.516% | 367999.2 | 5320.8 | 1.446% | 1. The site tripped offline at 09:15 and came back online at 14:00 on 09/19. | 1. SR108267
Powder Hill | CT | 314588 | 335927.1 | -21339.1 | -6.352% | 245616 | 68972 | 28.08% | 1. Inverter IH tripped offline at 14:00 on 09/01 and came back online at 06:30 on 09/02. 2. Inverter IF started production late at 15:30 on 09/05. 3. Inverter IF was offline on 09/07. 4. Inverter IB has been offline since 09/11. 5. Inverter IH was offline from 13:45 to 15:45 on 09/18. 6. Inverter IH tripped offline at 15:15 on 09/21 and came back online at 06:30 on 09/22. It again tripped offline at 13:45 on 09/22 and came back online at 17:30 on the same day. 7. Inverter IF remained offline on 09/25. 8. Inverter IK tripped offline at 12:30 on 09/28 and came back online at 07:00 on 09/29. | 1. SR107215 2. SR106665 3. SR106665 4. SR107886 5. SR108252 6. SR108326 7. SR106665 8. SR108702 | SR106665 | SR106665 | SR107886 | SR108252 | SR108326 | SR106665 | SR108702
Sand Road | CT | 347611 | 318979 | 28632 | 8.976% | 273983 | 73628 | 26.87% | 1. The site tripped offline at 14:00 on 09/06 and came back online at 12:45 on 09/07. 2. The site went offline at 17:45 on 09/07 and came back online at 11:00 on 09/08. | 1. SR107559 2. SR107590 | SR107590
Suffield | CT | 335903 | 329061.5 | 6841.5 | 2.079% | 316656.5 | 19246.5 | 6.078% | 1. Inverter 1, combiner box 1.5 tripped offline at 07:45 on 09/20 and came back online at 16:00 on 09/26. 2. Combiner box 1.13 was offline throughout the month. | 1. SR108313 2. SR103565 | SR103565
Ashby-Duffy | MA | 328009 | 366367.5 | -38358.5 | -10.47% | 296508.1 | 31500.9 | 10.62% | 1. Inverter 39 was producing with strings 5 and 6 offline throughout the month. Approval is needed for further troubleshooting. 2. Inverter 17 was offline from 08:15 on 08/25 and came back online at 13:15 on 09/04. It again tripped offline at 08:15 on 09/08 and came back online at 11:15 on 09/09. 3. Inverter 24 was offline on 09/24 and 09/25, and came back online at 08:30 on 09/26. | 1. SR103282 2. SR107298, SR106834 3. SR108489 | SR107298 | SR106834 | SR108489
Ashland | MA | 305544 | 328642.5 | -23098.5 | -7.028% | 325763 | -20219 | -6.207% | 1. Inverter 5 was offline on 09/14 and came back online at 14:45 on 09/15. 2. Inverter 65 was offline on 09/24 and 09/25 and came back online at 09:30 on 09/26. | 1. SR107940 2. SR108490 | SR108490
Barrington | MA | 70150 | 60906.98 | 9243.02 | 15.18% | 73860 | -3710 | -5.023% | 1. The weather station readings have been dropping to their minimum values during high-irradiance afternoons.
Bedford - 205 Burlington Rd | MA | 31838 | N/A |  |  | N/A |  |  | 1. Inverter 6 has been offline since 15:20 on 06/29 and is under RMA. 2. Inverters 2 and 5 have been running with one string down each throughout the month. | 1. SR103728 2. SR103770 | SR103770
Billerica - 6 Cook Street | MA | 32847 | N/A |  |  | N/A
Billerica - 780 Boston Road | MA | 37658 | N/A |  |  | N/A
Cheshire | MA | 75555.6203 | 79470.88 | -3915.2597 | -4.927% | 50846.8 | 24708.8203 | 48.59% | 1. Inverter 1 was barely producing and later tripped offline at 07:00 on 09/11, reporting 'Grid line voltage out of range.' It remained offline throughout the month and is currently under RMA. | 1. SR105297
Lilly Lane | MA | 159784 | 160762.9 | -978.9 | -0.6089% | 162482.9 | -2698.9 | -1.661% | 1. Inverter 61 remained offline throughout the month. 2. Inverter 69 tripped offline at 13:45 since 06/24 and reporting grid line voltage out of range and inverter is back online at 16:15 on 09/22. 3. Inverter 65 tripped offline at 14:30 on 09/09 and reporting "bus(sum) over voltage fault bus sum high fault - fault0130" and later back online at 07:00 on 09/10. 4. SIte tripped offline at 00:15 due to recloser open after technician closed the relay the site is back online at 09:15 on 09/26. | 1. SR097795 2. SR101921 3. SR107728 4. SR108585 | SR101921 | SR107728 | SR108585
Monument Valley | MA | 335965.9738 | 292057.4 | 43908.5738 | 15.03% | 290368 | 45597.9738 | 15.7% | 1. Pad 2 inverters (5 to 8) tripped offline at 17:15 on 08/31 and back online at 07:00 on 09/01. 2. Inverters 1 to 4 and 13 to 16 have tripped offline 11:15 on 09/01 after remote reset all inverters are back online at 12:45 on 09/01. 3. Site was offline at 01:00 on 09/05 due to relay open after technician closed the relay the site is back online at 11:00 on 09/05. 4. Site was offline at 13:45 on 09/06 due to relay open after technician closed the relay the site is back online at 09:00 on 09/08. 5. Inverters 1-4 and 13-16 tripped offline at 14:15 on 09/14 and reporting "Emergency stop" and back online at 07:00 on 09/15. | 1. SR106982 2. SR106982 3. SR107488 4. SR107557 5. SR107942 | SR106982 | SR107488 | SR107557 | SR107942
Nationwide | MA | 453817 | 487544.8 | -33727.8 | -6.918% | 459890.6 | -6073.6 | -1.321% | 1. Inverter 13 was offline at 07:00 on 09/07 and came back online at 14:00 on 09/07. It went offline again at 07:00 on 09/24 and was back online at 12:15 on 09/25. 2. Inverter 1 has been underproducing by 13 kW, possibly due to a string being down since 09/08. | 1. SR107577 2. SR107644 | SR107644
Pulpit Hill | MA | 737006.75 | 712009.2 | 24997.55 | 3.511% | 642143.2 | 94863.55 | 14.77% | 1. Site tripped offline at 16:04 on 09/06 due to severe storms and back online at 13:45 on 09/07. 2. Inverter 78 has tripped offline at 14:30 on 09/07 and reporting "Grid Under Frequency - GridF.OutLim" and after replacing the powerhead, the inverter came back online at 12:30 on 09/16. | 1. SR107558 2. SR107589 | SR107589
Sandwich | MA | 450745 | N/A |  |  | 503184 | -52439 | -10.42% | 1. PAD 4 inverters went offline at 14:15 on 09/13, reporting 'AC disconnected and grid shutdown.' After replacing the fuses, the inverters came back online at 10:30 on 09/16. 2. PADs 1-3 inverters went offline at 07:00 on 09/24 and back online at 12:00 on 09/25. | 1. SR107927 2. SR108457 | SR108457
Sturbridge Barn | MA | 162833 | 170033.5 | -7200.5 | -4.235% | 164121.4 | -1288.4 | -0.785% | 1. Inverter 28 tripped offline at 14:30 on 09/09 and reporting "PV abnormal input" and back online at 17:00 on 09/09. 2. Inverter 36 tripped offline at 14:30 on 09/09, reporting 'Bus Sum Over Voltage Fault / Bus Sum High Fault – Fault0130,' and came back online at 07:00 on 09/10. It went offline again at 07:00 on 09/12, reporting 'Bus Sum High Fault,' and was back online at 06:15 on 09/13. 3. Site tripped offline at 06:45 on 09/12 and back online at 13:45 on 09/12. 4. Site tripped offline at 00:30 on 09/26 and back online at 10:15 on 09/26. | 1. SR107720 2. SR107721 3. SR107898 4. SR108586 | SR107721 | SR107898 | SR108586
Sturbridge Garage | MA | 78429.5 | 81382.04 | -2952.54 | -3.628% | 80262.8 | -1833.3 | -2.284%
Halsey Valley | NY | 902812 | 894808.2 | 8003.8 | 0.8945% | 840000 | 62812 | 7.478% | 1. Inverter 13 was offline at 07:00 on 09/06 and came back online at 13:15 on 09/06. | 1. SR107550
Hunt Creek | NY | 593230 | 632125.2 | -38895.2 | -6.153% | 602800 | -9570 | -1.588% | 1. Inverter 18 remained offline throughout the month. 2. Inverters 23 and 27 tripped offline at 09:30 on 09/09 and reporting "Grid voltage unbalance" and back online at 17:15 on 09/09. 3. Inverters 2 to 6, 8, 10, 14 to 19, 22 to 30 and 32 tripped offline at 07:00 on 09/22 and reporting "Grid voltage unbalance" and back online at 11:47 on 09/22. | 1. SR094254 2. SR107692 3. SR108340 | SR107692 | SR108340
Smith Creek | NY | 664709 | 697042.4 | -32333.4 | -4.639% | 630168 | 34541 | 5.481%
Bradford - 256 Presidential Dr | MA | 722210.273 | N/A |  |  | 763830 | -41619.727 | -5.449% | 1. Inverter 34 is underproducing by about 10kw down Since 06/30. 2. Inverter 21 was LOTO'd and is currently under RMA. | 1. SR103781 2. SR107959, SR108028 | SR107959 | SR108028
Charlton – 111 Brookfield Road - Bus Lot | MA | 79705.984 | N/A |  |  | 92000 | -12294.016 | -13.36% | 1. All inverters were offline at 07:00 on 09/12 and reporting "Grid line voltage out of range" and back online at 06:00 on 09/13. | 1. SR107903
Charlton – 154 Center Depot Road KMARD | MA | 65400.96 | N/A |  |  | 85300 | -19899.04 | -23.33% | 1. Inverter 1 has tripped offline at 13:00 on 09/03 and reporting "Bus(sum) over voltage fault (Fault0130)" and back online at 07:00 on 09/04. 2. All inverters went offline at 07:00 on 09/12, reporting 'Grid line voltage out of range.' Except for Inverter 1, all inverters came back online at 13:00 on the same day. Inverter 1 came back online at 07:00 on 09/13. 3. All inverters went offline again at 07:00 on 09/26, reporting 'Grid line voltage out of range.' Except for Inverter 1, all inverters came back online at 08:00 on 09/27. Inverter 1 came back online at 07:00 on 09/28. | 1. SR107396 2. SR107905 3. SR108616 | SR107905 | SR108616
Charlton – 142A Brookfield Rd (Mitchell) | MA | 74189.824 | N/A |  |  | 92072 | -17882.176 | -19.42% | 1. Inverter 1 has been offline since 13:00 on 07/17 and is currently under RMA. 2. Inverter 3 tripped offline at 15:00 on 09/03 and reporting "Bus(sum) over voltage fault (Fault0130)" and back online at 07:00 on 09/04. | 1. SR104528, SR104686 2. SR107397 | SR104686 | SR107397
Great Barrington – 3 Nolan Drive | MA | 139925.76 | N/A |  |  | 181600 | -41674.24 | -22.95% | 1. Inverter 18 has been offline since 04/09/25 and is currently under RMA. 2. Inverter 5 has been offline since 12:00 on 06/29 and is currently under RMA. 3. Inverter 14 has been underperforming by about 5 kW throughout the month. 4. Inverter 27 has been offline since 15:00 on 07/04 and is currently under RMA. 5. Inverter 16 has been offline since 14:00 on 08/05 and is currently under RMA. 6. Inverter 11 tripped offline at 09:00 on 09/01 and reporting Bus(sum) over voltage fault (Fault0130) and is currently under RMA. 7. Inverter 12 was offline at 07:00 on 09/10 and reporting "Grid over frequency" and "PV abnormal input (Protect0260)"and back online at 15:00 on 09/10. 8. Inverter 22 and 28 tripped offline at 15:00 on 09/26 and reporting "Grid line voltage out of range" and back online at 08:00 on 09/29. | 1. SR099815, SR099920 2. SR103531 3. SR098468 4. SR104024 5. SR105724, SR105808 6. SR107262 7. SR107778, SR107912 8. SR108646 | SR099920 | SR103531 | SR098468 | SR104024 | SR105724 | SR105808 | SR107262 | SR107778 | SR107912 | SR108646
Stockbridge – 92 State Line Road Truck Stop | MA | 205454.104 | N/A |  |  | 362100 | -156645.896 | -43.26% | 1. The site tripped offline at 16:00 on 08/29 and came back online at 11:00 on 09/03. It tripped offline again at 15:00 on 09/03 and came back online at 17:00 on 09/06. 2. Inverter 40 tripped offline at 12:00 on 08/29 and came back online at 15:00 on 09/04. 3. The site went offline at 19:00 on 09/07 and came back online at 12:00 on 09/09. 4. The site was offline on 09/18 and came back online at 12:00 on 09/19. 5. The site was offline on 09/26 and came back online at 12:00 on 09/28. 6. The site tripped offline at 11:00 on 09/29 and remained offline. 7. Inverters 51 and 53 were offline on 09/24 and later came back online at 12:00 on 09/28. | 1. SR107395, SR107218 2. SR105747 3. SR107616 4. SR108238 5. SR108618 6. SR108746 7. SR108493 | SR107218 | SR105747 | SR107616 | SR108238 | SR108618 | SR108746 | SR108493
NY: New Windsor - Moores Hill | NY | 349057.779 | 376818.3 | -27760.521 | -7.367% | 364100 | -15042.221 | -4.131% | 1. All trackers were stuck at -51° and affected production during the evening for all inverters except Inverter 1. 2. All inverters tripped offline at 13:30 on 09/06 and reporting "Arc fault detected" and back online at 06:45 on 09/07. 3. The meter is currently capturing excess data (~400-500 kW) irrespective of inverter production. | 1. SR105950 2. SR106216 3. SR107288 | SR106216 | SR107288

## Oct
Lodestar |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 7772738.2768 | 6234266.5 | 1538471.7768 | 24.68% | 7121773.898 | 650964.3788 | 9.14%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Barkhamsted | CT | 138491 | 155364 | -16873 | -10.86% | 132521.2 | 5969.8 | 4.505% | 1. Inverter module 1.5 tripped offline at 14:15 on 10/07 due to blown fuse and back online at 12:00 on 10/08. 2. Site tripped offline at 01:30 on 10/15 and back online at 11:15 on 10/15. | 1. SR109167 2. SR109484 | 1. Closed 2. Closed | SR109484
Bunce | CT | 260255 | 183363 | 76892 | 41.93% | 0 | 260255 |  | 1. Weather station module temperature and ambient temperature are stuck reading at 184.95 and 120 degrees Fahrenheit since 5/2. On 06/03 both sensors were RMA'd. 2.Site was taken offline at 13:30 and later back online at 14:15 on 10/10 as tech was onsite for combiner box troubleshooting | 1. SR101404 2.SR102498 | 1. Pending 2. Pending | SR102498
Norcap North | CT | 277628 | 319574.2 | -41946.2 | -13.13% | 260010.4 | 17617.6 | 6.776% | 1. Inverter 1 had been derating by approximately 20 kW on 10/22. The technician replaced the fan, and the inverter is now back to normal operation. 2. Inverter 17 had been derating by approximately 20 kW on 10/22. The technician replaced the RMA'd inverter, and the inverter is now back to normal operation. 3. Inverter 12 tripped offline at 15:30 on 09/30 and back online at 08:45 on 10/02. 4. Inverter 23 was tripping on and off on 10/22 technician replaced the inverter, and the inverter is now back to 22:00 on 10/22. | 1. SR104474 2. SR104730 3. SR108793 4. SR106597 | 1. completed 2. pending 3. closed 4. closed | SR104730 | SR108793 | SR106597
Norcap South | CT | 302878 | 344129.2 | -41251.2 | -11.99% | 249144.5 | 53733.5 | 21.57% | 1. Inverter 55 had been derating by 24 kW but has been back online and producing as expected since 10/09. | 1. SR100021 | 1.Closed
Platt Hill | CT | 317455 | 319555.7 | -2100.7 | -0.6574% | 275343.9 | 42111.1 | 15.29% | 1. Site tripped offline at 07:15 on 10/13 and back online at 08:15 on 10/14. | 1. SR109401 | 1.Closed
Powder Hill | CT | 249994 | 279218.5 | -29224.5 | -10.47% | 189168 | 60826 | 32.15% | 1. Inverter IB has been offline since 09/11 and offline throughout the month. Due to CT's are under replacement. 2. Inverter K tripped offline from 09:15 to 10:30 on 10/03, reporting a critical hardware failure. After a remote reset, the inverter came back online. It tripped offline again at 11:15 on 10/11, and after another remote reset, it was back online at 10:45 on 10/11. | 1. SR107886 2. SR108955 | 1. Pending 2. New | SR108955
Sand Road | CT | 297607 | 277088.4 | 20518.6 | 7.405% | 190297 | 107310 | 56.39% | 1. Site was offline at 21:30 on 10/31 and rest of the month. | 1. SR110438 | 1. Closed
Suffield | CT | 287019.0084 | 250148.9 | 36870.1084 | 14.74% | 248952.1 | 38066.9084 | 15.29% | 1. The site went offline at 04:00 on 10/31 due to the recloser tripping open. 2. Combiner box 1.13 was offline at 07:45 on 09/20 and came back online at 13:00 on 10/10. | 1. SR110151 2. SR103565 | 1. Completed 2. Closed | SR103565
Ashby-Duffy | MA | 278830 | 346551.4 | -67721.4 | -19.54% | 262568.2 | 16261.8 | 6.193% | 1. Inverter 39 was producing with strings 5 and 6 offline throughout the month. Approval is needed for further troubleshooting. 2. Inverter 17 tripped offline at 13:30 on 10/08, reporting an "Arc Fault," and came back online at 09:30 on 10/10. | 1. SR103282 2. SR109217 | 1. Closed 2. Closed | SR109217
Ashland | MA | 243315 | 276495 | -33180 | -12% | 254956.5 | -11641.5 | -4.566% | 1. Inverter 12 was offline most of the days throughout the month. 2. Inverter 41 tripped offline at 07:00 on 10/10 and came back online at 07:00 on 10/11. It tripped offline again at 09:15 on 10/18 and was back online at 16:15 the same day. Once again, it tripped offline at 07:00 on 10/24 and came back online at 11:00 on 10/25. 3. Inverter 53 was offline on 10/11 and 10/13 and back online on next day. | 1. SR109218, SR110031 2. SR109352, SR109659 3. SR109393 | 1. Closed 2. Closed 3. Closed | SR110031 | SR109352 | SR109659 | SR109393
Barrington | MA | 58200 | 54629.31 | 3570.69 | 6.536% | 60070 | -1870 | -3.113%
Bedford - 205 Burlington Rd | MA | 4625 | N/A |  |  | N/A |  |  | 1. Inverter 6 has been offline since 15:20 on 06/29 and is under RMA. 2. Inverters 2 and 5 have been running with one string down each throughout the month. | 1. SR103728, SR109200 2. SR103770 | 1. Pending 2. Pending | SR109200 | SR103770
Billerica - 6 Cook Street | MA | 24453 | N/A |  |  | N/A
Billerica - 780 Boston Road | MA | 28372 | N/A |  |  | N/A
Cheshire | MA | 60370.1297 | 65251.82 | -4881.6903 | -7.481% | 37247.82 | 23122.3097 | 62.08% | 1. Inverter 1 was barely producing and later tripped offline at 07:00 on 09/11, reporting 'Grid line voltage out of range.' It remained offline throughout the month and is currently under RMA. | 1. SR105297 | 1. Pending
Lilly Lane | MA | 53006.5 | 52138.06 | 868.44 | 1.666% | 126763 | -73756.5 | -58.18% | 1. Inverter 61 remained offline throughout the month. 2. Inverter 69 tripped offline at 13:30 on 10/03 and reporting "Inverter open-loop self-test fault" and it's under RMA'd. 3.No communication to DAS from 17:30 on 10/09 onsite site is operational. New data logger required. | 1. SR097795 2. SR109010, SR109201 3.SR109391 | 1. Denied 2. pending 3. Pending | SR109010 | SR109201 | SR109391
Monument Valley | MA | 288382.0262 | 239919.3 | 48462.7262 | 20.2% | 211119.048 | 77262.9782 | 36.6%
Nationwide | MA | 327039 | 407388.9 | -80349.9 | -19.72% | 355513.2 | -28474.2 | -8.009% | 1. Inverter 1 has been underproducing by 13 kW, possibly due to a string being down since 09/08. 2. PAD 2 production meter not capturing all respected inverters data from 07/16 due to B phase voltages dropped to 0. | 1. SR107644 2.SR111056 | 1. pending 2.Pending | SR111056
Pulpit Hill | MA | 638010.5 | 610435.4 | 27575.1 | 4.517% | 547810.4 | 90200.1 | 16.47% | 1. Inverter 81 tripped offline at 10:00 on 10/13 and came back online at 12:00 on 10/23. Additionally, Inverter 12 went offline at 07:00 on 10/19 and back online at 07:00 on 10/20. | 1. SR109673 | 1. Closed
Sandwich | MA | 375780 | N/A |  |  | 413420.92 | -37640.92 | -9.105% | 1. Pad 2 inverters (2.1-2.3) are offline at 06:30 on 10/06 due to low isolation faults and back online at 08:00 on 10/06. and again tripped offline at 06:45on 10/07 and back online at 11:00 on 10/07. 2. Site was offline at 06:00 on 10/14 and back online at 08:30 on 10/15. 3. Site was offline at 13:15 on 10/22 and back online at 13:15 on 10/23. | 1. SR109075 2. SR109468 3. SR109856 | 1. Closed 2. Closed 3. Closed | SR109468 | SR109856
Sturbridge Barn | MA | 144489 | 147752.8 | -3263.8 | -2.209% | 144999.4 | -510.4 | -0.352%
Sturbridge Garage | MA | 64775.75 | 70978.71 | -6202.96 | -8.739% | 62618.21 | 2157.54 | 3.446% | 1. Inverter 14 was offline at 07:00 on 10/22 and reporting "Relay fault - Fault0100 Grid Relay Error - Protect0020" and is under RMA. 2. Inverter R-2-2 is offline and is currently under RMA. | 1. SR109835, SR110016 2. SR101916, SR109206 | 1. Pending 2. Pending | SR110016 | SR101916 | SR109206
Halsey Valley | NY | 734596 | 738444.9 | -3848.9 | -0.5212% | 659000 | 75596 | 11.47% | 1. Site tripped offline at 12:00 on 10/25 | 1. SR109980 | 1. Closed
Hunt Creek | NY | 466432 | 518353.3 | -51921.3 | -10.02% | 444300 | 22132 | 4.981% | 1. Inverter 18 remained offline throughout the month. 2.Site was taken offline from 14:00 to 14:45 on 10/27 due to PM work | 1. SR094254 2.SR110115 | 1. Pending 2.Closed | SR110115
Smith Creek | NY | 558450 | 577485.7 | -19035.7 | -3.296% | 485607.1 | 72842.9 | 15%
Bradford - 256 Presidential Dr | MA | 565755.256 | N/A |  |  | 585436 | -19680.744 | -3.362% | 1. Site was offline at 07:00 on 10/01 and back online at 09:00 on 10/01. 2. Inverters 1,2,3,4,42 &104 tripped offline at 09:00 on 10/31 and reporting "Power module fault (Fault0010)". 3. Inverter 21 was LOTO'd and is currently under RMA. | 1. SR108804 2. SR110396 3. SR107959, SR108028 | 1. Closed 2. Closed 3. Pending | SR110396 | SR107959 | SR108028
Charlton – 111 Brookfield Road - Bus Lot | MA | 67712.832 | N/A |  |  | 71100 | -3387.168 | -4.764%
Charlton – 154 Center Depot Road KMARD | MA | 60546.944 | N/A |  |  | 69400 | -8853.056 | -12.76% | 1. Inverter 4 was offline on 10/07 whole day.
Charlton – 142A Brookfield Rd (Mitchell) | MA | 62513.92 | N/A |  |  | 72207 | -9693.08 | -13.42% | 1. Inverter 1 has been offline since 13:00 on 07/17 and is currently under RMA. | 1. SR104528, SR104686 | 1. Pending | SR104686
Great Barrington – 3 Nolan Drive | MA | 113918.4 | N/A |  |  | 145800 | -31881.6 | -21.87% | 1. Inverter 18 has been offline since 04/09/25 and is currently under RMA. 2. Inverter 5 has been offline since 12:00 on 06/29 and is currently under RMA. 3. Inverter 27 has been offline since 15:00 on 07/04 and is currently under RMA. 4. Inverter 16 has been offline since 14:00 on 08/05 and is currently under RMA. 5. Inverter 11 tripped offline at 09:00 on 09/01 and reporting Bus(sum) over voltage fault (Fault0130) and is currently under RMA. 6. The 24 inverter has been tripping on and off throughout the month and is currently under RMA. 7. Inverter 7 went offline at 07:00 on 10/16 and later self-resolved, coming back online at 07:00 on 10/17. 8. Inverter 23 is currently under RMA. 9.Meter 1 started communicating from 10/23 but reporting 0 production. | 1. SR099815, SR099920 2. SR103531, SR109204 3. SR104024 4. SR105724, SR105808 5. SR107262, SR109205 6. SR099298 7. SR109610 8. SR108680 9.SR109284 | 1. Pending 2. Pending 3. Closed 4. pending 5. pending 6. pending 7. Closed 8. pending 9.Closed | SR099920 | SR103531 | SR109204 | SR104024 | SR105724 | SR105808 | SR107262 | SR109205 | SR099298 | SR109610 | SR108680 | SR109284
Stockbridge – 92 State Line Road Truck Stop | MA | 159604.823 | N/A |  |  | 280200 | -120595.177 | -43.04% | 1. The site tripped offline at 11:00 on 09/29 and back online at 09:00 on 10/01. 2. The site was offline at 02:00 on 10/06 and back online at 06:00 on 10/08. 3. The site went offline at 15:00 on 10/08 and came back online at 12:00 on 10/10 after the technician closed the SEL relay. 4. The site was offline at 12:25 on 10/20 and back online at 14:00 on 10/21. 5. The site went offline at 23:48 on 10/22 and came back online at 09:00 on 10/24. It went offline again at 16:00 on 10/24 and remained offline for the rest of the month. | 1. SR108746 2. SR109070 3. SR109231 4. SR109714 5. SR109859 | 1. Closed 2. Closed 3. Closed 4. Closed 5. Closed | SR109070 | SR109231 | SR109714 | SR109859
NY: New Windsor - Moores Hill | NY | 262233.1875 | N/A |  |  | 286200 | -23966.8125 | -8.374% | 1. All trackers were stuck at -51° and affected production during the evening for all inverters except Inverter 1. | 1. SR105950 | 1. Closed

## Nov
Lodestar |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 4209367.0942 | 4058259.71 | 151107.3842 | 3.723% | 4817177.55 | -607810.4558 | -12.62%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Barkhamsted | CT | 87104 | 106396.9 | -19292.9 | -18.13% | 99959.12 | -12855.12 | -12.86% | 1. Site production was low on 11/10, 11/17, 11/23, 11/25, 11/30 due to low weather
Bunce | CT | 151878 | 139841 | 12037 | 8.608% | 0 | 151878
Norcap North | CT | 174376 | 238337.8 | -63961.8 | -26.84% | 199634.5 | -25258.5 | -12.65% | 1. Inverters 26 to 29 were offline from 11:00 on 11/24 to end of the month. 2. Inverter 17 was derating by about 20kw for whole month. 3. Inverter 1 was underproducing by 30kW and Inverter 2 was underproducing by 20kW and inverter 3 was underproducing by 13kW compared to peers for whole month due to seasonal shading | 1. SR111637 2. SR104730 | 1. Closed 2. Pending | SR104730
Norcap South | CT | 196473 | 261432.7 | -64959.7 | -24.85% | 180795.7 | 15677.3 | 8.671% | 1. Few Inverters have morning and evening shading.
Platt Hill | CT | 170237 | 215614.2 | -45377.2 | -21.05% | 214363.6 | -44126.6 | -20.58% | 1.Site was offline from 10:15 on 11/06 and back online at 13:00 on 11/07. 2. Site was offline from 11:00 on 11/26 and back online at 14:00 on 11/27 and was again offline from 09:00 on 11/28 and back online at 14:30 on 11/29. | 1. SR110713 2. SR111771 | 1. Closed 2. Closed | SR111771
Powder Hill | CT | 146438 | 185203.8 | -38765.8 | -20.93% | 141768 | 4670 | 3.294% | 1. Inverter 2 was offline for whole month. 2. Inverter 11 was offline from 07:45 on 11/06 to end of the month. 3. Inverter 8 was offline from 09:30 to 17:00 on 11/19 and was remained offline from 11/24 to end f the month. 4. Inverter 4 was derated to 4kW on 11/08 from 13:00 to 17:00. 5. inverter 6,10 underperforming by 30kW. inverter 3,9 underperforming by 17 kW. Inverter 7,12 underperforming by 10 kW. Inverter 4 underperforming by 6kW from 11/01 to 11/20. | 1. SR107886 2. SR108955 3. SR111324 4. SR110812 5. SR111372 | 1. Pending 2. Pending 3. Closed 4. Closed 5. Closed | SR108955 | SR111324 | SR110812 | SR111372
Sand Road | CT | 145286 | 133666.3 | 11619.7 | 8.693% | 135386 | 9900 | 7.312%
Suffield | CT | 162203.9916 | 157084.9 | 5119.0916 | 3.259% | 187711 | -25507.0084 | -13.59% | 1. Site was offline from 04:00 on 10/31 to 11:45 on 11/04. | 1. SR110151 | 1. Closed
Ashby-Duffy | MA | 177666 | 291791.4 | -114125.4 | -39.11% | 177083.7 | 582.3 | 0.3288% | 1. Inverters 8,9,11,12,13,14,15, and 16 have tripped offline at 11:00 on 11/18 and later back online on 11/19 at 13:30 2. String 39-5 and 6 were offline for whole month. 3. Inverters 8,9,11,12,13,14,15, and 16 have tripped offline at 12:45 on 11/01 and later back online on 11/03 at 08:30 4. All inverters have morning and evening shading issue. | 1. SR111269 2. SR099765 3. SR110475 | 1. Closed 2. Pending 3. Closed | SR099765 | SR110475
Ashland | MA | 155447.5 | 193692.2 | -38244.7 | -19.75% | 152755.9 | 2691.6 | 1.762% | 1. Inverter 12 parts being RMA'd. 2. Inverter 16 being RMA'd 3. Inverter 64 was offline from 08:15 to 16:30 on 11/01, from 12:15 to 14:15 on 11/09 and again it was offline from 08:30 on 11/13 to 16:00 on 11/14. 4. Inverter 53 was offline from 12:15 to end of the day on 11/12. 5. All inverters have seasonal shading. | 1. SR097799 2. SR095816, SR107405 3. SR110440 | 1. Pending 2. Pending 3. Closed | SR095816 | SR107405 | SR110440
Barrington | MA | 30040 | 27548.87 | 2491.13 | 9.043% | 39410 | -9370 | -23.78% | 1. Site production was low on 11/10, 11/17, 11/23, 11/25, 11/30 due to low weather
Bedford - 205 Burlington Rd | MA | 15415 | N/A |  |  | N/A |  |  | 1. Inverter 6 parts being RMA'd 2. Inverter 2 and 5 were down a string for whole month. | 1. SR109200 2. SR103770 | 1. Pending 2. Pending | SR103770
Billerica - 6 Cook Street | MA | 14743 | N/A |  |  | N/A |  |  | 1. Inverters have seasonal shading.
Billerica - 780 Boston Road | MA | 17106 | N/A |  |  | N/A |  |  | 1. Inverters have seasonal shading.
Cheshire | MA | 29897.25 | 34177.48 | -4280.23 | -12.52% | 21472.23 | 8425.02 | 39.24% | 1. Inverter 1 being RMA'd. 2. Inverters have seasonal shading | 1. SR109203 | 1. Pending
Lilly Lane | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1. Inverter 61 remained offline throughout the month. 2. Inverter 69 tripped offline at 13:30 on 10/03 and reporting "Inverter open-loop self-test fault" and it's under RMA'd. 3.No communication to DAS from 17:30 on 10/09 onsite site is operational. New data logger required. | 1. SR097795 2. SR109010, SR109201 3.SR109391 | 1. Denied 2. pending 3. Pending | SR109010 | SR109201 | SR109391
Monument Valley | MA | 131810.0556 | 119514.7 | 12295.3556 | 10.29% | 156272 | -24461.9444 | -15.65% | 1. Inverters 1–4 tripped offline at 13:15 on 11/17 with an “Emergency Stop” fault and came back online at 08:00 on 11/18. 2. Pad 1 inverters tripped offline at 09:00 on 11/27 with a “Remote Emergency Stop” fault and came back online at 12:45 on 11/27. | 1. SR111212 2. SR111798 | 1. Closed 2. Closed | SR111798
Nationwide | MA | 196186 | 282471.5 | -86285.5 | -30.55% | 258464.4 | -62278.4 | -24.1% | 1. Inverter 1 has been underperforming by 13 kW since 09/08/25, possibly due to a string being down. 2. Pad 2 production meter phase B is stopped communicating since 07/16. | 1. SR107644 2. SR111056 | 1. Pending 2. Closed | SR111056
Pulpit Hill | MA | 374710.75 | 383968.2 | -9257.45 | -2.411% | 349428.8 | 25281.95 | 7.235% | 1. Inverter 12 went offline at 07:00 on 11/09, reporting a 'Bus Differential Fault,' and came back online at 09:00 on 11/10. It tripped offline again at 07:00 on 11/13, reporting a 'Bus Differential High Fault – Fault 0110,' and returned online at 07:00 on 11/14. Once again, it tripped offline at 07:00 on 11/26, reporting a 'Bus Differential High Fault – Fault 0110,' and came back online at 07:00 on 11/27. | 1. SR110840, SR111026, SR111774 | 1. Pending | SR111026 | SR111774
Sandwich | MA | 122672.013 | N/A |  |  | 279859 | -157186.987 | -56.17% | 1. Site was offline at 13:23 on 11/07 and back online at 10:00 on 11/08. 2. The site went offline at 17:30 on 11/12 due to a utility outage and remained offline throughout the month. | 1. SR110800 2. SR110992 | 1. Closed 2. Closed | SR110992
Sturbridge Barn | MA | 95039.5 | 105108.2 | -10068.7 | -9.579% | 102369.9 | -7330.4 | -7.161%
Sturbridge Garage | MA | 38357.5 | 49063.86 | -10706.36 | -21.82% | 52082.4 | -13724.9 | -26.35% | 1. Inverter 9 went offline at 07:00 on 11/19, reporting 'Bus sum high fault - Fault 0130,' and it is currently under RMA. 2. Inverter 14 went offline at 07:00 on 10/22, reporting 'Relay fault - Fault0100 Grid Relay Error - Protect0020,' and it is currently under RMA. 3. Inverter 3 went offline at 07:00 on 05/25, reporting 'Bus(sum) over voltage fault,' and it is currently under RMA. | 1. SR111328 2. SR109835, SR110016 3. SR101916, SR109206 | 1. Pending 2. Pending 3. Pending | SR109835 | SR110016 | SR101916 | SR109206
Halsey Valley | NY | 370752 | 402709.4 | -31957.4 | -7.936% | 424000 | -53248 | -12.56%
Hunt Creek | NY | 181783 | 282713.8 | -100930.8 | -35.7% | 254400 | -72617 | -28.54% | 1. Inverter 18 tripped offline at 08:20 on 12/08/24, and after the technician replaced it, the inverter came back online at 10:00 on 11/13/25. 2. The site tripped offline at 12:13 on 11/07 due to the SEL relay opening. After the technician closed the relay, the site came back online at 11:00 on 11/08. | 1. SR094254 2. SR110778 | 1. Closed 2. Closed | SR110778
Smith Creek | NY | 289883 | 324106.2 | -34223.2 | -10.56% | 381936.3 | -92053.3 | -24.1% | 1. The site tripped offline at 12:13 on 11/07 due to the SEL relay opening. After the technician closed the relay, the site came back online at 11:00 on 11/08. | 1. SR110779 | 1. Closed
Bradford - 256 Presidential Dr | MA | 339827.203 | N/A |  |  | 397267 | -57439.797 | -14.46% | 1. Inverters 1, 2, 3, 4, 42, and 104 tripped offline at 09:00 on 10/31 with a “Power Module Fault (Fault0010)” and came back online at 07:00 on 11/01. 2. Inverter 21 was LOTO'd and is currently under RMA. | 1. SR110396 2. SR107959, SR108028 | 1. Closed 2. Pending | SR107959 | SR108028
Charlton – 111 Brookfield Road - Bus Lot | MA | 45942.016 | N/A |  |  | 54100 | -8157.984 | -15.08% | 1. Site has low production on 11/10, 11/13, 11/21 to 11/23, 11/30 due to bad weather
Charlton – 154 Center Depot Road KMARD | MA | 41440.896 | N/A |  |  | 56900 | -15459.104 | -27.17% | 1. Site has low production on 11/10, 11/13, 11/21 to 11/23, 11/30 due to low weather
Charlton – 142A Brookfield Rd (Mitchell) | MA | 43129.088 | N/A |  |  | 55658 | -12528.912 | -22.51% | 1. Inverter 5 was offline at 07:00 on 11/30 and reporting "Bus(sum) over voltage fault (Fault0130)". | 1. SR111845 | 1. Closed
Great Barrington – 3 Nolan Drive | MA | 55106.304 | N/A |  |  | 100100 | -44993.696 | -44.95% | 1. Inverter 18 has been offline since 04/09/25 and is currently under RMA. 2. Inverter 5 has been offline since 12:00 on 06/29 and is currently under RMA. 3. Inverter 27 has been offline since 15:00 on 07/04 and is currently under RMA. 4. Inverter 16 has been offline since 14:00 on 08/05 and is currently under RMA. 5. Inverter 11 tripped offline at 09:00 on 09/01 and reporting Bus(sum) over voltage fault (Fault0130) and is currently under RMA. 6. The 24 inverter has been tripping on and off throughout the month and is currently under RMA. 7. Meter 1 started communicating from 10/23 but reporting 0 production. 8. Inverter 7 is offline on 11/11 and 11/14. 9. Inverter 4 has been tripping on and off for the whole month. | 1. SR099815, SR099920 2. SR103531, SR109204 3. SR104024,SR111353 4. SR105724, SR105808 5. SR107262, SR109205 6. SR099298 7. SR109284 8. SR109610 9. SR111511, SR112408 | 1. Pending 2. Pending 3. pending 4. pending 5. pending 6. pending 7. Closed 8. Closed 9. New | SR099920 | SR103531 | SR109204 | SR104024 | SR111353 | SR105724 | SR105808 | SR107262 | SR109205 | SR099298 | SR109284 | SR109610 | SR111511 | SR112408
Stockbridge – 92 State Line Road Truck Stop | MA | 90970.027 | N/A |  |  | 181000 | -90029.973 | -49.74% | 1. The site went offline at 16:00 on 10/24 due to an open SEL relay. After the technician closed the relay, the site came back online at 13:00 on 11/05. 2. The site went offline at 07:00 on 11/28. Additionally, multiple inverters were reporting “Grid line voltage out of range (GridV.OutLim).” The meter also stopped communicating. After the technician reset the site, it came back online at 14:00 on 11/28. | 1. SR109859 2. SR111811 | 1. Closed 2. Closed | SR111811
NY: New Windsor - Moores Hill | NY | 117447 | 123816.3 | -6369.3 | -5.144% | 163000 | -45553 | -27.95% | 1. Inverters 3, 8, 9, 10, 11, 12, and 13 tripped offline at 12:30 on 11/16, reporting "Arc Detected", and back online at 07:00 on 11/17. 2. The meter and weather station stopped communicating at 07:00 on 11/23, and the issue persisted throughout the month. | 1. SR111173 2. SR111499 | 1. Pending 2. Pending | SR111499

## Dec
Lodestar |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 2734581.833 | 3988833.01 | -1254251.177 | -31.44% | 3900572.65 | -1165990.817 | -29.89% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Barkhamsted | CT | 54991 | 103574.9 | -48583.9 | -46.91% | 77256.07 | -22265.07 | -28.82% | 1. Site has tripped offline at 20:00 on 12/02 and back online at 09:30 on 12/03. 2. The site went offline at 08:45 on 12/19 due to the SEL relay being in an open state. After the technician closed the relay, the site came back online at 09:15 on 12/20. 3. All inverters were offline from 10:45 to 12:00 on 12/23 while the PE was on site replacing the current measuring board. 4. The site went offline at 09:00 on 12/24 due to the SEL relay being in an open state. After the technician closed the relay, the site came back online at 13:30 on 12/24. 5. Inverters 1.2, 1.3, 1.4, and 1.5 went offline on 12/26 and reported recurring faults of “Homopolar fault” and “Optic fiber/sync CAN communication fault.” Later, the PE was on site and brought inverter 1.5 back online at 12:00. All other inverters were brought back online on 12/31. | 1. SR112019 2. SR113246 3. SR113431 4. SR113583 5. SR113662 | 1. Closed 2. Closed 3. Closed 4. Closed 5. Closed | SR113246 | SR113431 | SR113583 | SR113662
Bunce | CT | 104154 | 172519.1 | -68365.1 | -39.63% | 0 | 104154 |  | 1. The site experienced short trips that later self-resolved starting on 12/08. The issue was resolved on 12/15, and the site is producing as expected. | 1. SR112670 | 1. Closed
Norcap North | CT | 126906.5 | 230092.7 | -103186.2 | -44.85% | 153339.2 | -26432.7 | -17.24% | 1. Inverters 26 through 29 were offline at 11:00 on 11/24. After the technician replaced the shunt trip unit, the inverters came back online at 10:45 on 12/01. 2. Inverter 17 was derating by approximately 20 kW for the whole month. The inverter powerhead is being RMA’d. 3. Inverter 5 went offline at 07:00 on 12/19 and reported a “Bus hardware overvoltage fault – Fault0020” for the whole month. The inverter is under RMA. 4. Inverter 1 was underproducing by 30kW and Inverter 2 was underproducing by 20kW and inverter 3 was underproducing by 13kW compared to peers for whole month due to seasonal shading | 1. SR111637 2. SR104730, SR114162 3. SR113187 | 1. Closed 2. New 3. Completed | SR104730 | SR114162 | SR113187
Norcap South | CT | 146891.5 | 256633.9 | -109742.4 | -42.76% | 129416 | 17475.5 | 13.5% | 1. Few Inverters have morning and evening shading. 2. Site production was low on 12/02, 12/14, 12/15, 12/19. 12/23, 12/27 to 12/29.
Platt Hill | CT | 140425 | 209654.5 | -69229.5 | -33.02% | 167936.6 | -27511.6 | -16.38% | 1. The site tripped offline at 08:30 on 12/01. After the technician reset the breaker and pulled the logs, the site came back online at 16:15 on 12/01. 2. Site has tripped offline at 12:00 on 12/03 and back online at 16:15 on 12/03. 3. Site has tripped offline at 12:00 on 12/04 and back online at 16:00 on 12/04. 4. The site tripped offline at 09:30 on 12/05 and came back online at 11:15 on 12/06. It tripped offline again at 12:15 on 12/06 and returned online at 07:45 on 12/08. | 1. SR111860, SR111771 2. SR112036 3. SR112036, SR112211 4. SR112264 | 1. Closed 2. Closed 3. Closed 4. Closed | SR111771 | SR112036 | SR112036 | SR112211 | SR112264
Powder Hill | CT | 94846 | 175246.8 | -80400.8 | -45.88% | 117108 | -22262 | -19.01% | 1. Inverter 2 was offline since 09/11/25 and back online at 15:00 on 12/09. 2. Inverter 11 has been offline since 07:45 on 11/06 and remained offline for the whole month. Parts replacement is pending. 3. Inverter 8 has been offline since 11/24 and remained offline for the entire month. Parts replacement is pending. 4. Inverter 4 was derated to 4kW from 12/13. | 1. SR107886 2. SR108955 3. SR111324 4. SR113395 | 1. Closed 2. Closed 3. Closed 4. New | SR108955 | SR111324 | SR113395
Sand Road | CT | 117106 | 149982.8 | -32876.8 | -21.92% | 118038 | -932 | -0.7896% | 1. Site has low production on 12/02, 12/03, 12/13 to 12/15 due to snow.
Suffield | CT | 129442 | 171639.9 | -42197.9 | -24.59% | 149954 | -20512 | -13.68% | 1. The production was low on 12/02,12/14,12/19,12/23,12/27 to 12/29 due to snow.
Ashby-Duffy | MA | 93256 | 334432.7 | -241176.7 | -72.12% | 139093.7 | -45837.7 | -32.95% | 1. Inverters 8, 9, 11, 12, 13, 14, 15, and 16 tripped offline at 11:00 on 12/20, reporting “Waiting for grid voltage Grid failure.” After the technician reset the main breaker, all inverters came back online at 15:00 on 12/20. 2. Inverters 8,9,11,12,13,14,15, and 16 tripped offline at 11:00 on 12/21, reporting “Waiting for grid voltage Grid failure.” After the technician reset the main breaker, all inverters came back online at 09:30 on 12/30. 3. String 39-5 and 6 were offline for whole month. 4. All inverters have morning and evening shading issue. 5. Weather station reporting erroneous values since 12/03. | 1. SR113312 2. SR113312, SR113753 3. SR099765 | 1. Closed 2. Closed 3. Closed | SR113312 | SR113753 | SR099765
Ashland | MA | 105456.5 | 190434.7 | -84978.2 | -44.62% | 99947.98 | 5508.52 | 5.511% | 1. Inverter 12 parts being RMA'd. 2. Inverter 16 being RMA'd 3. Inverter 53 was offline from 11:45 on 12/01 to end of the day on 12/01. 4. All inverters have seasonal shading. | 1. SR097799 2. SR095816, SR107405 | 1. Pending 2. Pending | SR095816 | SR107405
Barrington | MA | 11420 | 22982.58 | -11562.58 | -50.31% | 27320 | -15900 | -58.2% | 1. The site stopped communicating with the DAS at 08:15 on 12/02 and was possibly offline. It came back online at 11:45 on 12/03. 2. The inverter went offline at 07:00 on 12/05, reporting “AC Voltage too low – Wait for grid,” and came back online at 12:15 on 12/05. The inverter had a delayed start on 12/04. 3. The site went offline at 10:30 on 12/10. After the technician repaired the blown fuse, the site came back online at 13:00 on 12/15. | 1. SR111945 2. SR112266 3. SR112513 | 1. Closed 2. Closed 3. Closed | SR112266 | SR112513
Bedford - 205 Burlington Rd | MA | 10323 | N/A |  |  | N/A |  |  | 1. Inverter 6 parts being RMA'd 2. Inverter 2 and 5 were down a string for whole month. | 1. SR109200 2. SR103770 | 1. Pending 2. Pending | SR103770
Billerica - 6 Cook Street | MA | 9495 | N/A |  |  | N/A |  |  | 1. Inverters have seasonal shading.
Billerica - 780 Boston Road | MA | 10866 | N/A |  |  | N/A |  |  | 1. Inverters have seasonal shading.
Cheshire | MA | 11661.3726 | 32983.64 | -21322.2674 | -64.64% | 19005.41 | -7344.0374 | -38.64% | 1. Inverter 1 being RMA'd. 2. Inverters have seasonal shading | 1. SR109203 | 1. Pending
Lilly Lane | MA | [7 empty] | 1. Inverter 61 remained offline throughout the month. 2. Inverter 69 tripped offline at 13:30 on 10/03 and reporting "Inverter open-loop self-test fault" and it's under RMA'd. 3.No communication to DAS from 17:30 on 10/09 onsite site is operational. New data logger required. | 1. SR097795 2. SR109010, SR109201 3.SR109391 | 1. Denied 2. pending 3. Pending | SR109010 | SR109201 | SR109391
Monument Valley | MA | 80335.8244 | 114828.2 | -34492.3756 | -30.04% | 128336 | -48000.1756 | -37.4% | 1. The production was low on 12/02,12/14,12/15,12/19,12/23,12/27 to 12/29 due to snow.
Nationwide | MA | 54594 | 258625.8 | -204031.8 | -78.89% | 237962.1 | -183368.1 | -77.06% | 1. Inverter 1 has been underperforming by 13 kW since 09/08/25, possibly due to a string being down. 2. Pad 2 Phase B voltage reading was zero, which appeared to be affecting production by approximately 20% since 07/16. After the technician replaced a blown fuse, the site is producing as expected. | 1. SR107644 2. SR111056, SR112075 | 1. Pending 2. Closed | SR111056 | SR112075
Pulpit Hill | MA | 217446.5 | 352607.5 | -135161 | -38.33% | 290892.9 | -73446.4 | -25.25% | 1. Inverter 12 was offline at 07:00 on 12/06 and reporting "Bus differential high fault - Fault0110" and back online at 07:00 on 12/08. additionally inverter is offline on 12/14,12/23,12/25,12/27, 12/28 and 12/29 2. Inverter 56 was offline at 07:00 on 12/06 and reporting "Bus differential high fault - Fault0110" and back online at 07:00 on 12/07. 3. Inverter 74 was offline at 07:00 on 12/06 and reporting "Bus differential high fault - Fault0110" and back online at 07:00 on 12/30. | 1. SR111026, SR111774, SR113446 2. SR112319 3. SR113760 | 1. Closed 2. Closed 3. Closed | SR111774 | SR113446 | SR112319 | SR113760
Sandwich | MA | 165593.987 | 171564.5 | -5970.513 | -3.48% | 228866 | -63272.013 | -27.65% | 1. The site went offline at 17:30 on 11/12 due to a utility outage and back online at 10:00 on 12/04. | 1. SR110992 | 1. Closed
Sturbridge Barn | MA | 67685 | 102284.8 | -34599.8 | -33.83% | 92285.55 | -24600.55 | -26.66% | 1. Inverter 36 tripped offline at 08:45 on 12/11, reporting a "Bus Sum High Fault – Fault0130" and came back online at 07:00 on 12/12. | 1. SR112588 | 1. Closed
Sturbridge Garage | MA | 26284.25 | 46589.89 | -20305.64 | -43.58% | 47159.34 | -20875.09 | -44.27% | 1. Inverter 9 went offline at 07:00 on 11/19, reporting 'Bus sum high fault - Fault 0130,' and it is currently under RMA. 2. Inverter 14 went offline at 07:00 on 10/22, reporting 'Relay fault - Fault0100 Grid Relay Error - Protect0020,' and it is currently under RMA. 3. Inverter 3 went offline at 07:00 on 05/25, reporting 'Bus(sum) over voltage fault,' and it is currently under RMA. | 1. SR111328 2. SR109835, SR110016 3. SR101916, SR109206 | 1. Pending 2. Pending 3. Pending | SR109835 | SR110016 | SR101916 | SR109206
Halsey Valley | NY | 151716 | 364777.3 | -213061.3 | -58.41% | 330000 | -178284 | -54.03% | 1. Inverters 13, 25, and 37 were offline at 07:00 on 12/04 and later self-resolved, coming back online at 11:30 on 12/04. | 1. SR112196 | 1. Closed
Hunt Creek | NY | 82352 | 239886.8 | -157534.8 | -65.67% | 202300 | -119948 | -59.29% | 1. Inverter 27 tripped offline at 13:15 on 12/14, reporting a ‘Grid Voltage Unbalance’ fault, and later self-resolved, coming back online at 15:15 on 12/15. It tripped offline again at 10:15 on 12/20 and later self-resolved, coming back online at 11:45 on 12/20. 2. Inverter 2 tripped offline at 11:30 AM on 12/24, reporting an "Overcurrent Protection" fault, and came back online at 07:00 on 12/24. Inverter 2 tripped offline again at 08:45 on 12/25 with an "Overcurrent Protection" fault and continued tripping on and off throughout the month. The inverter is currently under RMA'd. 3. Inverters 3, 4, 5, 8, 14, 15, 18, 19, 22, 23, and 27 tripped offline at 15:45 on 12/25, reporting a ‘Grid Voltage Unbalanced’ fault, and later self-resolved, coming back online at 07:00 on 12/26. | 1. SR112709 2. SR113313 3. SR113622 | 1. Closed 2. Pending 3. Closed | SR113313 | SR113622
Smith Creek | NY | 173969 | 287490 | -113521 | -39.49% | 328827.5 | -154858.5 | -47.09% | 1. The site was expired in AlsoEnergy.
Bradford - 256 Presidential Dr | MA | 241700.6 | N/A |  |  | 305035 | -63334.4 | -20.76% | 1. Inverter 21 was LOTO'd and is currently under RMA. | 2. SR107959, SR108028 | 1. pending | SR108028
Charlton – 111 Brookfield Road - Bus Lot | MA | 33385 | N/A |  |  | 44600 | -11215 | -25.15% | 1. The production was low on 12/02,12/07,12/14,12/15,12/19,12/23,12/27 to 12/29 due to snow.
Charlton – 154 Center Depot Road KMARD | MA | 31014.14 | N/A |  |  | 51900 | -20885.86 | -40.24% | 1. The production was low on 12/02,12/07,12/14,12/15,12/19,12/23,12/27 to 12/29 due to snow.
Charlton – 142A Brookfield Rd (Mitchell) | MA | 31324.16 | N/A |  |  | 45625 | -14300.84 | -31.34% | 1. Inverter 3 tripped offline at 09:00 on 12/16and reporting "Bus(sum) over voltage fault (Fault0130)" and back online at 07:00 on 12/17. and later inverter is under RMA'd. 1. Inverter 5 was offline at 07:00 on 11/30 and reporting "Bus(sum) over voltage fault (Fault0130)" and back online at 07:00 on 12/01. | 1. SR112900, SR113085 2. SR111845 | 1. pending 2. Closed | SR113085 | SR111845
Great Barrington – 3 Nolan Drive | MA | 22673.6 | N/A |  |  | 84700 | -62026.4 | -73.23% | 1. Inverter 18 has been offline since 04/09/25 and is currently under RMA. 2. Inverter 5 has been offline since 12:00 on 06/29 and is currently under RMA. 3. Inverter 27 has been offline since 15:00 on 07/04 and is currently under RMA. 4. Inverter 16 has been offline since 14:00 on 08/05 and is currently under RMA. 5. Inverter 11 tripped offline at 09:00 on 09/01 and reporting Bus(sum) over voltage fault (Fault0130) and is currently under RMA. 6. The 24 inverter has been tripping on and off throughout the month and is currently under RMA. 7. Meter 1 started communicating from 10/23 but reporting 0 production. 8. Inverter 7 has been tripping on and off for the whole month. Currently under RMA. 9. Inverter 4 has been tripping on and off for the whole month. | 1. SR099815, SR099920 2. SR103531, SR109204 3. SR104024,SR111353 4. SR105724, SR105808 5. SR107262, SR109205 6. SR099298 7. SR109284 8. SR109610 9. SR111511, SR112408, SR110794 | 1. Pending 2. Pending 3. pending 4. pending 5. pending 6. pending 7. Closed 8. Closed 9. Pending | SR099920 | SR103531 | SR109204 | SR104024 | SR111353 | SR105724 | SR105808 | SR107262 | SR109205 | SR099298 | SR109284 | SR109610 | SR111511 | SR112408 | SR110794
Stockbridge – 92 State Line Road Truck Stop | MA | 61262.499 | N/A |  |  | 145700 | -84437.501 | -57.95% | 1. All inverters was offline at 07:00 12/06 and reporting "Grid over frequency" and back online at 07:00 on 12/07. 2. Site was barely producing from 12/02 to 12/07, 12/14 to 12/16, 12/23, 12/27 to 12/30 due to snow | 1. SR112322 | 1. Closed
NY: New Windsor - Moores Hill | NY | 126005.4 | 0 |  |  | 137968.3 | -11962.9 | -8.671% | 1. The meter and weather station stopped communicating at 07:00 on 11/23, and the issue persisted throughout the month. | 2. SR111499 | 1. pending

## Sites
Portfolio: | Lodestar
Site DAS Name | Site | State | Update | DAS
Barkhamsted Solar | Barkhamsted | CT | AEF | PowerTrack
Bunce Solar | Bunce | CT | AEF | PowerTrack
Norcap North | Norcap North | CT | AEF | PowerTrack
Norcap South | Norcap South | CT | AEF | PowerTrack
Platt Hill | Platt Hill | CT | AEF | PowerTrack
Powder Hill | Powder Hill | CT | AEF | PowerTrack
Sand Road Solar | Sand Road | CT | AEF | PowerTrack
Suffield Solar | Suffield | CT | AEF | PowerTrack
Ashby-Duffy | Ashby-Duffy | MA | AEF | PowerTrack
Ashland Solar | Ashland | MA | AEF | PowerTrack
Barrington Fairgrounds | Barrington | MA | AEF | PowerTrack
MA: Bedford - 205 Burlington Rd | Bedford - 205 Burlington Rd | MA |  | GPM
MA: Billerica: 6 Cook Street | Billerica - 6 Cook Street | MA |  | GPM
MA: Billerica - 780 Boston Road | Billerica - 780 Boston Road | MA |  | GPM
Cheshire Solar | Cheshire | MA | AEF | PowerTrack
Lilly Lane (N-4) | Lilly Lane | MA | AEF | PowerTrack
Monument Valley | Monument Valley | MA | AEF | PowerTrack
Nationwide | Nationwide | MA | AEF | PowerTrack
Pulpit Hill | Pulpit Hill | MA | AEF | PowerTrack
MA: Sandwich - 9 Victory Drive Solar | Sandwich | MA |  | PowerTrack
Sturbridge Barn (N-3) | Sturbridge Barn | MA | AEF | PowerTrack
Sturbridge Garage (R-2) | Sturbridge Garage | MA | AEF | PowerTrack
Halsey Valley | Halsey Valley | NY | AEF | PowerTrack
Hunt Creek Solar | Hunt Creek | NY | AEF | PowerTrack
Smith Creek Solar | Smith Creek | NY | AEF | PowerTrack
006 - Bradford O&M | Bradford - 256 Presidential Dr | MA |  | PF Drive
007 - Bus Lot O&M | Charlton – 111 Brookfield Road - Bus Lot | MA |  | PF Drive
010 - Kmard O&M | Charlton – 154 Center Depot Road KMARD | MA |  | PF Drive
011 - Mitchell O&M | Charlton – 142A Brookfield Rd (Mitchell) | MA |  | PF Drive
012 - Nolan O&M | Great Barrington – 3 Nolan Drive | MA |  | PF Drive
014 - Truck Stop O&M | Stockbridge – 92 State Line Road Truck Stop | MA |  | PF Drive
Moores Hill | NY: New Windsor - Moores Hill | NY | AEF | PowerTrack